2026-06-30 10:38 | NO | YES | NO | 20210061 | 35508 | 2021-07-09 15:13 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2021-04-21 17:14 | EASTERN | YES | 2021 | COUNTY RD. 200 W. AT ABBEY LN. | COLUMBUS | BARTHOLOMEW | IN | 47201-8586 | 39.237 | -85.9502 | YES |  |  | YES | [5 empty] | 2021-04-21 20:59 | 1303207 | 1303361 & 1309152 | NATURAL GAS |  | 1400 | 140 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 15 | 2021-04-21 17:14 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-04-21 17:14 | 2021-04-21 17:31 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 146 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2020 | 2020 |  |  |  |  | 10 | X52 | TMK IPSCO WILDER | STEEL |  | SEAMLESS |  | 0.25 | [6 empty] | OTHER | [8 empty] | VERTICAL DRILLING AUGER CUT SLOT IN PIPELINE APPROXIMATELY 2" X 8" | CLASS 3 LOCATION | 0 | 0 | 168201 | 185821.920705220973811 | 0 | 0 | 0 | 0 |  | 14.66 | 20524 | 16535.1162790697674418604651162790697674 | 2052 | 1653.189368770764119601328903654485049834 | 190777 | 90267.9442391868591713554817275747508305 | 204010.2263530615053724617940199335548172 | 0 | 0 | 388 | 0 | 0 | 388 | 0 | 200 | 210 | 225 | 192.619(A)(2) | 2020-09-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER(S) ACTIONS WERE FOCUSED ON ASSISTANCE AND PROVIDING INFORMATION TO FIELD OPERATIONS | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE EASEMENT | YES | [9 empty] | CONTRACTOR | AUGER | DRAINAGE | NO | [5 empty] | YES | 20 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JERRY KNECHT | LEAD SPECIALIST OPERATIONS | jerry.knecht@centerpointenergy.com | 317-718-3614 |  | JERRY KNECHT | jerry.knecht@centerpointenergy.com | 317-718-3614 | SHANE ALEXANDER | MANAGER PIPELINE SAFETY - COMPLIANCE | 317-718-3603 | shane.alexander@centerpointenergy.com | A CONTRACTOR WORKING WITHOUT VALID LOCATE REQUEST, WAS WORKING TO DE-WATER THE SITE OF A RESIDENTIAL SUBDIVISION BY USING A VERTICAL AUGER TO PERFORM THIS DE-WATERING PROCESS WHEN THEY AUGER-ED INTO A 10" STEEL HIGH PRESSURE DISTRIBUTION NATURAL GAS PIPELINE (HOLE APPROX. 2" X 8"). THIS RESULTED IN VALVING-OFF, ISOLATING AND BLOWING DOWN APPROXIMATELY 4.7 MILES OF THIS 10" STEEL HIGH PRESSURE DISTRIBUTION PIPELINE THAT WAS OPERATING AT APPROXIMATELY 210 PSIG, EFFECTING 338 RESIDENTIAL CUSTOMERS. AFTER BLOW-DOWN OF THIS LINE, TEMPORARY REPAIRS WERE PERFORMED BY REMOVING THE DAMAGED PIPELINE AND CAPPING THE PIPELINE ON EITHER SIDE OF THE DAMAGE. STOPPLE FITTINGS AND PIPE WERE LATER USED TO RECONNECT THE PIPELINE. ORIGINAL INCIDENT NOTIFICATION WAS MADE TO NRC ON REPORT #1303207 ASSUMING THAT THE NATURAL GAS RELEASE WOULD BE IN EXCESS OF 3 MMCF HOWEVER, LATER UPDATED ON REPORT #1303361 WHEN IT WAS DETERMINED THAT THIS GAS RELEASE THRESHOLD WAS NOT ACHIEVED. ON 6/29/21 AT 10:39 HOURS, AN UPDATE WAS MADE TO THE NRC ON REPORT #1309152 WHEN IT WAS DETERMINED THAT ACTUAL COSTS HAD NOW EXCEEDED THE FINANCIAL THRESHOLD FOR INCIDENT REPORTING.
2026-06-30 10:38 | NO | YES | NO | 20210062 | 36090 | 2021-07-12 18:04 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2021-07-11 07:30 | CENTRAL | YES | 2021 | CHAVENELLE RD & RADFORD RD | DUBUQUE | DUBUQUE | IA | 52003 | 42.4917 | -90.7507 | [7 empty] | YES | VALVE ON CHART LINE SHUT OFF VERY SMALL LEAK. NOT BLOWING GAS | 2021-07-12 14:30 | 1310452 | 1310667 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-07-11 07:30 |  |  |  | 2021-07-11 07:42 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2006 | UNKNOWN | [7 empty] | STEEL |  | SEAMLESS |  | 0.188 | [6 empty] | LEAK |  |  | OTHER | .25" FITTING LEAKING | [5 empty] | CLASS 2 LOCATION | 5000 | 5523.805468018055 | 301270 | 332831.37466995988597 | 400 | 441.9044374414444 | 1000 | 1104.761093603611 | KRANE TO REMOVE VEHICLE FROM REGULATOR STATION. | 6.64 | 7 | 5.63953488372093023255813953488372093023 | 0 | 0 | 307677 | 138025.024843373437213488372093023255814 | 339907.4852039067173002325581395348837209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 250 | 192.619(C) | 2014-09-12 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | YES | UNKNOWN | PASSENGER CAR | OFF-ROAD | 25 | YES | YES | [117 empty] | YES | [23 empty] | ANTHONY ENGLING | PIPE LINE SAFETY PROFESSIONAL | tony.engling@blackhillscorp.com | 5635854014 |  | ANTHONY ENGLING | tony.engling@blackhillscorp.com | 5635854014 | ANTHONY ENGLING |  | 5635854014 | tony.engling@blackhillscorp.com | DRIVER FELL ASLEEP AT THE WHEEL WHILE OPERATING A PRIVATE OWNED PASSENGER CAR. VEHICLE HIT THE REGULATOR STATION BARRICADES AND DAMAGED THE BARRICADES AND REGULATOR STATION. LEAKAGE WAS ON A .25 FITTING. GAS WAS NOT BLOWING.
2026-06-30 10:38 | NO | YES | YES | 20210063 | 35898 | 2021-07-14 15:56 | SUPPLEMENTAL | 18496 | SOUTHERN CONNECTICUT GAS CO | 60 MARSH HILL ROAD | ORANGE | CT | 06477 | 2021-06-07 08:59 | EASTERN | YES | 2021 | 500 BIC DRIVE BLDG #4 | MILFORD | NEW HAVEN | CT | 06461 | 41.2195 | -73.1006 |  |  | YES | [6 empty] | 2021-06-07 13:24 | 1307077 | 1307343 | NATURAL GAS |  | 38 | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | NO | [5 empty] | 0 | YES | 2021-06-07 08:59 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 17 | NO | 50 | 2021-06-07 09:16 |  |  |  | 2021-06-07 09:16 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1988 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | YES |  |  |  | STEEL |  | OTHER | SERVICE REGULATOR BODY | UNKNOWN | [6 empty] | OTHER | [8 empty] | THE SERVICE REGULATOR WAS DAMAGED BY BEING HIT BY A COMMERCIAL LAWN MOWER, BREAKING THE OPERATING DIAPHRAM OFF OF THE REGULATOR BODY EXPOSING THE REGULATOR ORIFICE RESULTING IN A LEAK. | CLASS 2 LOCATION | 35000 | 38666.638276126385 | 5000 | 5523.805468018055 | 5000 | 5523.805468018055 | 0 | 0 | THESE ARE ESTIMATES ONLY. ACTUAL COSTS NOT YET KNOWN. | 2 | 76 | 61.22923588039867109634551495016611295681 | 0 | 0 | 45076 | 20236.8188173255614950166112956810631229 | 49775.478448042893671096345514950166113 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 57 | 57 | 60 | 192.619(A)(2) | 1994-03-25 | PRESSURE DID NOT EXCEED MAOP | DRIP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS THE RESULT OF DAMAGE FROM A LAWWNMOWER BREAKING THE SERVICE REGULATOR ON THE RISER RESULTING IN A LEAK. NO CONTROL ROOM ACTIONS RESULTED IN THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | NO | [5 empty] | UNKNOWN | UNKNOWN | MOTORCYCLE/ATV | OFF-ROAD | 0 | NO | [142 empty] | KEVIN GERETY | MANAGER OF TECHNICAL SERVICES | kgerety@soconngas.com | 203-795-7767 | 203-795-7784 | JOE MASELLI | jmaselli@soconngas.com | 203-650-7665 | AL LANGLAND | VICE PRESIDENT | 203-257-5855 | al.langland@avangrid.com | AT 08:59 AM JUNE 7, 2021, SCG RECEIVED A CALL FROM THE MILFORD FIRE DEPARTMENT REGARDING A GAS FIRE INVOLVING A VEHICLE AT 500 BIC DRIVE BUILDING #4 IN MILFORD. SCG FIRST RESPONDERS WERE INFORMED THAT A COMMERCIAL TYPE LAWN MOWER HAD STRUCK THE GAS SERVICE REGULATOR TO THE ADDRESS RESULTING IN A GAS LEAK AND FIRE. THE FIRE DEPARTMENT REPORTED THAT APPROXIMATELY 50 OCCUPANTS OF THE BUILDING WERE EVACUATED. THE FIRE WAS EXTINGUISHED BY THE MILFORD FIRE DEPARTMENT. THE GAS WAS SHUT OFF TO THE BUILDING BY SCG. THE OPERATOR OF THE LAWNMOWER SUSTAINED BURNS FROM THE GAS FIRE, AND WAS TAKEN TO THE HOSPITAL. SCG HAS LEARNED THAT THE OPERATOR OF THE LAWNMOWER DIED OF HIS INJURIES ON JULY 2, 2021. THIS SUPPLEMENTAL REPORT UPDATES THE NUMBER OF FATALITIES FROM "0" TO "1" TO REFLECT THE DEATH OF THE LAWNMOWER OPERATOR.
2026-06-30 10:38 | NO | YES | YES | 20210064 | 35952 | 2021-07-22 10:37 | SUPPLEMENTAL FINAL | 766 | ATHENS GAS DEPARTMENT | 1806 WILKINSON STREET | ATHENS | AL | 35611 | 2021-07-10 08:10 | EASTERN | YES | 2021 | 27667 KAYLYN CIRCLE | HARVEST | LIMESTONE | AL | 35749 | 34.7706 | -86.8296 |  | YES |  |  |  | YES |  |  |  | 2021-07-10 14:18 | 1310312 | 1310316, 1310364,1310426,1310435 | NATURAL GAS |  | 210 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2021-07-10 08:10 | OTHER | VALVE LINE OFF ON ONE END OF FEED AND SQUEEZED OFF OTHER END OF FEED. | 210 | NO | 0 | 2021-07-10 08:21 |  |  |  | 2021-07-10 08:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 26 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1998 | 1998 |  |  |  |  | 2 | ASTMD 2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 0.8 | 0.8 | [7 empty] | CLASS 3 LOCATION | 30000 | 33142.83280810833 | 1500 | 1657.1416404054165 | 3240 | 3579.42594327569964 | 0 | 0 |  | 3.79 | 796 | 641.295681063122923588039867109634551495 | 0 | 0 | 35536 | 16106.6190771414464309634551495016611296 | 39020.6960728525690635880398671096345515 | 0 | 0 | 21 | 0 | 1 | 21 | 0 | 36 | 36 | 75 | 192.619(A)(2) | 1998-10-27 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | YES | [9 empty] | CONTRACTOR | TRENCHER | LANDSCAPING | YES | 211880359 |  |  | UTILITY OWNER | NO | YES | 4 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | STEVE CARTER | MANAGER | scarter@athens-utilities.com | 2562338016 | 2562621432 | STEVE CARTER | scarter@athens-utilities.com | 2567596971 | STEVE CARTER | MANAGER | 2567596971 | scarter@athens-utilities.com | CONTRACTOR DID NOT REQUEST LOCATE HOMEOWNER DID FOR LANDSCAPING AND REQUEST FOR ENTIRE AREA LOCATOR INDETIFIED AND LOCATED SERVICE TO HOUSE BUT FAILED TO LOCATE MAIN IN EASEMENT. DRAINAGE WORK WAS BEING PERFORMED BY WALK BEHIND TRENCHER ON THE RIGHT-AWAY OR UTILITY EASEMENT. CONTRACTOR HIT 2 INCH PE GAS LINE AND IT IGNITED. CONTRACTOR WAS BURNED AND SENT TO HOSPITAL. GAS DEPARTMENT EMPLOYEES ARRIVED AND AFTER ACCESSING THE SITUATION ACTIVATED THE EMERGENCY PLAN AND INFORMED SUPERVISOR WHOM IN RETURN CALLED OTHER CREWS IN TO HELP AND GAS DEPARTMENT MANAGER . THE SUPERVISOR AND MANAGER DECIDED IT WAS BEST TO LET THE GAS STAY BURNING AS NO MORE DAMAGE WAS OCCURRING AND WE KNEW THE GAS WAS BEING CONSUMED BY THE FIRE. THIS CONTINUED UNTIL WE TURNED VALVE OFF TO ONE FEED AND THEN SQUEEZED OFF THE OTHER. THE EAST LIMESTONE VOLUNTEER FIRE DEPARTMENT STYED UNTIL THIS WAS ACCOMPLISHED.
2026-06-30 10:38 | NO | NO | NO | 20210066 | 35563 | 2021-08-02 17:28 | SUPPLEMENTAL FINAL | 2128 | CASCADE NATURAL GAS CORP | 8113 W. GRANDRIDGE BLVD | KENNEWICK | WA | 99336 | 2021-07-08 16:00 | PACIFIC | YES | 2021 | INTERSECTION OF FOSTER WELLS RD AND CAPITOL AVE | PASCO | FRANKLIN | WA | 99301 | 46.2832 | -119.0878 | [6 empty] | YES |  |  | 2021-07-08 16:10 | 1310098 | 1310225 | NATURAL GAS |  | 6637 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-07-08 11:57 | YES | OPERATOR | 2021-07-08 11:57 | 2021-07-08 11:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 84 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1958 | UNKNOWN |  |  |  |  | 8 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 2 | 6 | [7 empty] | CLASS 1 LOCATION | 4000 | 4419.044374414444 | 8000 | 8838.088748828888 | 17000 | 18780.938591261387 | 0 | 0 |  | 4.5 | 29867 | 24062.2840531561461794019933554817275748 | 0 | 0 | 58867 | 32606.4868184890975481727574750830564784 | 56100.3557676608651794019933554817275748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 185 | 200 | 192.619(A)(3) | 2021-04-05 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PUNCTURE WAS NOT IDENTIFIED VIA SCADA DUE TO OPERATOR PERSONNEL ON SITE WHEN THE LINE WAS PUNCTURED. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 21275913 |  |  | UTILITY OWNER | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | GREG WATKINS | MANAGER POLICY AND PROCEDURE | greg.watkins@mdu.com | 208-377-6032 |  | GREG WATKINS | greg.watkins@mdu.com | 208-377-6032 | GREG WATKINS | MANAGER POLICY AND PROCEDURE | 208-377-6032 | greg.watkins@mdu.com | AT 11:57 A.M. PST ON JULY 8, 2021, A THIRD PARTY EXCAVATOR WAS CROSSING AN EXPOSED 8" PIPELINE. WHILE TUNNELING UNDER THE EXPOSED PIPELINE WITH AN EXCAVATOR, THE 3RD PARTY EXCAVATOR STRUCK THE 8" PIPELINE. THE LINE STRIKE RESULTED IN A 2" BY 6" HOLE IN THE PIPELINE. CNG PERSONNEL USED EXISTING LINE STOPPER FITTINGS (STOPPLE FITTINGS) TO CONTROL THE RELEASE WHICH ALLOWED THE TEMPORARY INSTALLATION OF A PLIDCO CLAMP. THE PERMANENT REPAIR WAS COMPLETED AT 4:15 P.M. PST ON 7/14/2021. PER §192.5 CLASS LOCATIONS, THIS LINE STRIKE OCCURRED IN A CLASS 1 LOCATION. PER INTERNAL PROCEDURES, ALL DISTRIBUTION PIPELINES (LESS THAN 20% SMYS) ARE CLASSIFIED AS CLASS 3, UNLESS LOCATED IN A CLASS 4 LOCATION. APRIL 5, 2021 (PART E 3.B DATE MAOP ESTABLISHED:) IS THE DATE THIS PIPELINE WAS DOWNRATED TO A 200 PSIG MAOP.
2026-06-30 10:38 | NO | NO | NO | 20210068 | 35648 | 2021-08-11 08:08 | SUPPLEMENTAL FINAL | 7348 | DOMINION ENERGY WEST VIRGINIA | 781 CHESTNUT RIDGE RD | MORGANTOWN | WV | 26505 | 2021-07-25 11:58 | EASTERN | YES | 2021 | 286 DAVIDSON DR | GLENVILLE | GILMER | WV | 26351 | 38.9486 | -80.8723 |  | YES | [7 empty] | 2021-07-25 12:42 | 1311734 | 1311886 | NATURAL GAS |  | 613.935 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-07-24 20:30 | OPERATOR/CONTRACTOR |  | 613 | NO | 0 | 2021-07-24 21:43 | YES | OPERATOR | 2021-07-25 12:50 | 2021-07-25 00:45 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2002 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | MECHANICAL PUNCTURE | 4 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1574 | 1738.893961332083714 | 0 | 0 | 0 | 0 |  | 2.46 | 1510 | 1216.528239202657807308970099667774086379 | 0 | 0 | 3084 | 1696.875441739357738777408637873754152824 | 2955.422200534741521308970099667774086379 | 0 | 0 | 4 | 1 | 0 | 4 | 0 | 20 | 20 | 60 | 192.619(A)(2) | 2002-11-13 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | DATA NOT COLLECTED | TRENCHER | ELECTRIC | YES | 2119188442 |  |  | UTILITY OWNER | YES | YES | 5 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CALEB GALL | DOT COMPLIANCE ANALYST | caleb.i.gall@dominionenergy.com | 3046278824 |  | CALEB GALL | caleb.i.gall@dominionenergy.com | 3046278824 | CAROL HAGER | MANAGER - GAS OPERATIONS PIPELINE INTEGRITY | 3304379557 | carol.m.hager@dominionenergy.com | AT APPROXIMATELY 21:43 ON 7/24/21, PROPERTY OWNER/CUSTOMER CALLED DEWV DISPATCH CENTER STATING LINE HAD BEEN STRUCK WITH TRENCHER AND HAD IGNITED DUE TO EQUIPMENT STALLING AND THEN THE EQUIPMENT OPERATOR TRYING TO RE-START THE MACHINE. THE EXCAVATION WAS BEING PERFORMED BY A FRIEND/HELPER OF THE PROPERTY OWNER/CUSTOMER. AT A LATER TIME, DEWV WAS INFORMED THAT THE EQUIPMENT OPERATOR HAD RECEIVED FLASH BURNS TO HIS ARMS AND FACE AND REQUIRED MEDICAL ATTENTION. THE PERSON INJURED RECEIVED MEDICAL TREATMENT AND WAS RELEASED SHORTLY AFTER AND DID NOT REQUIRE IN-PATIENT HOSPITALIZATION. DEWV INVESTIGATED AND DETERMINED THAT THERE WAS AN 811 EXCAVATION TICKET CALLED IN. DEWV ALSO DETERMINED THAT THE LINE HAD BEEN CORRECTLY LOCATED AND EXCAVATION PRACTICES WERE INSUFFICIENT BY THE EQUIPMENT OPERATOR, RESULTING IN THE LINE BEING STRUCK AND SUBSEQUENTLY IGNITING.
2026-06-30 10:38 | NO | YES | NO | 20210069 | 36093 | 2021-08-12 13:40 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2021-07-16 14:14 | EASTERN | YES | 2021 | 10385 HICKORY FLAT HIGHWAY | WOODSTOCK | CHEROKEE | GA | 30188 | 34.1232 | -84.392 | YES |  |  |  |  | YES |  |  |  | 2021-07-21 10:38 | 1311350 | 1311561 | NATURAL GAS |  | 4900 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-07-16 14:14 |  |  |  | 2021-07-16 14:33 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 111 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1979 | UNKNOWN |  |  |  |  | 2 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.154 | [6 empty] | MECHANICAL PUNCTURE | 3 | 0.5 | [7 empty] | CLASS 3 LOCATION | 100000 | 110476.1093603611 | 20000 | 22095.22187207222 | 20000 | 22095.22187207222 | 0 | 0 |  | 3.57 | 17493 | 14093.1976744186046511627906976744186047 | 0 | 0 | 157493 | 74281.8148735399897674418604651162790698 | 168759.7507789241446511627906976744186047 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 190 | 230 | 300 | 192.619(A)(2) | 1979-08-08 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 11.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | BORING | SEWER (SANITARY/STORM) | YES | 210428001007 |  |  | CONTRACT LOCATOR | YES | YES | 12 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A 2-INCH STEEL NATURAL GAS MAIN WAS RUPTURED NEAR ITS TAP ON A 4-INCH STEEL MAIN BY A T&J INDUSTRIES CONTRACT CREW WHILE INSTALLING SEWER MAIN BY BORING. ONCE THE INCIDENT WAS MADE SAFE AND THE COSTS ASSOCIATED WITH THE INCIDENT WAS BEING TALLIED IT WAS DETERMINED THAT REQUIRED MILLING AND RESURFACING REPAIRS TO THE HIGHWAY BY THE LOCAL GOVERNMENT, REPAIRS TO THE AFFECTED PIPELINE AND EMERGENCY RESPONSE WOULD EXCEED THE $122,000 THRESHOLD FOR REPORTING WHERE THE TIMELINE FOR QUESTION A4 WAS MET ABOVE AND THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. NOTIFICATION TO THE ONE-CALL CENTER WAS MADE WHERE THE MAIN WAS CORRECTLY LOCATED, HOWEVER, THE EXCAVATOR FAILED TO ATTEMPT TO POTHOLE WHERE THE FACILITY WAS MARKED AND DAMAGED. ADDITIONAL NRC REPORT NUMBER 1311561 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2026-06-30 10:38 | NO | YES | YES | 20210070 | 36310 | 2021-08-13 15:40 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2021-07-07 10:13 | EASTERN | NO | 2021 | 14360 CORNELL TAYLOR | TAYLOR | WAYNE | MI | 48180 | 42.2023 | -83.2657 | [7 empty] | YES | EXPANSION STOPPER | 2021-07-07 11:24 | 1309932 | 1310302 | NATURAL GAS |  | 3.5 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2021-07-07 09:30 | OPERATOR/CONTRACTOR |  | 3.5 | NO | 0 | 2021-07-07 10:13 |  |  |  | 2021-07-07 10:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | YES | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | SERVICE TEE | 1959 | UNKNOWN | [7 empty] | STEEL |  | OTHER | CAST FITTING | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | 3/4INCH SERVICE TEE BROKEN OFF | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 1800 | 1988.5699684864998 | 243 | 268.456945745677473 | 0 | 0 |  | 2.53 | 9 | 7.25083056478405315614617940199335548173 | 0 | 0 | 2052 | 922.392923143789794199335548172757475083 | 2264.277744796961326156146179401993355482 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 10 | 10 | 10 | 192.619(A)(1) | 1959-09-04 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | NO | YES | OTHER | [12 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | B11400158 | N/A |  | FACILITY OWNER | YES | YES | 8 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | FRENAE F SMITH | MANAGER OF CODES AND STANDARDS | frenae.smith@dteenergy.com | 13134601681 |  |  |  |  | FRENAE F SMITH | MANGER OF CODES AND STANDARD | 13134601681 | frenae.smith@dteenergy.com | ON WEDNESDAY, JULY 7, 2021, AT APPROXIMATELY 9:30 AM A GENERAL FITTER (GF) WAS EXCAVATING A 3/4-INCH STEEL GAS SERVICE LINE IN A CUSTOMER'S LAWN TO COMPLETE A SERVICE RENEWAL. DURING THE COURSE OF THE WORK ACTIVITIES, THE 3/4-INCH STEEL GAS SERVICE LINE WAS BROKEN AT THE 3/4-INCH OUTLET OF THE SERVICE TEE, AND A 240 VOLT ENERGIZED ELECTRIC CABLE SUPPLYING STREET LAMPS WAS SEVERED. IT IS BELIEVED THAT THE SEVERED ELECTRICAL CABLES SERVED AS AN IGNITION SOURCE, IGNITING THE GAS WITHIN THE EXCAVATION. DURING THE RESULTING FIRE, THE GF SUFFERED INJURIES TO THE EXTENT THAT EMS RESPONDED AND TRANSPORTED THE EMPLOYEE TO THE HOSPITAL FOR TREATMENT. THE ROOT CAUSE IS THAT GENERAL FITTER AND FITTER FAILED TO FOLLOW THE PROCEDURE AND HAVE SEPARATED FROM THE COMPANY. SPECIFICALLY, FAILURE TO FOLLOW DISTRIBUTION & TRANSMISSION PROCEDURE(D&TP) 1.1 "PREVENTING ACCIDENTAL IGNITION", D&TP1.6 "ENERGY GAS EXCAVATION AND CONFINED SPACE ENTRY," AND D&TP 4.6 "IDENTIFYING AND PROTECTING UNDERGROUND UTILITIES, CONDUITS, AND STRUCTURES."
2026-06-30 10:38 | NO | YES | YES | 20210072 | 36946 | 2021-08-17 13:29 | SUPPLEMENTAL FINAL | 12878 | MOUNTAINEER GAS CO | 501 56TH ST. SE | CHARLESTON | WV | 25304 | 2021-07-18 16:51 | EASTERN | YES | 2021 | 103 BEAVER PLAZA | BEAVER | RALEIGH | WV | 25813 | 37.75 | -81.1375 |  | YES | [7 empty] | 2021-07-18 17:59 | 1311101 | 1311291 | NATURAL GAS |  | 2 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2021-07-18 16:51 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 0 | 2021-07-18 16:51 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-07-18 16:51 | 2021-07-18 16:51 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 38 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1983 | 1978 |  |  |  |  | 4 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2306 | MECHANICAL PUNCTURE | 3 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 111 | 122.628481390000821 | 626 | 691.580444595860486 | 0 | 0 | 0 | 6.739 | 13 | 10.47342192691029900332225913621262458472 | 0 | 0 | 750 | 339.147309411520899621262458471760797342 | 824.682347912771606003322259136212624585 | 15 | 0 | 0 | 0 | 1 | 0 | 15 | 35 | 35 | 44 | 192.619(A)(4) | 1998-06-23 | PRESSURE DID NOT EXCEED MAOP | NONE |  | 0 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2021-05-03 | NO | [12 empty] | NO | [7 empty] | YES | [6 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | DRAINAGE | NO | [5 empty] | UNKNOWN/OTHER |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [152 empty] | YES | [17 empty] | PHILIP KINGREY | MANAGER ENGINEERING | philipkingrey@mgcwv.com | 8884204427 | 3049259605 | PAUL THURBON | paulthurbon@mgcwv.com | 8884204427 | THOMAS WESTFALL | VICE PRESIDENT GAS SUPPLY AND TECHNICAL SERVICES | 8884204427 | thomaswestfall@mgcwv.com | AT 16:20 JULY 18, 2021, OPERATOR'S DISPATCH CENTER RECEIVED AN ODOR OF GAS CALL FROM 123 BEAVER PLAZA, A UNITED STATES POST OFFICE SERVING THE COMMUNITY OF BEAVER, RALEIGH COUNTY, W.VA. A FIRST RESPONDER WAS DISPATCHED. AT 16:51, RALEIGH COUNTY EMERGENCY SERVICES NOTIFIED OPERATOR'S DISPATCH CENTER OF A REPORTED EXPLOSION AT 103 BEAVER PLAZA. AN OPERATIONS MANAGER ALSO WAS DISPATCHED. OPERATOR'S EMPLOYEES NOTED THAT A STRUCTURE AT 103 BEAVER PLAZA WAS VISIBLY DAMAGED. EMERGENCY RESPONDERS INFORMED OPERATOR'S EMPLOYEES THAT ONE PERSON WAS INJURED AND HAD BEEN AIRLIFTED TO CABELL-HUNTINGTON HOSPITAL. AN ODOR OF GAS WAS DETECTED AT A NEARBY SEWER MANHOLE. OPERATOR'S EMPLOYEES ALSO CHECKED NEARBY BUSINESSES FOR GAS WITH CONSISTENTLY NEGATIVE RESULTS. THERE ARE TWO BUILDINGS LOCATED AT 103 BEAVER PLAZA. THE DAMAGED BUILDING IS LOCATED ON THE SOUTHERN SIDE OF THE PROPERTY AND HOUSES A GAMBLING ESTABLISHMENT. A SECOND BUILDING IS LOCATED ON THE NORTHERN SIDE OF THE PROPERTY AND HOUSES ONLY TWO RESTROOMS, BUT AT THE TIME OF THE INCIDENT WAS BOARDED UP. OPERATOR HAS A 4-INCH MEDIUM-PRESSURE PLASTIC GAS DISTRIBUTION MAIN IN AN EASEMENT IMMEDIATELY NORTH OF THE SECOND BUILDING. OPERATOR'S EMPLOYEES CHECKED NEARBY SEWER MANHOLES AND DETERMINED THAT GAS WAS PRESENT IN THE AREA OF THE SECOND BUILDING. EMPLOYEES BEGAN EXCAVATING THE MAIN TO DETERMINE THE SOURCE OF THE LEAK. WHEN THE MAIN WAS EXPOSED, A SEWER CONNECTION FOR THE SECOND BUILDING WAS FOUND DIRECTLY OVER THE MAIN. CONCRETE HAD BEEN POURED OVER THE SEWER CONNECTION. OPERATOR'S EMPLOYEES DISCOVERED A GOUGE IN THE MAIN. A CLAMP WAS FOUND COVERING THE GOUGE. FASTENINGS ON THE CLAMP WERE CORRODED. THE DAMAGED SECTION OF MAIN AND THE CLAMP WERE RECOVERED AND ARE BEING PRESERVED. PRIOR TO THE COMPLETION OF WORK AT THE SITE, OPERATOR'S EMPLOYEES PERFORMED AN ODORIZATION READ, SHOWING A .30 AVERAGE THRESHOLD, .51 READILY DETECTABLE. THE ANSWERS TO THE FOLLOWING QUESTIONS HAVE BEEN PROVIDED PROVISIONALLY USING GUIDANCE RECEIVED ON AUGUST 16, 2021 FROM MARY FRIEND, DIRECTOR OF GAS PIPELINE SAFETY AT THE PUBLIC SERVICE COMMISSION OF WEST VIRGINIA DUE TO RECOGNIZED PROGRAMMING ERRORS IN THE PHMSA PORTAL USED TO SUBMIT THIS REPORT: A7, A8, A21C, A22, D2A, D2B, D2C, D2D, D2E, D2F, D2G, D2H, D2I, E6.
2026-06-30 10:38 | NO | YES | YES | 20210073 | 38344 | 2021-08-28 16:33 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2021-07-29 10:45 | CENTRAL | YES | 2021 | 826 SOUTH HOPKINS ST. | NEW IBERIA | IBERIA | LA | 70560 | 30.006 | -91.8321 | [5 empty] | YES |  |  |  | 2021-07-29 11:39 | 1312130 | 1312139, 1312341 | NATURAL GAS |  | 12 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 2 | 0 | 0 | 2 | YES | 2021-07-29 09:58 | OTHER | FIRE DEPT. EXTINGUISHED FIRE AND OPERATOR SQUEEZED PIPE AND INSTALLED STOPPLE FITTINGS. | 7.2 | NO | 6 | 2021-07-29 10:09 | YES | OPERATOR | 2021-07-29 09:59 | 2021-07-29 10:20 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 42 | YES | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1938 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO | 1 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.14 | [6 empty] | OTHER | [8 empty] | GOUGE AND DEFORMATION OF PIPE BY CONTRACTOR. | CLASS 3 LOCATION | 40000 | 44190.44374414444 | 11686 | 12910.238139851798146 | 141 | 155.771314198109151 | 0 | 0 |  | 5.7 | 68 | 54.78405315614617940199335548172757475083 | 0 | 0 | 51895 | 23294.1545214104905541727574750830564784 | 57311.2372513504934764019933554817275748 | 1 | 0 | 0 | 1 | 0 | 3 | 2 | 35 | 35 | 60 | 192.619(A)(4) | 1999-01-11 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 7 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | NATURAL GAS | YES | 210441819 |  |  | CONTRACT LOCATOR | YES | YES | 10 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | JAMES TODD HEBERT | OPERATIONS SPECIALIST | james.hebert@centerpointenergy.com | 337-256-2161 | 337-373-1520 | JAMES TODD HEBERT | james.hebert@centerpointenergy.com | 337-256-2161 | BLAINE SPELL | DISTRICT OPERATIONS MANAGER | 337-475-6377 | blaine.spell@centerpointenergy.com | THE INVESTIGATION TO DATE INDICATES THAT LINE LOCATES WERE OBTAINED AND A PRE-BORE VERIFICATION POTHOLE WAS DUG AT THE SUBJECT LOCATION BY THE CONTRACTOR ON JULY 15, 2021, AT WHICH TIME THE DEPTH OF THE SERVICE LINE WAS OBSERVED AND RECORDED; THE CONTRACTOR BACKFILLED THE POTHOLE BEFORE THE CONTRACTOR CONDUCTED THE DIRECTIONAL BORE OPERATION ON THE AFTERNOON OF JULY 28, 2021. THERE WAS NO INDICATION OF DAMAGE TO THE GAS SERVICE LINE AT THE SCENE OF THE INCIDENT BEFORE THE PULL-BACK OPERATION ON THE MORNING OF JULY 29, 2021. AS INDICATED IN PART A.11, OPERATOR'S INITIAL INDICATION OF THE FAILURE WAS FROM INFORMATION SUPPLIED BY CONTRACTOR PERSONNEL. PART A.12 OF THIS REPORT DOES NOT ALLOW FOR AN EXPLANATION. THE CONTRACTOR PERSONNEL IDENTIFIED DAMAGE TO THE GAS LINE AND THE ODOR OF GAS AT 9:59 A.M. ON JULY 29, 2021. CONTRACTOR PERSONNEL CALLED 911 AT 9:59 AM. WITHIN MINUTES OF THE ARRIVAL OF THE FIRST RESPONDING POLICE OFFICER, CONTRACTOR PERSONNEL INFORMED THE POLICE OFFICER THAT A GAS LINE HAD BEEN HIT. BOTH OF THESE COMMUNICATIONS TO 911 AND TO THE POLICE OFFICER OCCURRED BEFORE CENTERPOINT WAS NOTIFIED OF THE INCIDENT. PART A.14 DOES NOT PROVIDE THE OPTION TO INCLUDE THE CONTRACTOR AS HAVING PROVIDED THAT INFORMATION TO LOCAL EMERGENCY RESPONDERS. THE TIME INDICATED IN PART A.15 OF THE COMMUNICATION TO EMERGENCY RESPONDERS WAS BY THE CONTRACTOR. THE TIME INSERTED IN PART A.4 AS THE EARLIEST LOCAL TIME THAT INCIDENT REPORTING CRITERIA WAS MET WAS DETERMINED BASED UPON THE POSSIBILITY OF PROPERTY DAMAGES EXCEEDING THE REPORT CRITERIA AMOUNT, AT WHICH TIME CENTERPOINT DID NOT HAVE ACCURATE INFORMATION ABOUT THE AMOUNT OF PROPERTY DAMAGE OR INJURIES REQUIRING HOSPITALIZATION. THE INITIAL VISUAL EXAMINATION OF THE SERVICE LINE AFTER THE INCIDENT AT THE SITE REVEALED THAT THE STEEL SERVICE LINE APPEARED TO HAVE BEEN GOUGED AND DEFORMED BY DIRECTIONAL BORING EQUIPMENT. THE DAMAGED SERVICE LINE PIPE WAS REMOVED FROM THE SCENE AND WAS EXAMINED AS PART OF A JOINT INSPECTION AT A METALLURGICAL LABORATORY. THE EXAMINATION CONFIRMED THAT THE STEEL SERVICE LINE WAS GOUGED BY THE DIRECTIONAL BORE DRILL BIT ON JULY 28. THE FAILURE ANALYSIS OF THE PIPE INDICATED THAT THE BREACH OCCURRED AS A RESULT OF A SINGLE EVENT DUCTILE OVERLOAD DUE TO CONTACT BETWEEN THE PIPE AND THE EQUIPMENT USED DURING THE PULL-BACK OF THE NEWLY INSTALLED POLY PIPE ON JULY 29. NO EVIDENCE WAS FOUND TO INDICATE THAT THE STEEL SERVICE LINE LEAKED AT THE LOCATION OF THE ULTIMATE BREACH BEFORE THE DIRECTIONAL DRILLING AND PULL-BACK OPERATION. THERE WAS NO EVIDENCE OF ANY CORROSION OR PIPE MATERIAL DEFICIENCY THAT CONTRIBUTED TO THE ULTIMATE BREACH OF THE PIPE. IN REFERENCE TO PART F QUESTION 2, ONLY 1 CONTRACTOR EMPLOYEE WAS DOT DRUG AND ALCOHOL TESTED. WITHIN 5 HOURS OF THE INCIDENT, OPERATOR DIRECTED BOTH CONTRACTOR COMPANIES TO PERFORM DOT DRUG AND ALCOHOL TESTING OF THEIR EMPLOYEES INVOLVED IN THE OPERATION. THE SOLE MAGNOLIA RIVER EMPLOYEE INVOLVED IN THE OPERATION SUBMITTED FOR THE APPROPRIATE TESTING, AND THE RESULTS WERE NEGATIVE. SUBSEQUENT TO ITS INITIAL DIRECTION TO MDR GROUP CONSTRUCTION REGARDING TESTING REQUIREMENTS, OPERATOR LEARNED THAT THE TESTING FACILITY CHOSEN BY MDR GROUP CONSTRUCTION WAS CLOSED, AND IT USED AN ALTERNATIVE FACILITY. OPERATOR LEARNED BEYOND THE TESTING WINDOW THAT THE ALTERNATIVE FACILITY DID NOT ADMINISTER ALCOHOL TESTING TO ANY OF THE MDR GROUP CONSTRUCTION EMPLOYEES DURING THE PRESCRIBED TESTING WINDOW. THE DRUG TESTS FOR THE MDR GROUP CONSTRUCTION EMPLOYEES WERE NEGATIVE.
2026-06-30 10:38 | YES | NO | NO | 20210074 | 36094 | 2021-08-30 21:09 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2021-08-04 21:52 | EASTERN | YES | 2021 | 2124 CHESHIRE BRIDGE ROAD NE | ATLANTA | FULTON | GA | 30324 | 33.8131 | -84.3542 | [5 empty] | YES |  |  |  | 2021-08-05 06:35 | 1312852 | 1313055 | NATURAL GAS |  | 6690 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-08-04 21:52 | OPERATOR/CONTRACTOR |  | 6690 | NO | 50 | 2021-08-04 22:08 |  |  |  | 2021-08-04 22:36 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | YES | YES | CASED | [9 empty] | INVESTOR OWNED |  | MAIN |  | 2021 | 2020 |  |  |  |  | 4 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2708 | OTHER | [8 empty] | ENCASED 4-INCH PLASTIC MAIN MELTED DUE TO EXTERNALLY APPLIED HEAT FROM AN UNCONTROLLED FIRE. | CLASS 3 LOCATION | 10200000 | 11268563.1547568322 | 86000 | 95009.454049910546 | 15000 | 16571.416404054165 | 0 | 0 |  | 3.93 | 26292 | 21182.093023255813953488372093023255814 | 0 | 0 | 10327292 | 4638268.94070272818730232558139534883721 | 11401326.11823405272495348837209302325581 | 41 | 0 | 0 | 0 | 0 | 0 | 41 | 45 | 45 | 60 | 192.619(A)(2) | 2021-02-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 5.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | 4045843733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | 4045844910 | rslagle@southernco.com | THE COMPANY'S 24/7 EMERGENCY CALL CENTER RECEIVED A LEAK CALL FROM FULTON COUNTY EMERGENCY COMMUNICATIONS ADVISING THAT THE CITY OF ATLANTA'S FIRE DEPARTMENT RESPONDED TO A FIRE THAT ORIGINATED UNDERNEATH A BRIDGE ALONG CHESHIRE BRIDGE ROAD AT SOUTH FORK PEACHTREE CREEK. THE FIRE CONSISTED OF BURNING WOODEN PALLETS, MATTRESSES AND OTHER TYPES OF FURNITURE AND ITEMS THAT APPEAR TO HAVE ACCUMULATED FROM PERSONS LIVING UNDERNEATH THE BRIDGE. UPON INVESTIGATION, IT WAS DETERMINED THAT HEAT FROM THIS FIRE DAMAGED A 4-INCH PE PLASTIC ONE-WAY FEED MAIN INSERTED INTO A 16-INCH STEEL CASING, CAUSING IT TO FAIL. ONCE THE INCIDENT WAS MADE SAFE IT WAS DETERMINED THAT COSTS ASSOCIATED WITH THE INCIDENT WOULD EXCEED THE $122,000 THRESHOLD FOR REPORTING WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. THE ATLANTA DEPARTMENT OF TRANSPORTATION HAS DETERMINED THAT THE STRUCTURAL INTEGRITY OF THE BRIDGE HAS BEEN COMPROMISED AND THE BRIDGE WILL NEED TO BE REPLACED. ADDITIONAL NRC REPORT NUMBER 1313055 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2026-06-30 10:38 | NO | YES | YES | 20210075 | 36353 | 2021-09-02 11:39 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2021-08-03 13:00 | EASTERN | YES | 2021 | 3645 E 57TH STREET | CLEVELAND | CUYAHOGA | OH | 44105 | 41.4591 | -81.6496 |  |  | YES | [6 empty] | 2021-08-03 14:43 | 1312652 | 1312859 | NATURAL GAS |  | 5.125 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 2021-08-03 13:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 5 | YES | 3 | 2021-08-03 14:00 |  |  |  | 2021-08-03 14:12 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1961 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | UNDETERMINED. | [5 empty] | CLASS 3 LOCATION | 500000 | 552380.5468018055 | 5000 | 5523.805468018055 | 5000 | 5523.805468018055 | 0 | 0 |  | 5.248 | 27 | 21.75249169435215946843853820598006644518 | 0 | 0 | 510027 | 228803.1686340086338205980066445182724252 | 563449.9102295359621594684385382059800664 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0.44 | 0.44 | 1 | 192.623 | 1960-05-13 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  | YES |  |  |  | YES | AQUEOUS |  |  | YES | YES |  |  | NO | [11 empty] | NO | N/A Bare/Ineffectively Coated Pipe | NONE |  | UNKNOWN | [19 empty] | 2019-07-05 | NO | [227 empty] | CAROL HAGER | MANAGER COMPLIANCE AND INTEGRITY | carol.m.hager@dominionenergy.com | 330-437-9557 |  | CAROL HAGER | carol.m.hager@dominionenergy.com | 330-437-9557 | CAROL HAGER | MANAGER COMPLIANCE AND INTEGRITY | 330-437-9557 | carol.m.hager@dominionenergy.com | ON 8-3-21, AT APPROX. 1:00 PM, AN EXPLOSION AND FIRE OCCURRED AT A RESIDENTIAL PROPERTY AT 3645 E.57TH ST, CLEVELAND, OHIO. TWO ADULT INDIVIDUALS WERE INSIDE THE STRUCTURE AT THE TIME OF THE INCIDENT AND SUBSEQUENTLY HOSPITALIZED. THE INCIDENT SEVERELY DAMAGED THE STRUCTURE AT 3645 E.57TH ST, WHICH WAS RAZED ON THE EVENING OF 8-3-21 BY CITY OF CLEVELAND CONTRACTORS. TWO NEIGHBORING STRUCTURES (3643 AND 3649 E.57TH ST) ALSO SUSTAINED DAMAGES. ON 8-3-21, AT APPROX. 2:00 PM, DOMINION ENERGY OHIO (DEO) RECEIVED A CALL FROM THE CITY OF CLEVELAND FIRE DEPARTMENT REPORTING THE INCIDENT. DEO FIRST RESPONDER ARRIVED AT APPROX. 2:12 PM AND STOPPED THE FLOW OF GAS TO 3645 E.57TH BY CLOSING THE SERVICE LINE CURB VALVE AT APPROX. 2:35 PM. DEO ALSO SHUT OFF THE FLOW OF GAS TO NEIGHBORING STRUCTURES (3643 AND 3649 E.57TH) BY CLOSING THE SERVICE LINE CURB VALVES. DEO BAR-HOLED ALONG THE MAINS ON BOTH SIDES OF E.57TH AND ALONG THE CUSTOMER SERVICE LINES AT 3633, 3639, 3642, 3643, 3644, 3645, 3646, 3649, 3653, AND 3659 E.57TH, AND 0% READINGS WERE FOUND. DEO LEAK SURVEYED ALONG E.57TH AS WELL AS E.54TH, E.55TH, AND E.59TH. NO LEAKS WERE DETECTED, WITH THE EXCEPTION OF A GRADE-TWO LEAK AT 3683 E.55TH. DEO PERFORMED ODORANT TESTING AT 3653 E.57TH, AND THE ODORANT WAS READILY DETECTIBLE AT 0.48%. ON 8-3-21, THE GAS METER, MANIFOLD, AND A SECTION OF SERVICE LINE PIPING WERE REMOVED FROM THE BASEMENT AT 3645 E.57TH. DEO PRESSURE TESTED THE REMAINING SERVICE LINE PIPING AT 3645 E.57TH AT 7 OZ (OPERATING PRESSURE) FOR 10 MIN. A PRESSURE DROP OF APPROX. 0.5 OZ WAS OBSERVED, BUT NO LEAKS WERE DISCOVERED. A SECTION CONTAINING THE CURB VALVE AND MAIN-TO-CURB TRANSITION WAS REMOVED, AND THE REMAINING SERVICE LINE WAS RE-TESTED AT 7 OZ FOR 10 MIN. A PRESSURE DROP OF APPROX. 0.5 OZ WAS OBSERVED. CITY CONTRACTORS RAZED THE STRUCTURE AT 3645 E.57TH THAT EVENING. ON 8-4-21, DEO EXCAVATED, EXPOSED, AND RE-TESTED THE REMAINING SERVICE LINE (APPROX. 24 FT) AT 7 OZ FOR 10 MIN. A PRESSURE DROP OF APPROX. 1 OZ WAS OBSERVED, BUT NO IDENTIFIABLE LEAKS WERE DISCOVERED. A CUT WAS MADE APPROX. 8 FT FROM THE END OF THE SERVICE LINE (CLOSEST TO THE MAIN), AND THE 8-FT SECTION WAS RE-TESTED AT 7 OZ FOR 10 MIN. A PRESSURE DROP OF SLIGHTLY LESS THAN 2 OZ WAS OBSERVED, BUT NO IDENTIFIABLE LEAKS WERE DISCOVERED. THE REMAINING 16-FT SECTION WAS RE-TESTED AT 7 OZ FOR 10 MIN, AND NO PRESSURE DROP WAS OBSERVED. THE GAS METER, MANIFOLD, AND SERVICE LINE SECTIONS WERE PRESERVED FOR LABORATORY INSPECTION AND TESTING. THREE APPLIANCES (FURNACE, WATER HEATER, AND STOVE/RANGE) AND MISCELLANEOUS HOUSE LINE PIPING ALSO WERE IDENTIFIED DURING THE CITY'S POST-DEMOLITION DEBRIS REMOVAL ON 8-5-21 AND 8-6-21. THESE ARTIFACTS WERE EXAMINED ON 9-17-21. THE 8-FT SECTION OF SERVICE LINE THAT PREVIOUSLY WAS TESTED ON 8-4-21 WAS FLOW RATE LEAK TESTED AT 7 OZ, AND NO MEASURABLE FLOW RATE WAS OBSERVED. THE SERVICE LINE SECTION FROM THE BASEMENT OF 3645 E.57TH WAS KINKED APPROX. 45 DEGREES BY THE CITY'S CONTRACTORS DURING ITS REMOVAL ON 8-3-21, AND A THROUGH-WALL CRACK WAS OBSERVED AT THE KINK. THE KINKED SERVICE LINE SECTION WAS EXAMINED ON 12-17-21, WHICH INCLUDED COMPUTED TOMOGRAPHY (CT) SCANNING. EVIDENCE OF EXTERNAL CORROSION AND THINNING OF THE PIPING WALL WAS OBSERVED IN THE AREA WHERE THE SERVICE LINE PASSED THROUGH THE FOUNDATION INTO THE BASEMENT, WHICH WOULD HAVE CAUSED IT TO BE LESS RESISTANT TO BENDING FORCES. THE CRACK AT THE KINK WAS VISUALLY EXAMINED, REVEALING THAT THE PIPING WALL WAS COLLAPSED INTO THE INTERIOR OF THE SERVICE LINE. FOR REPORTING PURPOSES, DEO CLASSIFIES THE APPARENT CAUSE OF THIS INCIDENT AS EXTERNAL CORROSION FAILURE (SEE PART G1), BUT THE ROOT CAUSE REMAINS UNKNOWN AND UNDETERMINED. A NATURAL GAS LEAK FROM EXTERNAL CORROSION ON THE SERVICE LINE INSIDE THE BASEMENT CANNOT BE RULED OUT AS A POSSIBLE FUEL SOURCE, BUT THE PHYSICAL EVIDENCE WAS COMPROMISED DURING POST-INCIDENT REMOVAL BY THE CITY'S CONTRACTORS.
2026-06-30 10:38 | YES | NO | NO | 20210076 | 35710 | 2021-09-03 09:55 | ORIGINAL FINAL | 2128 | CASCADE NATURAL GAS CORP | 8113 W. GRANDRIDGE BLVD | KENNEWICK | WA | 99336 | 2021-08-09 16:30 | PACIFIC | YES | 2021 | 312 REDWOOD PLACE | COLLEGE PLACE | WALLA WALLA | WA | 99324 | 46.0534 | -118.3788 | [5 empty] | YES |  |  |  | 2021-08-09 16:38 | 1313242 | 1313414 | NATURAL GAS |  | 34.83 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-08-09 14:18 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 34.83 | NO | 0 | 2021-08-09 14:18 |  |  |  | 2021-08-09 14:34 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1999 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | A SUSPECTED NON-JURISDICTIONAL GAS EXPLOSION OCCURRED IN AN ATTACHED GARAGE CAUSING THE WALL WHERE THE GAS METER SET ASSEMBLY WAS LOCATED TO CONTACT AND BREAK THE GAS METER SET ASSEMBLY. | CLASS 3 LOCATION | 212000 | 234209.351843965532 | 500 | 552.3805468018055 | 1500 | 1657.1416404054165 | 0 | 0 |  | 4.51 | 157 | 126.486710963455149501661129568106312292 | 0 | 0 | 214157 | 96103.1852934078049568106312292358803987 | 236545.3607421362091495016611295681063123 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 46 | 46 | 60 | 192.619(A)(2) | 1999-06-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.6 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | GREG WATKINS | MANAGER POLICY AND PROCEDURE | greg.watkins@mdu.com | 208-377-6032 |  | GREG WATKINS | greg.watkins@mdu.com | 208-377-6032 | GREG WATKINS | MANAGER POLICY AND PROCEDURE | 208-377-6032 | greg.watkins@mdu.com | ON AUGUST 9, 2021 AT 2:18 P.M. PST CASCADE NATURAL GAS CORPORATION WAS NOTIFIED OF A FIRE THAT CAUSED A SUSPECTED NON-JURISDICTIONAL GAS EXPLOSION IN AN ATTACHED GARAGE AT 312 REDWOOD PLACE IN COLLEGE PLACE, WA. THE EXPLOSION CAUSED THE OUTSIDE WALL OF THE GARAGE TO BREAK THE GAS METER SET ASSEMBLY UPSTREAM OF THE SERVICE REGULATOR CAUSING A RELEASE OF JURISDICTIONAL GAS THAT IGNITED AND SUBSEQUENTLY SPREAD TO THE ADJACENT HOUSE AT 322 REDWOOD PLACE (GAS SERVICE LINE ALSO INSTALLED IN 1999). THE FIRE AT 322 REDWOOD PLACE WAS IN THE AREA OF THE GAS METER SET ASSEMBLY WHICH MELTED CAUSING A SECOND RELEASE OF NATURAL GAS WHICH ALSO IGNITED. CASCADE NATURAL GAS CORPORATION CONSTRUCTION CREWS REMOTELY SECURED THE RELEASES BY PERFORMING A SQUEEZE-OFF OF THE 2 INCH HDPE MAIN SERVING THE SERVICE LINES TO 312 AND 322 REDWOOD PLACE.
2026-06-30 10:38 | NO | YES | NO | 20210077 | 36489 | 2021-09-08 17:46 | SUPPLEMENTAL FINAL | 21349 | VIRGINIA NATURAL GAS | 544 S. INDEPENDENCE BLVD | VIRGINIA BEACH | VA | 23452 | 2021-08-12 10:20 | EASTERN | YES | 2021 | INTERSECTION OF CEDAR ROAD AND WATERS ROAD | CHESAPEAKE | CHESAPEAKE | VA | 23322 | 36.7112 | -76.2734 | [5 empty] | YES |  |  |  | 2021-08-12 10:50 | 1313471 | 1313577 | NATURAL GAS |  | 10090.6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 100 | 2021-08-11 14:42 | YES | OPERATOR | 2021-08-11 15:01 | 2021-08-11 15:01 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 8 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 3 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 247458 | 273381.970700962370838 | 102179 | 112883.383783323368369 | 0 | 0 |  | 3.4182 | 34492 | 27788.4053156146179401993355481727574751 | 0 | 0 | 384129 | 179478.5770026438140032757475083056478405 | 414053.7597999003571471993355481727574751 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 53 | 53 | 60 | 192.619(A)(4) | 1985-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 100 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FAILURE WAS REPORTED BY A THIRD PARTY IMMEDIATELY FOLLOWING THE DAMAGE. THIS LEAK DID NOT CAUSE A PRESSURE REDUCTION WHICH WOULD HAVE BEEN IDENTIFIED VIA A SCADA MEASUREMENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | A120701656 |  |  | CONTRACT LOCATOR | NO | YES | 24 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | JONATHAN HEATH | DIRECTOR - COMPLIANCE AND SYSTEM INTEGRITY | jbheath@southernco.com | (757) 298-5729 |  | JONATHAN HEATH | jbheath@southernco.com | (757) 298-5729 | JONATHAN HEATH | DIRECTOR - COMPLIANCE AND SYSTEM INTEGRITY | 7572985729 | jbheath@southernco.com | DAMAGED LINE REPORTED BY 3RD PARTY CONTRACTOR (UTILITY CABLE) FOR THE INTERSECTION OF CEDAR RD & WATERS RD IN CHESAPEAKE VA. CONTRACTOR WAS USING HDD MACHINE FROM THE SW CORNER OF INTERSECTION TO THE NW CORNER TO INSTALL CONDUIT FROM VAULT TO VAULT. CONTRACTOR HAD VALID TICKET AND LOCATE CONTRACTOR MARKED WHAT THEY THOUGHT WAS THE 8 INCH STEEL MAIN. GIS DID NOT SHOW AN OFFSET IN ROADWAY WHERE THE HDD MACHINE STRUCK THE EIGHT INCH EPOXY COATED STEEL MAIN IN THE STREET.
2026-06-30 10:38 | NO | NO | NO | 20210078 | 37312 | 2021-09-14 16:26 | SUPPLEMENTAL FINAL | 15462 | PECO ENERGY CO | 2301 MARKET STREET, S9-1 | PHILADELPHIA | PA | 19103 | 2021-08-12 20:07 | EASTERN | YES | 2021 | 203 LANDOVER ROAD | BRYN MAWR | DELAWARE | PA | 19010 | 40.0144 | -75.3265 | [5 empty] | YES |  | YES | CAST IRON STOPPER FITTING | 2021-08-12 22:08 | 1313536 | 1313600 | NATURAL GAS |  | 7800 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-08-12 19:29 | YES | OPERATOR | 2021-08-12 21:15 | 2021-08-12 19:29 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO LOSS OF COVER |  | 39 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1924 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | OTHER | [8 empty] | EXCAVATION COLLAPSED, 22-FOOT SECTION OF CAST IRON MAIN SNAPPED OFF AND FELL INTO EXCAVATION | CLASS 3 LOCATION | 0 | 0 | 20000 | 22095.22187207222 | 5000 | 5523.805468018055 | 0 | 0 |  | 3.99 | 31122 | 25073.3720930232558139534883720930232558 | 0 | 0 | 56122 | 31635.5545662882872093023255813953488372 | 52692.3994331135308139534883720930232558 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 7 | 7 | 25 | 192.619(A)(4) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS ON A 7 PSIG SYSTEM THAT IS NOT MONITORED BY SCADA | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | EROSION OF SUPPORT DUE TO OTHER UTILITIES | OTHER OUTSIDE FORCE DAMAGE | EROSION OF SUPPORT DUE TO OTHER UTILITIES | OTHER OUTSIDE FORCE DAMAGE | EROSION OF SUPPORT | [112 empty] | EROSION OF SUPPORT DUE TO OTHER UTILITIES | [168 empty] | MATTHEW Y. MARINZOLI | MANAGER GAS STANDARDS COMPLIANCE AND REPORTING | matthew.marinzoli@exeloncorp.com | [5 empty] | MATTHEW Y. MARINZOLI | MANAGER GAS STANDARDS COMPLIANCE AND REPORTING | 267.533.1169 | matthew.marinzoli@exeloncorp.com | ON AUGUST 12, 2021 AT APPROXIMATELY 18:53, PECO RESPONDED TO ODOR CALLS RECEIVED NEAR 203 LANDOVER ROAD IN BRYN MAWR, PA. IT WAS DETERMINED THAT GAS WAS BLOWING UNDER A PLATED ROADWAY. THE PLATES WERE REMOVED BY PECO'S CONTRACTOR TO REVEAL THAT A TERRACOTTA SEWER HAD FAILED, CAUSING A WASHOUT AND A 22-FOOT SECTION OF CAST IRON MAIN TO SNAP OFF INTO THE EXCAVATION. THE MAIN WAS SQUEEZED OFF ON THE EAST SIDE (20:30), AND CAST STOPPER INSTALLED ON THE WEST SIDE (02:21 ON AUGUST 13) TO STOP THE FLOW OF GAS. LATER THAT MORNING THE PERMANENT REPAIR COMPLETED. THIS WAS A NEW 22' SECTION OF 6" HIGH DENSITY POLYETHYLENE PLASTIC JOINED BY 2 COUPLINGS (BETWEEN THE EXISTING PLASTIC ON THE EAST SIDE AND THE CAST IRON ON THE WEST SIDE).
2026-06-30 10:38 | NO | YES | NO | 20210079 | 35816 | 2021-09-17 14:47 | SUPPLEMENTAL FINAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2021-08-18 21:47 | EASTERN | NO | 2021 | 4626 RT. 49 | KNOXVILLE | TIOGA | PA | 16928 | 41.9541 | -77.4428 | YES | [8 empty] | 2021-08-19 09:59 | 1314130 | 1314244 | NATURAL GAS |  | 11440 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-08-18 21:47 |  |  |  | 2021-08-18 22:05 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1976 | UNKNOWN | [7 empty] | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 2 | 2 |  | CLASS 3 LOCATION | 0 | 0 | 220000 | 243047.44059279442 | 24702 | 27289.808534196398922 | 0 | 0 |  | 3.75 | 42900 | 34562.2923588039867109634551495016611296 | 0 | 0 | 287602 | 137921.7256913545267061661129568106312292 | 304899.5414857948056329634551495016611296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 230 | 275 | 192.619(A)(4) | 1976-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY FLOODING. NO SCADA OPERATIONS WERE INVOLVED. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  | YES | [216 empty] | ROMAN HIGH | SENIOR ENGINEER - STANDARDS | rhigh@ugi.com | 484-332-8402 |  | BRAD HECK | bheck@ugi.com | 814-952-0738 | PAMELA JOCSAK | VP ENGINEERING | 484-824-5508 | pjocsak@ugi.com | AT APPROXIMATELY 21:47 ON AUGUST 18, 2021, UGI CENTRAL DISPATCH RECEIVED A CALL FROM 911 STATING THERE IS BLOWING GAS. EMERGENCY RESPONDERS WERE ALREADY ON SCENE AND EVACUATING THE TOWN OF KNOXVILLE DUE TO SEVERE FLASH FLOODING. UGI FIRST RESPONDER ARRIVED ON SCENE AT 22:05 AND CONFIRMED THAT THERE WAS BLOWING GAS BUT COULD NOT DETERMINE THE SOURCE AS IT WAS SUBMERGED IN THE FLOOD WATERS. FLOOD WATERS AT THE LOCATION OF THE INCIDENT CONTINUED TO RISE PEAKING AT APPROXIMATELY 03:00 ON AUGUST 19. AT APPROXIMATELY 06:38 ON AUGUST 19 THE WATER HAD RECEDED AND UGI IDENTIFIED THE SOURCE OF THE BLOWING GAS WHICH WAS AN ABOVE-GROUND REGULATOR STATION. THE STATION HAD BEEN DAMAGED BY RUSHING FLOOD WATERS AND DEBRIS, WHICH BROKE A 4" BY 2" REDUCER ON THE STATION PIPING. THE SITUATION WAS MADE SAFE BY CLOSING THE TWO INLET VALVES TO THE REGULATOR STATION AT 08:50. THERE WERE NO CUSTOMER OUTAGES AS A RESULT OF THIS INCIDENT.
2026-06-30 10:38 | NO | YES | YES | 20210080 | 37226 | 2021-09-20 16:19 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2021-08-26 09:30 | MOUNTAIN | NO | 2021 | 4940 WEST RAY ROAD | CHANDLER | MARICOPA | AZ | 85226 | 33.3214 | -111.9257 | [5 empty] | YES |  |  |  | 2021-08-26 | 1314811 | 1314910 | NATURAL GAS |  | 7 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 4 | 4 | YES | 2021-08-26 09:30 | ALLOWED TO BURN OUT |  | 7 | YES | 20 | 2021-08-26 09:55 |  |  |  | 2021-08-26 09:55 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 44 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1999 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO | 1 | ASTM D2513 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 5000000 | 5523805.468018055 | 43129 | 47647.241206030138819 | 4000 | 4419.044374414444 | 0 | 0 |  | 38.57 | 270 | 217.524916943521594684385382059800664452 | 0 | 0 | 5047399 | 2264313.81247925675176798006644518272425 | 5576089.27851544310441368438538205980066 | 6 | 0 | 1 | 0 | 0 | 1 | 6 | 56 | 56 | 60 | 192.619(A)(2) | 1999-07-12 | PRESSURE DID NOT EXCEED MAOP | NONE |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [9 empty] | YES |  |  |  | OTHER | THERMAL-OXIDATIVE DEGRADATION | NO | [86 empty] | SHAWN BRINK | ADMINISTRATOR DIVISION COMPLIANCE | shawn.brink@swgas.com | 602-484-5489 | 602-484-5322 | SHAWN BRINK | shawn.brink@swgas.com | 602-484-5489 | ROBERT MCGEE | DIRECTOR CENTRAL SUPPORT | 602-484-5367 | robert.mcgee@swgas.com | PL 2021-0128 SOUTHWEST GAS CORPORATION (SWG) RESPONDED TO A REPORTED FIRE AT 4940 WEST RAY ROAD IN CHANDLER CALLED IN BY THE FIRE DEPARTMENT AT 09:30. SWG CONSTRUCTION TECHNICIAN RESPONDED TO FIND A STRIP-MALL THAT APPEARED TO BE DAMAGED BY AN EXPLOSION. FIRE DEPARTMENT REPORTED THAT FOUR PEOPLE WERE TRANSPORTED TO THE HOSPITAL WITH INJURIES. SWG CREWS RESPONDED AND CONTROLLED THE FLOW OF GAS BY SQUEEZING THE 2-INCH PLASTIC PIPELINE THAT SUPPLIES GAS TO THE COMMERCIAL PROPERTY RESULTING IN AN OUTAGE OF SEVEN ACTIVE ACCOUNTS (SIX COMMERCIAL AND ONE RESIDENTIAL). NOTIFICATION WAS MADE TO PHMSA VIA THE NATIONAL RESPONSE CENTER (NRC) ON AUGUST 26, 2021 AT 11:09 AND WAS GIVEN NRC REPORT #1314811. AN UPDATE WAS PROVIDED TO THE NRC ON AUGUST 27, 2021 AT 11:31 AND WAS GIVEN NRC REPORT #1314910. NOTIFICATION WAS MADE TO CHEMICAL SAFETY AND HAZARD INVESTIGATION BOARD (CSB) ON AUGUST 26,2021 AT 12:05. THE APPARENT LEAK CAUSE IS LISTED AS G5 - PIPE, WELD, OR JOINT FAILURE. THE INCIDENT INVESTIGATION IS STILL ONGOING, AND A SUPPLEMENTAL REPORT WILL BE SUBMITTED UPON COMPLETION OF THE INVESTIGATION BY SWG. NOTE: FOR PART A, #10, THE ESTIMATED VOLUME OF GAS RELEASED THAT IS IDENTIFIED REPRESENTS AN ESTIMATE THAT PRESUMES A CRACK THAT IS LEAKING AT 56 PSI, BEGINNING AT THE TIME OF THE INITIAL REPORT OF THE INCIDENT AND ENDING AT THE TIME THE PIPELINE WAS SHUT DOWN. HOWEVER, THE ACTUAL AMOUNT OF GAS LOSS IS UNKNOWN BECAUSE THE TIME THE GAS PIPELINE BEGAN LEAKING IS UNKNOWN. SUPPLEMENTAL REPORT: LABORATORY DATA ANALYSIS SHOWS THE LEAK WAS CAUSED BY THERMAL-OXIDATIVE DEGRADATION EXTENDING FROM THE INNER WALL TO THE MID-WALL OF THE TUBING THAT RESULTED IN A THROUGH-WALL AXIAL CRACK. SECTION G5 WAS UPDATED FROM "SLIT CRACK" TO "THERMAL-OXIDATIVE DEGRADATION".
2026-06-30 10:38 | NO | NO | NO | 20210081 | 35758 | 2021-09-21 15:54 | ORIGINAL FINAL | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | P.O. BOX 430 | MEMPHIS | TN | 38101 | 2021-08-20 10:00 | CENTRAL | YES | 2021 | 9508 MUDVILLE RD | MILLINGTON | SHELBY | TN | 38053 | 35.3766 | -89.7443 | YES | [8 empty] | 2021-08-23 16:32 | 1314834 |  | NATURAL GAS |  | 3500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-08-20 09:01 | NO |  |  | 2021-08-20 09:36 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 6 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1931 | UNKNOWN |  |  |  |  | 10 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 8 | 5 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.65 | 16275 | 13111.9186046511627906976744186046511628 | 0 | 0 | 16275 | 10678.7790697674418604651162790697674419 | 13111.9186046511627906976744186046511628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 90 | 99 | 192.619(A)(3) | 1996-09-07 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXCAVATION DAMAGE CAUSED INCIDENT. CONTROL ROOM FUNCTIONED PROPERLY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | FARMER | UNKNOWN/OTHER | AGRICULTURE | NO | [5 empty] | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [143 empty] | YES | [26 empty] | CLIFTON | PIPELINE INTEGRITY LEAD ENGINEER | cphillips@mlgw.org | 9013201061 |  | CLIFTON PHILLIPS | cphillips@mlgw.org | 9013201061 | CLIFTON PHILLIPS | PIPELINE INTEGRITY LEAD ENGINEER | 9013201061 | cphillips@mlgw.org | AT APPROXIMATELY 9AM ON 8/21/21 A BULLDOZER STRUCK A 10 INCH STEEL DISTRIBUTION MAIN THAT OPERATES AROUND 90 PSIG. THE BULLDOZER WAS WORKING FOR A FARMER RESHAPING A POND. THE BULLDOZER CAUSED AN APPROXIMATE 9IN BY 6IN HOLE IN THE PIPELINE.
2026-06-30 10:38 | NO | YES | NO | 20210082 | 39062 | 2021-09-23 05:16 | SUPPLEMENTAL FINAL | 180 | SPIRE ALABAMA INC. | 605 RICHARD ARRINGTON JR BLVD N | BIRMINGHAM | AL | 35203 | 2021-08-24 11:03 | CENTRAL | NO | 2021 | 211 WASHINGTON STREET | SELMA | DALLAS | AL | 36703-4453 | 32.4099 | -87.0206 |  |  |  | YES | [5 empty] | 2021-08-24 11:03 | 1314563 | 1314799 | NATURAL GAS |  | 2.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-08-23 18:30 | OTHER | GAS WAS CONSUMED IN EXPLOSION, THERE WAS NO SUBSEQUENT FIRE. | 2.7 | YES | 0 | 2021-08-23 18:30 | YES | OPERATOR | 2021-08-23 18:55 | 2021-08-23 18:30 | 2021-08-24 11:00 | NO | PUBLIC PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2021 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | YES | NO | NO |  |  |  | OTHER | MATERIAL NOT INVOLVED IN INCIDENT | [9 empty] | OTHER | [8 empty] | UNREGULATED MAIN PRESSURE INTRODUCED TO CUSTOMER'S EQUIPMENT CAUSING RELEASE OF GAS. | CLASS 3 LOCATION | 419567 | 463521.297759986256437 | 0 | 0 | 550 | 607.61860148198605 | 0 | 0 |  | 11.82 | 32 | 25.78073089700996677740863787375415282392 | 0 | 0 | 420149 | 188485.0320239636204133754152823920265781 | 464154.6970923652524537774086378737541528 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 25 | 192.619(A)(1) | 1970-08-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | RANDY WILSON | DIRECTOR PIPELINE AND SYSTEM INTEGRITY | randy.wilson@spireenergy.com | 205-337-1337 |  | RANDY WILSON | randy.wilson@spireenergy.com | 205-337-1337 | CRAIG HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES AND SMS | 314-575-3950 | craig.hoeferlin@spireenergy.com | ON AUGUST 23, 2021 AT 6:30 PM AN EXPLOSION OCCURRED AT 211 WASHINGTON STREET, SELMA, AL, CAUSING DAMAGE TO THE BOILER ROOM AT THE SELMA CONVENTION CENTER. WHILE PERFORMING A METER SWAP-OVER FOR THE CUSTOMER FROM A UTILIZATION PRESSURE TO INTERMEDIATE PRESSURE SYSTEM, SPIRE'S SERVICE TECH FAILED TO INSTALL THE REQUIRED SERVICE REGULATOR. THIS CAUSED THE INTRODUCTION OF LINE PRESSURE TO CUSTOMER'S EQUIPMENT RESULTING IN AN EXPLOSION AND DAMAGE TO THE BUILDING. SPIRE DETERMINED THE DAMAGE EXCEEDED THE FEDERAL REPORTING LIMITS ON AUGUST 24, 2021 AT APPROXIMATELY 11 AM.
2026-06-30 10:38 | NO | YES | NO | 20210083 | 39733 | 2021-09-24 13:43 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2021-08-25 09:55 | PACIFIC | YES | 2021 | RACE STREET & PARK AVENUE | SAN JOSE | SANTA CLARA | CA | 95126 | 37.326 | -121.9115 | [5 empty] | YES | YES |  |  | 2021-08-25 13:53 | 1314710 | 1314934 | NATURAL GAS |  | 6107 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 300 | 2021-08-25 09:55 |  |  |  | 2021-08-25 10:03 | 2021-08-25 09:55 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 32 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 3 | STEEL | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 498000 | 550171.024614598278 | 0 | 0 | 0 | 0 |  | 8.66 | 52887 | 42608.2973421926910299003322259136212625 | 0 | 0 | 550887 | 258103.8685551470665913621262458471760797 | 592779.3219567909690299003322259136212625 | 15 | 0 | 28 | 0 | 1 | 28 | 15 | 50 | 50 | 60 | 192.619(A)(2) | 1975-06-10 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DIG-IN INCIDENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | YES | > 36” |  | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | X118101646 | 811 DIG | YES | FACILITY OWNER | YES | YES | 23 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | rosa.duenas@pge.com | 510-298-7063 |  | FRANCES YEE | frances.yee@pge.com | 925-200-4736 | ROSA DUENAS | GAS PROGRAM MANAGER | 510-298-7063 | rosa.duenas@pge.com | A THIRD-PARTY CONTRACTOR DAMAGED A UN-MARKED 3" STEEL GAS MAIN DURING HORIZONTAL BORING. THE 3" GAS MAIN WAS NOT LOCATED BY PG&E AND WAS STRUCK BY A 10" REAMER CAUSING A RELEASE OF GAS. GAS TRAVELED IN STORM AND SEWER SYSTEMS AS WELL AS COMMUNICATIONS VAULTS. CREWS ON SITE VENTED THE GAS TO PREVENT FURTHER MIGRATION AND ISOLATE. SAFE ZONES WERE ESTABLISHED, AND THE FD ASSISTED WITH EVACUATIONS WITHIN THE ESTABLISHED ZONE. THERE WERE NO INJURIES AND/OR FATALITIES. THIS INCIDENT IS BEING REPORTED DUE TO THE DAMAGE THRESHOLD REPORTING CRITERIA OF $122K+.
2026-06-30 10:38 | NO | YES | YES | 20210084 | 40728 | 2021-10-01 17:32 | SUPPLEMENTAL FINAL | 2652 | NSTAR GAS COMPANY | 157 CORDAVILLE ROAD | SOUTHBOROUGH | MA | 01772 | 2021-09-02 18:35 | EASTERN | NO | 2021 | 27 PARK ST | MAYNARD | MIDDLESEX | MA | 01754 | 42.4268 | -71.4564 |  |  | YES |  |  |  |  | YES | TD WILLIAMSON THREE WAY STOPPERS | 2021-09-02 19:45 | 1315634 | 1315635, 1315730 | NATURAL GAS |  | 1 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2021-09-02 16:15 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 4 | 2021-09-02 18:35 |  |  |  | 2021-09-02 17:12 | 2021-09-02 16:33 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | COUPLING ON MAIN | 1968 | UNKNOWN | [7 empty] | STEEL |  | OTHER | UNKNOWN AT THIS TIME | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 468000 | 517028.191806489948 | 15874 | 17536.977599863721014 | 38676 | 42727.740056213259036 | 0 | 0 |  | 4.606 | 5 | 4.02823920265780730897009966777408637874 | 0 | 0 | 522555 | 234418.6499498733938667774086378737541528 | 577296.9377017695858573089700996677740864 | 0 | 0 | 1 | 3 | 0 | 3 | 0 | 58 | 56.8 | 60 | 192.619(C) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | DRIP |  | 0.1 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SYSTEM NEVER EXCEEDED MAOP THUS NO INVESTIGATION WAS REQUIRED | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [9 empty] | YES |  |  | YES | NO |  | NO | NO | [8 empty] | NO | NONE |  | NO | [248 empty] | KATHERINE SILVER | MANAGER COMPLIANCE | katherine.silver@eversource.com | 5088641836 |  | KATHERINE SILVER | katherine.silver@eversource.com | 5088641836 | KATHERINE SILVER | MANAGER COMPLIANCE | 5088641836 | katherine.silver@eversource.com | 3.31/25 UPDATED REPORT BASED ON PHMSA REQUEST A, B, C, D AND G BASED UPON THE INITIAL NARRATIVE PROVIDED BY THE MAYNARD FIRE DEPARTMENT TO EVERSOURCE, ON SEPTEMBER 2, 2021 AT 16:14, THE MAYNARD FIRE DEPARTMENT DISPATCHED RESOURCES TO 27 PARK ST MAYNARD, MA DUE TO AN ODOR CALL. THE MAYNARD FIRE DEPARTMENT ARRIVED ON SITE AT 16:17 TO A STRUCTURE FIRE. EVERSOURCE RECEIVED A CALL FROM THE MAYNARD FIRE DEPARTMENT AT 16:33 NOTIFYING EVERSOURCE OF THE SUBJECT STRUCTURE FIRE. EVERSOURCE COORDINATED WITH THE MAYNARD FIRE DEPARTMENT, MASSACHUSETTS STATE FIRE MARSHALL, AND STATE REGULATORY AGENCY ON SITE. THE SITUATION WAS MADE SAFE THROUGH A MAINLINE REPAIR ON SEPTEMBER 3, 2021. A SECTION OF THE MAIN WITH A COUPLING WAS SECURED AND DELIVERED TO THE MASSACHUSETTS MATERIAL RESEARCH FACILITY FOR 3RD PARTY ANALYSIS. MASSACHUSETTS MATERIAL RESEARCH'S INVESTIGATION OF THE GAS MAIN SEGMENT REVEALED SIGNIFICANT CORROSION ON THE ENTIRE OUTER DIAMETER SURFACE OF THE COUPLING TUBE FROM THE SOIL/DIRT SERVICE ENVIRONMENT. THE COUPLING SHOWED SIGNIFICANT WALL THINNING AT ISOLATED LOCATIONS. AT THESE ISOLATED SPOTS ON THE COUPLING, THE PITS BREACHED THROUGH THE WALL THICKNESS, WHICH CREATED A LEAK PATH FOR THE GAS TO ESCAPE FROM THE INSIDE OF THE GAS MAIN. MASSACHUSETTS MATERIAL RESEARCH FOUND THE GAS MAIN TO BE IN SIGNIFICANTLY GOOD CONDITION WITHOUT ANY ANOMALIES THROUGH THE ENTIRE LENGTH OF THE PIPE SEGMENT. PART A.4, A.12 THIS WAS THE TIME THE COMPANY COMMENCED A LEAK INVESTIGATION DURING WHICH GAS READINGS WERE DETECTED. PART A.21 THE COMPANY RESPONDED YES BASED UPON THE INITIAL NARRATIVE PROVIDED BY THE MAYNARD FIRE DEPARTMENT AND GAS READINGS FOUND IN NEAR PROXIMITY TO THE STRUCTURE FIRE. PART A.21.A THE TIME THE MAYNARD FIRE DEPARTMENT ARRIVED ON SITE TO A STRUCTURE FIRE. PART A.21.D PER "SECTION III. CONCLUSION" OF THE MASSACHUSETTS FIRE DISTRICT FOURTEEN'S REGIONAL FIRE INVESTIGATION TEAM FIRE ORIGIN AND CAUSE INVESTIGATION REPORT, ISSUED TO EVERSOURCE ON OCTOBER 13, 2021, "THE MOST PLAUSIBLE HYPOTHESIS IS THAT OF FUEL GAS EXPLOSION. IT IS BELIEVED TO BE AN ACCIDENTAL LOW ORDER FUEL GAS EXPLOSION CAUSED [THE] FIRE." PART A.7,A.21.C, D2.F VALUES DEFAULTED TO 1 AND 0. THE AMOUNT OF GAS RELEASE IS UNKNOWN AT THIS TIME. PART D.2.A THE PUBLIC AND NON-OPERATOR PRIVATE PROPERTY DAMAGE IS CURRENTLY BASED ON A PROPERTY ASSESSMENT PROVIDED BY THE FIRE DEPARTMENT AS WELL AS COSTS ASSOCIATED WITH LANDSCAPING, PAVING AND CONCRETE. HAS BEEN UPDATED TO REFLECT BUILDING AND ITS CONTENTS ESTIMATE. PART D.2.B THE REPAIR COST INCLUDES THE REPAIR COSTS AS WELL AS THE FOLLOW UP LEAK SURVEY COSTS PART E.2 AN AVERAGE OPERATING PRESSURE WAS OBTAINED PRIOR TO THE INCIDENT. PART E.3.B THE MAIN WAS INSTALLED IN 1968 PRE-CODE. THE DATE FOR MAOP WAS DEFAULTED TO 7/1/1970 AS THAT WAS WHEN 192.619(C) WAS ESTABLISHED. PART E.5 THE DRIP REFERENCED IS A DRIP ODORIZER - Z9000. PART E.6 THE COMPANY TOOK MULTIPLE READINGS NONE OF WHICH REACHED OR EXCEEDED 0.15%. THE READING PROVIDED WAS THE FIRST READILY DETECTABLE LEVEL RECORDED AT 0.07. THIS REPORT FUNCTIONALITY ROUNDED THE NUMBER UP TO 0.1. PART G.5 - CORROSION WAS ON COUPLING NOT ON PIPE.
2026-06-30 10:38 | NO | YES | NO | 20210086 | 36295 | 2021-10-11 22:58 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2021-09-13 10:24 | EASTERN | YES | 2021 | 10015 W FORT ST | DETROIT | WAYNE | MI | 48209 | 42.2925 | -83.1426 | [7 empty] | YES | BAG AND STOP SYSTEM | 2021-09-13 10:24 | 1316565 | 1316953 | NATURAL GAS |  | 2.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-09-11 17:08 |  |  |  | 2021-09-11 17:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1913 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 3 LOCATION | 20000 | 22095.22187207222 | 1000 | 1104.761093603611 | 1000000 | 1104761.093603611 | 1000000 | 1104761.093603611 | DAMAGE TO GREAT LAKES WATER AUTHORITY, ATT, COMAST, AND DTE ELECTRIC. | 2.75 | 6 | 4.83388704318936877076411960132890365449 | 0 | 0 | 2021006 | 906622.3680158215499601328903654485049834 | 2232727.0040599410203687707641196013289 | 4 | 0 | 7 | 0 | 0 | 7 | 4 | 2 | 2 | 2 | 192.619(A)(1) | 1970-01-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE UNEXPECTED GROUND MOVEMENT RESULTED IN TWO MAJOR HEAVE AREAS AND DAMAGE TO EXISTING BUILDINGS, PAVEMENT, AND UTILITY STRUCTURES INCLUDING DTE GAS INFRASTRUCTURE AT/NEAR THE INTERSECTION OF FORT STREET AND DEARBORN STREET IN DETROIT, MICHIGAN. INVESTIGATIONS THUS FAR CONFIRM THE GROUND FAILURE OCCURRED DUE TO A RELATIVELY RAPID LOADING OF A LAYER OF SOFT CLAYS BETWEEN 25 AND 40 FT BELOW THE GROUND SURFACE. | [154 empty] | FRENAE F SMITH | MANAGER OF CODES AND STANDARDS | frenae.smith@dteenergy.com | 13134601681 |  |  |  |  | FRENAE F SMITH | MANAGER OF CODES AND STANDARD | 13134601681 | frenae.smith@dteenergy.com | 9/12/21 GROUND HEAVE 10015 WEST FORT & DEARBORN STREET: GROUND HEAVE IMPACTED THE FOLLOWING UTILITIES: GREAT LAKES WATER AUTHORITY (GLWA), ATT, COMCAST, DTE ELECTRIC, AND DTE GAS (6-INCH CI 2 PSI, 16-INCH CI 10PSI, 24-INCH STEEL 145PSI). THE INVESTIGATION IS ONGOING WITH A UNIFORMED ICS (CITY OF DETROIT, MDOT, GLWA, DTE GAS) AND NO CAUSE HAS BEEN DETERMINED YET. A SUPPLEMENTAL REPORT WILL BE FILED WITH MORE DETAILS AND FOLLOW-UP OF THIS EVENT. 1/24/2022 UPDATE ON THE INCIDENT CAUSE: ON SEPTEMBER 11, 2021, SIGNIFICANT, UNEXPECTED GROUND MOVEMENT RESULTED IN TWO MAJOR HEAVE AREAS AND DAMAGE TO EXISTING BUILDINGS, PAVEMENT, AND UTILITY STRUCTURES INCLUDING DTE GAS INFRASTRUCTURE AT/NEAR THE INTERSECTION OF FORT STREET AND DEARBORN STREET IN DETROIT, MICHIGAN. INVESTIGATIONS THUS FAR CONFIRM THE GROUND FAILURE OCCURRED DUE TO A RELATIVELY RAPID LOADING OF A LAYER OF SOFT CLAYS BETWEEN 25 AND 40 FT BELOW THE GROUND SURFACE. DTE UNDERSTANDS THAT THE RELATIVELY RAPID LOADING WAS CAUSED BY THE INCREASE IN HEIGHT AND WEIGHT OF A MILL SCALE STOCKPILE AT THE FORT IRON AND METAL FACILITY. THE GROUND FAILURE OCCURRED CONCENTRICALLY AROUND THE LARGE STOCKPILE OF MATERIAL LOCATED AT THE PROPERTY, A METAL SCRAP YARD OWNED AND OPERATED BY FORT IRON & METAL COMPANY. ON INFORMATION AND BELIEF, THE MILL SCALE MATERIAL WAS STOCKPILED TO SOME DEGREE AT THIS LOCATION BY FORT SINCE AT LEAST MAY 2019.
2026-06-30 10:38 | NO | YES | YES | 20210087 | 36110 | 2021-10-12 22:18 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD N.E. SUITE 20 | ALBUQUERQUE | NM | 87109 | 2021-09-13 20:00 | MOUNTAIN | NO | 2021 | 777 CANYON ROAD | SANTA FE | SANTA FE | NM | 87501 | 35.6804 | -105.9243 | [5 empty] | YES |  |  |  | 2021-09-13 20:55 | 1316663 | 1317031 | NATURAL GAS |  | 3.8 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2021-09-13 10:50 | OPERATOR/CONTRACTOR |  | 2.3 | NO | 0 | 2021-09-13 10:50 | NO |  |  | 2021-09-13 09:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1971 | 1971 | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO | 0.75 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.113 | [6 empty] | OTHER | [8 empty] | AN IGNITION OCCURRED WHEN A NEW MEXICO GAS COMPANY (NMGC) CONSTRUCTION CREW CUT INTO A PRESSURIZED (55 PSIG) 3/4-INCH STEEL SERVICE WITH FOUR-WHEEL CUTTERS TO ISOLATE AND PLUG THE SERVICE LINE FOR ABANDONMENT. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15.21 | 58 | 46.72757475083056478405315614617940199336 | 0 | 0 | 58 | 38.05647840531561461794019933554817275748 | 46.72757475083056478405315614617940199336 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 55 | 55 | 60 | 192.619(A)(1) | 2016-10-27 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.5 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | AN IGNITION OCCURRED WHEN A NEW MEXICO GAS COMPANY (NMGC) CONSTRUCTION CREW CUT INTO A PRESSURIZED (55 PSIG) 3/4-INCH STEEL SERVICE WITH FOUR-WHEEL CUTTERS TO ISOLATE AND PLUG THE SERVICE LINE FOR ABANDONMENT. CREW FAILED TO FOLLOW PROCEDURE. |  |  | YES |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ANDREA MARTINEZ | PIPELINE SAFETY MANAGEMENT SYSTEMS MANAGER | andrea.martinez@nmgco.com | 505-697-3518 |  | ANDREA MARTINEZ | andrea.martinez@nmgco.com | 505-427-6343 | TOM BULLARD | VP ENG-GAS MGMT-TECH SERVICES | 505-697-3599 | tom.bullard@nmgco.com | ON 9/13/2021 AT 10:50 AM, WHILE A CREW WAS ISOLATING AND RETIRING A SERVICE, AN IGNITION OCCURRED WHEN A NEW MEXICO GAS COMPANY (NMGC) CONSTRUCTION CREW CUT INTO A PRESSURIZED 3/4-INCH STEEL SERVICE WITH FOUR-WHEEL CUTTERS. THE THREE-MAN CREW (ACTING FOREMAN & 2 CREWMEN) ARRIVED TO RETIRE THE 3/4-INCH STEEL SERVICE AND DISCOVERED THAT NEITHER CREW MEMBER NOR THE ACTING FOREMAN HAD BROUGHT THE SAW TO CUT THE ASPHALT TO ACCESS THE SERVICE TEE CONNECTION AND PROPERLY ISOLATE THE SERVICE FOR RETIREMENT. THE CREW DECIDED TO CONTINUE THE JOB WITHOUT RETURNING TO THE SHOP TO GET THE SAW, AND INSTEAD DECIDED TO PROCEED TO MAKE THE REPAIR HOT WITH WHAT THEY DESCRIBED AS A CUT AND PLUG PROCEDURE. DURING THE CUT AND PLUG, AN IGNITION OCCURRED, AND ONE CREWMEN SUFFERED FIRST DEGREE BURNS, AND THE OTHER SUFFERED FIRST AND SECOND DEGREE BURNS. NEITHER THE ACTING FOREMAN NOR THE CREWMEN REPORTED THE IGNITION FIRE OR INJURIES UNTIL APPROXIMATELY 14:30 THAT AFTERNOON WHEN CREWMAN #2 CALLED THE SUPERVISOR AND REPORTED THAT A FLASH HAD OCCURRED, AND HE HAD BEEN INJURED. HE WAS TOLD TO SEEK MEDICAL TREATMENT. HE WAS SEEN BUT RELEASED BY CONCENTRA. LATER THAT AFTERNOON, ALL THREE MEMBERS OF THE CREW REPORTED TO THE OFFICE FOR INTERVIEWS AT THE SANTA FE OFFICE AT APPROXIMATELY 17:20 AND UPON DISCOVERY OF THE SEVERITY OF THEIR INJURIES, THE CREWMEN WERE SENT THE HOSPITAL BY THE AREA MANAGER. BOTH CREWMEN PROCEEDED TO THE HOSPITAL, CREWMAN #2 WAS ADMITTED TO THE HOSPITAL AS THE RESULT OF THIS INJURIES, AND CREWMAN #1 WAS TREATED AND RELEASED THAT EVENING. THE INCIDENT MET REPORTABLE CRITERIA WHEN CREWMAN #2 WAS ADMITTED TO THE HOSPITAL, AND COULD NOT BE TESTED FOR DRUG AND ALCOHOL DUE TO HIS ADMITTANCE TO THE HOSPITAL. THE ACTING FOREMAN AND CREWMAN #1 WERE DRUG AND ALCOHOL TESTED. GAS ODORANT TESTING WAS PERFORMED BY NM GAS AT 21:11. READINGS CONFIRMED PROPER ODORANT AT 0.53% GAS-IN-AIR. CREW FAILED TO FOLLOW PROCEDURES.
2026-06-30 10:38 | NO | YES | NO | 20210088 | 36125 | 2021-10-20 15:18 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2021-09-28 18:00 | EASTERN | YES | 2021 | LONG STREET | FORT BRAGG | CUMBERLAND | NC | 28310 | 35.1493 | -79.0092 | [6 empty] | YES |  |  | 2021-09-28 21:49 | 1318145 | 1318329 | NATURAL GAS |  | 5269 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-09-28 18:57 | NO |  |  | 2021-09-28 18:57 |  | YES | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 3 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1965 | UNKNOWN |  |  |  |  | 8 | API 5L GRADE B | UNKNOWN | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 200000 | 220952.2187207222 | 15000 | 16571.416404054165 | 0 | 0 |  | 4.5 | 23711 | 19102.7159468438538205980066445182724252 | 0 | 0 | 238711 | 112006.6513298799344518272425249169435216 | 256626.3510716202188205980066445182724252 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 148 | 150 | 192.619(A)(1) | 1965-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT BEING A 3RD PARTY DAMAGE AND THE CONTRACTOR DAMAGED THE LINE WHILE BORING. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | NO | [5 empty] | YES | 48 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY ANALYST | christopher.ransome@duke-energy.com | (704) 731-4680 |  |  |  |  | FARRIS BERRY | MANAGER PIPELINE SAFETY | (704) 731-4618 | farris.berry@duke-energy.com | A 3RD PARTY CONTRACTOR BORED INTO A HIGH PRESSURE 8" STEEL DISTRIBUTION LINE WHILE INSTALLING TELECOMMUNICATION LINES. DAMAGE RESULTED IN 1 COMMERCIAL OUTAGE. EXCAVATION WAS PERFORMED ON A EXPIRED LOCATE TICKET. THE CONTRACTOR WAS AWARE THAT THEY WERE WORKING NEAR HIGH PRESSURE LINE. BETWEEN 07/27-08/05/2021 PIEDMONT WAS ON SITE WHILE THE CONTRACTOR WORKED NEAR THE GAS LINE. THE CONTRACTOR WAS ADVISED TO CONTACT PIEDMONT FOR ADDITIONAL STANDBYS WHEN NEEDED.
2026-06-30 10:38 | NO | YES | YES | 20210089 | 36201 | 2021-10-26 22:19 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2021-09-27 13:25 | CENTRAL | YES | 2021 | 501 WILLOW BLVD. | WILLOW SPRINGS | COOK | IL | 60480 | 41.7326 | -87.8787 | [5 empty] | YES |  |  |  | 2021-09-27 19:07 | 1318029 | 1318263 | NATURAL GAS |  | 238.9 | 18.5 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2021-09-27 13:25 | ALLOWED TO BURN OUT |  | 238.9 | NO | 0 | 2021-09-27 13:25 |  |  |  | 2021-09-27 14:06 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 38 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2009 | 2008 |  |  |  |  | 2 | ASTM D2513 | UPONOR PIPE COMPANY | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 29700 | 32811.4044800272467 | 8625 | 9528.564432331144875 | 2845 | 3143.045311302273295 | 0 | 0 |  | 5.49 | 1312 | 1057.009966777408637873754152823920265781 | 102 | 82.17607973421926910299003322259136212625 | 42584 | 19396.6085155775048646511627906976744186 | 46622.2002701722927769767441860465116279 | 5 | 0 | 2 | 0 | 1 | 2 | 1 | 21 | 22 | 25 | 192.619(A)(2) | 2009-02-16 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | PROBING DEVICE | POLE | YES | x2581427 | J.U.L.I.E. |  | CONTRACT LOCATOR | NO | YES | 15 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | lquezad@southernco.com | 6305142036 |  |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | 6305142036 | lquezad@southernco.com | BLUE PEAK TENTS, INC. PUT UP A TENT ON TUESDAY, 9/21/21. THEY UTILIZED EXISTING HOLES IN THE PARKING LOT PAVEMENT, AND MADE A NEW HOLES IN THE PARKWAY FOR THE STAKES THAT HOLD DOWN THE TENT. WHEN THE EMPLOYEES FROM BLUE PEAK TENTS, INC. CAME BACK ON MONDAY 9/27/21 TO REMOVE THE TENT, THEY USED A GASOLINE-OPERATED HYDRAULIC STAKE PULLING MACHINE TO REMOVE THE STAKES. WHILE IN THE PROCESS OF REMOVING ONE OF THE STAKES, THERE WAS IGNITION OF NATURAL GAS. TWO EMPLOYEES FROM BLUE PEAK TENTS, INC. WERE INJURED. ONE EMPLOYEE WAS TAKEN TO THE HOSPITAL AND RELEASED THE FOLLOWING DAY, AND THE OTHER REFUSED MEDICAL ATTENTION. AFTER STOPPING THE FLOW OF NATURAL GAS AND EXPOSING THE 2-INCH GAS MAIN, IT WAS REVEALED THAT A 1-INCH DIAMETER STAKE HAD PIERCED THE MAIN. PART G3, QUESTION 14: WHEN SELECTING "EXCAVATION PRACTICES NOT SUFFICIENT (OTHER)" FROM THE DROP DOWN MENU, THERE IS NO ADDITIONAL FIELD AVAILABLE TO PROVIDE AN EXPLANATION, AS REQUESTED BY PHMSA AID PERSONNEL; THEREFORE, THE EXPLANATION IS PROVIDED HERE IN PART H. EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) MEANS THE EXCAVATOR EXCAVATED OUTSIDE THE SCOPE OF THE ONE CALL TICKET.
2026-06-30 10:38 | NO | YES | NO | 20210090 | 35924 | 2021-10-27 16:43 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-09-26 17:15 | EASTERN | NO | 2021 | 13950 ANDORRA DR. | WOODBRIDGE | PRINCE WILLIAM | VA | 22193 | 38.6503 | -77.3277 | [5 empty] | YES |  |  |  | 2021-10-18 17:21 | 1319785 | 1319926 | NATURAL GAS |  | 47.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-09-26 17:15 | OPERATOR/CONTRACTOR |  | 47.5 | NO | 3 | 2021-09-26 17:40 |  |  |  | 2021-09-26 18:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1997 | 1997 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | METER & REGULATOR - ALUMINUM | [9 empty] | OTHER | [8 empty] | VEHICULAR IMPACT | CLASS 4 LOCATION | 574600 | 634795.7243846348806 | 18000 | 19885.699684864998 | 1120 | 1237.33242483604432 | 383 | 423.123498850183013 | ADMIN FEE - $383.00 | 5.31 | 252 | 203.023255813953488372093023255813953488 | 0 | 0 | 594355 | 266679.3170681949048595813953488372093023 | 656544.9032490000594213720930232558139535 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 30 | 30 | 33 | 192.619(A)(2) | 1997-03-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE CAUSED BY VEHICULAR IMPACT AND NOT CONTROLLER(S) OR CONTROL ROOM ISSUES. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  |  | YES | YES | CITATIONS: UNREASONABLE REFUSAL, EXPIRED REGISTRATION AND OPERATING AN UNINSURED VEHICLE | YES | UNKNOWN | PASSENGER CAR | ROADWAY | 75 | NO | [118 empty] | YES | [23 empty] | RICHARD FITZPATRICK | SUPERVISOR DOT COMPLIANCE | richardfitzpatrick@washgas.com | 7036397825 |  | SHANNON MALONEY | manager dot compliance | 703-750-5558 | SHANNON MALONEY | MANAGER DOT COMPLIANCE | 703-750-5558 | smaloney@washgas.com | ON 9/26/2021 AT APPROXIMATELY 17:15 HRS A VEHICLE TRAVELLING FROM HEREFORD RD TO SOUTHBOUND MINNEVILLE RD. LEFT THE ROADWAY AND TRAVELLED APPROXIMATELY 90 FEET AND STRUCK A METER SET ASSEMBLY SUPPLIED BY A 3/4" NATURAL GAS SERVICE, LOCATED AT 13950 ANDORRA DR. WOODBRIDGE, VA. PRINCE WILLIAM COUNTY FIRE BOARD NOTIFIED WASHINGTON GAS. WASHINGTON GAS RESPONDED AND LOCATED THE NATURAL GAS SERVICE AND OBTAINED GAS OFF BY SQUEEZE IN THE AREA OF THE FRONT YARD OF THE ABOVE ADDRESS. THE DRIVER WAS TRANSPORTED TO THE LOCAL HOSPITAL FOR PRECAUTIONARY MEASURES. THE NATURAL GAS SERVICE LINE WAS CAPPED OFF DUE TO STRUCTURAL DAMAGE TO THE RESIDENCE. THIS REPORT WAS DELAYED DUE TO THE UNKNOWN ESTIMATED PROPERTY DAMAGE AND SITE ACCESS LIMITATIONS.
2026-06-30 10:38 | NO | YES | NO | 20210091 | 37292 | 2021-10-29 09:03 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2021-10-06 10:08 | EASTERN | YES | 2021 | 3500 LAKELAND ROAD | GAINESVILLE | HALL | GA | 30506 | 34.369 | -83.8042 |  |  |  | YES | [5 empty] | 2021-10-06 12:12 | 1318790 | 1318985 | NATURAL GAS |  | 0.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-10-06 10:08 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.5 | NO | 0 | 2021-10-06 10:08 |  |  |  | 2021-10-06 10:28 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2002 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | TYPICAL METER SET | [9 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 0.5 | 0.5 |  | CLASS 3 LOCATION | 140000 | 154666.55310450554 | 200 | 220.9522187207222 | 200 | 220.9522187207222 | 0 | 0 |  | 6.65 | 3 | 2.41694352159468438538205980066445182724 | 0 | 0 | 140403 | 62985.2577665341571800664451827242524917 | 155110.8744854685790843853820598006644518 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 125 | 125 | 125 | 192.619(A)(2) | 1983-08-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 10 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A NATURAL GAS METER ON THE SIDE OF A RESIDENTIAL BUILDING RUPTURED WHEN LIGHTNING HIT AN UNKNOWN LOCATION AND TRAVELED ALONG THE CUSTOMER'S FUEL LINE AND ARCED ONTO THE GAS METER. AN ELBOW THAT WAS PART OF THE CUSTOMER'S FUEL LINE APPEARED TO BE IN CONTACT WITH THE GAS METER AT THE POINT WHERE THE DAMAGE OCCURRED. THE INCIDENT OCCURRED DURING A THUNDERSTORM, AND ACCORDING TO THE CUSTOMER, POWER TO THE HOME HAD GONE OUT AND CAME BACK ON SHORTLY BEFORE THE FIRE OCCURRED. THE ESCAPING NATURAL GAS IGNITED AS A RESULT OF THE ARC AND DAMAGED THE EXTERIOR OF THE RESIDENTIAL BUILDING LOCATED ADJACENT TO THE METER. ADDITIONAL NRC REPORT NUMBER 1318985 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2026-06-30 10:38 | NO | YES | NO | 20210093 | 36232 | 2021-11-05 16:02 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-07-21 11:18 | EASTERN | NO | 2021 | JOHN JAMES WAY & JOHN MARSHALL HWY | HAYMARKET | PRINCE WILLIAM | VA | 20169 | 38.8116 | -77.6458 |  | YES |  |  |  | YES |  |  |  | 2021-10-14 14:57 | 1319484 | 1319786 | NATURAL GAS |  | 2892 | 2508 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-07-21 11:20 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-07-21 11:19 | 2021-07-21 12:00 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2001 | 2000 |  |  |  |  | 12 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 4 | 3 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 84887 | 93779.854952729726957 | 5476 | 6049.671748573373836 | 0 | 0 |  | 3.96 | 11452 | 9226.27906976744186046511627906976744186 | 9932 | 8001.694352159468438538205980066445182724 | 111747 | 54567.7747261562867276212624584717607973 | 117057.5001232300110920033222591362126246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 2001-02-15 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA DOES NOT HAVE ANY CONTROL OVER THIS PORTION OF THE SYSTEM. IT IS MONITORING ONLY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | UNKNOWN/OTHER | GRADING | YES | A118200220 |  |  | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [143 empty] | YES | [26 empty] | RICHARD FITZPATRICK | SUPERVISOR DOT PIPELINE SAFETY | richardfitzpatrick@washgas.com | (703)639-7825 |  | RICHARD FITZPATRICK | richardfitzpatrick@washgas.com | (703)639-7825 | SHANNON B. MALONEY | MANAGER PIPELINE SAFETY COMPLIANCE QUALITY | (703)750-5558 | smaloney@washgas.com | ON 7/21/21 AT 1118 HRS, WASHINGTON GAS RECEIVED A REPORT OF A NATURAL GAS BROKEN LINE AT JOHN MARSHALL HIGHWAY AND TRADING SQUARE HAYMARKET, VA. 20169 FROM PRINCE WILLIAM COUNTY FIRE BOARD. 1119 HRS WASHINGTON GAS DISPATCHED FIELD OPS CREWS FOR RESPONSE. 1120 HRS WASHINGTON GAS RECEIVED AN ALARM ON SCADA OF PRESSURE DROPPING AND PRESSURE OPERATIONS CREWS WERE DISPATCHED. THE FIRST FIELD OPS CREW ARRIVED AT 1200 HRS AND WORKED WITH THE FIRE DEPARTMENT TO SECURE THE SCENE AND RELAY INFORMATION TO WASHINGTON GAS DISPATCH FOR ADDITIONAL SUPPORT. THE FIRST ARRIVING CREWS BEGAN TO LOCATE THE CLOSEST DISTRIBUTION VALVE. THE AREA OF THIS VALVE #1 HAD BEEN RECENTLY REGRADED AND HAD EXTENSIVE VEGETATION GROWTH. THE CREWS LOCATED A BROKEN PORTION OF A LINE MARKER (IT HAD RECENTLY BEEN BUSHED HOGGED AND BROKEN OFF) AND FOUND THE VALVE COVER WAS FOUND UNDER 3-4" OF SOIL. CUSTOMER IMPACT THROUGH THE UTILIZATION OF CRITICAL VALVES TO STOP GAS, AND AREA OF THE DAMAGE (NATURAL GAS VENTING INTO THE ATMOSPHERE IN AN OPEN LOT AND THE CLOSEST STRUCTURE APPROXIMATELY 300FT. AWAY) WERE FACTORS CONSIDERED AS PART OF THE RESPONSE PLANNING. AT APPROXIMATELY 1445 HRS WASHINGTON GAS PRESSURE OPS BEGAN TO CONTROL THE FLOW OF NATURAL GAS, REDUCING THE PRESSURE TO 5PSIG BY USE OF VALVE #1. ONCE THE PRESSURE WAS STABILIZED CREWS BEGAN TO EXCAVATE UPSTREAM AND DOWNSTREAM OF THE BREAK AREA TO INSTALL (2) 2" BYPASSES. THESE BYPASSES WERE INSTALLED TO MAINTAIN THE DOWNSTREAM CUSTOMERS AND TO USE THE EXPOSED 12' PLASTIC TO DOUBLE SQUEEZE THE PIPE. GAS WAS SQUEEZED OFF AT 0400 HRS ON 7/22/2021. FURTHER INVESTIGATION AND REPAIRS COMMENCED. CURRENT VALVE ASSIGNMENTS WERE REVALUATED NETTING AN INCREASE OF CRITICAL VALES ON THE EXISTING INFRASTRUCTURE.
2026-06-30 10:38 | NO | YES | NO | 20210094 | 40327 | 2021-11-09 15:01 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2021-10-17 00:15 | PACIFIC | YES | 2021 | MARKET CIRCLE & HWY 183 | SALINAS | MONTEREY | CA | 93901 | 36.6863 | -121.6773 | [5 empty] | YES |  |  |  | 2021-10-17 04:37 | 1319672 | 1319741 | NATURAL GAS |  | 5485 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-10-16 17:07 | YES | OPERATOR | 2021-10-16 17:19 | 2021-10-16 18:20 | 2021-10-17 04:00 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1940 | UNKNOWN |  |  |  |  | 4 | STEEL | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | THIRD PARTY DIG IN | CLASS 1 LOCATION | 0 | 0 | 90860 | 100378.59296482409546 | 3785 | 4181.520739289667635 | 0 | 0 | 0 | 3 | 16455 | 13256.9352159468438538205980066445182724 | 0 | 0 | 111100 | 53254.5308126023704744518272425249169435 | 117817.0489200606069488205980066445182724 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 54 | 54 | 60 | 192.619(A)(2) | 1975-06-10 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DIG-IN INCIDENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [6 empty] | NO | NO | 18” – 36” |  | CONTRACTOR | FARM EQUIPMENT | AGRICULTURE | NO |  |  |  | FACILITY OWNER | NO | YES | 4 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | ROSA DUENAS |  | r1dj@pge.com | [5 empty] | SUSIE RICHMOND | GAS OPS COMPLIANCE AND RISK MANAGER | 925-328-5776 | gsr8@pge.com | PG&E WAS NOTIFIED OF A DIG IN AT MARKET CIRCLE AND HWY 183 IN SALINAS, CA. FARM OPERATOR DUG AND DAMAGED TWO PG&E SUBSURFACE GAS FACILITIES: ONE 4-INCH STEEL DISTRIBUTION PIPE AND ONE 1 1/4-INCH STEEL SERVICE PIPE WITH MAOPS OF 60 PSI. PG&E CREW ARRIVED ON-SITE AND STOPPED THE FLOW OF GAS ON 10/17 AT 02:44 HOURS. THERE WERE NO INJURIES OR FATALITIES. THERE WAS NO MEDIA REPORTED. POLICE AND FIRE DEPARTMENT WERE ONSITE. THIS INCIDENT WAS REPORTED TO THE DOT (#1319672) AND CPUC DUE TO THE RELEASE OF GAS ESTIMATED TO BE GREATER THAN 3MMCF.
2026-06-30 10:38 | NO | NO | NO | 20210095 | 36213 | 2021-11-16 21:13 | SUPPLEMENTAL FINAL | 1720 | BRENHAM UTILITY, CITY OF | 200 W VULCAN ST | BRENHAM | TX | 77834 | 2021-10-22 09:20 | CENTRAL | NO | 2021 | HWY 290 E @ S CHAPPELL HILL ST | BRENHAM | WASHINGTON | TX | 77833 | 30.142 | -96.3821 | YES |  |  |  |  | YES |  |  |  | 2021-10-22 11:35 | 1320155 | 1320663 | NATURAL GAS |  | 250 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-10-22 09:20 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 250 | NO | 0 | 2021-10-22 09:20 | YES | OPERATOR | 2021-10-22 09:20 | 2021-10-22 09:27 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 18 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1994 | 1992 |  |  |  |  | 6 | ASTM D2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 2904 | 3208.226215824886344 | 583 | 644.075717570905213 | 2025 | 2237.141214547312275 | COST OF BRENHAM FD ALONG WITH 3 OTHER FIRE DEPARTMENTS MUTUAL AID | 8.05 | 2013 | 1621.76910299003322259136212624584717608 | 0 | 0 | 7525 | 3793.49954386494256058471760797342192691 | 7711.21225093313705459136212624584717608 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 28 | 28 | 60 | 192.619(A)(4) | 1980-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PRESSURE CHANGES WAS FROM THE DAMAGE DUE TO THE PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | UNKNOWN/OTHER | ROAD WORK | YES | 2178065546 | TEXAS 811 IS THE ONLY ONE-CALL |  | UTILITY OWNER | YES | UNKNOWN/OTHER |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ANDE BOSTAIN | GAS SUPERINTINDENT | abostain@cityofbrenham.org | 19793377416 | 19793377419 | ANDE BOSTAIN | abostain@cityofbrenham.org | 19794511772 | ANDE BOSTAIN | GAS SUPERINTINDENT | 19794511772 | abostain@cityofbrenham.org | THE EXCAVATOR WAS WORKING ON THE ACCESS ROAD FOR THE ENTRANCE TO THE NEW SHOPPING CENTER. THE PROJECT HAS BEEN ONGOING SINCE FEBRUARY. THEY HAD NOT STARTED ON THIS SECTION UNTIL THE LAST COUPLE OF MONTHS. AFTER REMOVING AN OLD DRIVEWAY THAT EXISTED ALONG THE ROAD THEY HAD CHANGED THE GRADE OF THE AREA BY REMOVING A PORTION OF THE DIRT THAT COVERED THE 6" MAIN. THERE HAD BEEN A LOCATE DONE FOR A FIBER CONTRACTOR THAT WAS BASICALLY ALONG THE SAME PATH OF THE ROAD CONTRACTORS WORKSITE. THE MAIN WAS FLAGGED AND MARKED CORRECTLY ALONG THE PATH. ALL THE MARKINGS WERE PRESENT WHEN BURTS CONSTRUCTION REMOVED SOME MORE MATERIAL WITH A DOZER AND THEN BROUGHT IN A RECLAIMER TO MIX THE DIRT AND ROAD BASE FOR STABILIZATION. WHEN THE MIXER STARTED TO TILL THE DIRT IT HIT THE LINE DAMAGING IT AND CAUSING AN IGNITION. THE EQUIPMENT OPERATOR SHUT OFF THE MACHINE AND JUMPED OFF BUT BUT DID GET HIS RIGHT ARM BURNT TO THE POINT HE WAS TAKEN TO THE HOSPITAL BY HELICOPTER. THE RECLAIMER WAS ENGULFED IN FLAMES AND COMPLETELY DESTROYED. WE CLOSED A VALVE OFF ON THE WEST SIDE OF THE DAMAGE AND THEN DUG UP THE 6" AND SQUEEZED IT OFF TO STOP THE FLOW OF GAS ON THE EAST SIDE. THE FIRE DEPARTMENT PUT THE FIRE OUT. I CONTACTED THE RRC BY PHONE AND ALSO THE NRC. THE RRC SENT INVESTIGATORS OUT TO ACCESS THE SCENE AND INVESTIGATE IT. I CHECKED ON THE EMPLOYEE WHO WAS INJURED AND HIS SUPERVISOR SAID HE WAS RELEASED FROM THE HOSPITAL THAT SAME NIGHT WITH SEVERE BURNS ON HIS RIGHT ARM. THE DAMAGED RECLAIMER WAS REMOVED FROM THE SPOT ON THE 25TH OF OCTOBER 2021. ON TUESDAY THE 26TH OCTOBER 2021 WE DUG UP, LOWERED AND REPAIRED THE LINE WAS DAMAGED WITH THE RRC INSPECTORS ON SITE. ON THURSDAY THE GAS DEPARTMENT EXPOSED THE GAS MAIN ALONG THE AREA IN 4 DIFFERENT SPOTS VERIFYING ITS LOCATION AND DEPTH. ALL WERE ALREADY CORRECTLY MARKED BUT THESE AREAS HAD NOT HAD DIRT REMOVED FROM THE TOP OF THEM. THE CITY OF BRENHAM GAS DEPOARTMENT WILL CONTINUE TO MARK OUR FACILITIES IN ACCORDANCE WITH THE TEXAS AMINISTRATIVE CODE TITLE 16 PART 1 CHAPTER 18 FOR UNDERGROUND PIPELINE DAMAGE PREVENTION. WE HAVE PUT IN PLACE IN OUR PLAN REVIEW FOR DEVELOPEMENT SERVICES UNDER THE GAS DEPARTMENT COMMENTS SECTION VERBIAGE STATING THAT THE BUILDER, CONTRACTOR, DEVELOPER AND/OR EXCAVATORS THAT TAKE PART IN THESE WORK PROJECTS WILL MAINTAIN CONTACT WITH THE CITY OF BRENHAM AND BE AWARE OF THEIR RESPONSIBILITY OF PROTECTION OF EXISTING CITY UNTILITIES ON THESE SITES DURING THE DURATION OF THE PROJECT.
2026-06-30 10:38 | NO | YES | YES | 20210096 | 36361 | 2021-11-17 17:43 | SUPPLEMENTAL FINAL | 22364 | WEST BATON ROUGE PARISH NATURAL GAS SYSTEM | 880 N ALEXANDER, P.O. BOX 807 | PORT ALLEN | LA | 70767 | 2021-11-01 17:00 | CENTRAL | YES | 2021 | 4826 WOODLAWN | ADDIS | WEST BATON ROUGE | LA | 70710 | 30.38 | -91.2778 |  | YES | [7 empty] | 2021-11-01 16:16 | 1320955 | 1321074 | NATURAL GAS |  | 0.23 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2021-11-01 11:30 | ALLOWED TO BURN OUT |  | 0.23 | NO | 0 | 2021-11-01 11:30 | YES | OPERATOR | 2021-11-01 17:30 | 2021-11-01 11:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 2021 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | YES | YES | NO | 0.75 | 2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 250 | 276.19027340090275 | 2000 | 2209.522187207222 | 0 | 0 |  | 5.59 | 1 | 0.8056478405315614617940199335548172757475 | 0 | 0 | 2251 | 1010.003731563952493355481727574750830565 | 2486.518108448656311461794019933554817276 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 50 | 50 | 60 | 192.619(A)(1) | 2019-01-01 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | CONSTRUCTION | YES | NO, BUT THEY WERE PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [34 empty] | YES |  |  |  | YES | [10 empty] | ADRIAN GENRE |  | adrian.genre@wbrcouncil.org | 2253362406 |  |  |  |  | ADRIAN GENRE |  | 2253362406 | adrian.genre@wbrcouncil.org | GAS CREW WAS INSTALLING A NEW 3/4 INCH PE SERVICE LINE WITH A PLASTIC BOLT ON SERVICE TEE ON A 4" PE MAIN. THE SERVICE LINE BEING INSTALLED WITH AN EFV WAS CONNECTED TO THE SERVICE TEE AT THE MAIN. THE TAP CUTTER ON THE SERVICE TEE WAS SCREWED CLOCKWISE TO TAP INTO THE MAIN TO PROVIDE GAS TO THE NEW CUSTOMER. AFTER TAP WAS COMPLETED AND THE GAS HAD BEEN INTRODUCED INTO THE SERVICE LINE FOR APPROXIMATELY 30 MINUTES, THE TAP SIDE OF THE EFV, THE FITTING (NUT THAT FASTENS THE EFV TO THE TAP) BLEW OFF. THE EMPLOYEE THAT WAS INJURED JUMPED INTO THE HOLE AND ATTEMPTED TO SCREW THE TAP CUTTER BACK DOWN INTO THE MAIN TO STOP GAS FLOW. WHILE TURNING THE TAP, APPROXIMATELY 2 ROUNDS, THE GAS IGNITED. THE INDIVIDUAL JUMPED OUT OF THE HOLE AND A CREW MEMBER WENT TO A CLOSE BY MAIN LINE VALVE TO TURN OFF THE GAS FEEDING THE DAMAGED SERVICE LINE. THIS MAIN LINE VALVE SHUT OFF GAS DOWNSTREAM OF THE CLOSED VALVE. THERE WAS A WATER SERVICE LOCATED IN THE SAME EXCAVATION THAT MELTED AND THE WATER EXTINGUISHED THE FIRE. THE MAIN LINE VALVE WAS TURNED OFF ELIMINATING THE GAS FLOW.
2026-06-30 10:38 | NO | YES | YES | 20210097 | 36095 | 2021-11-19 15:20 | SUPPLEMENTAL FINAL | 2392 | CITIZENS GAS & COKE UTILITY | 2020 N MERIDIAN ST | INDIANAPOLIS | IN | 469202 | 2021-10-22 09:04 | EASTERN | YES | 2021 | 558 N RYBOLT AVE | INDIANAPOLIS | MARION | IN | 46222 | 39.7749 | -86.2324 |  | YES | [7 empty] | 2021-10-22 10:13 | 1320137 | 132033 & 132538 | NATURAL GAS |  | 46000 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES | 2021-10-22 08:35 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 44000 | YES | 0 | 2021-10-22 08:42 |  |  |  | 2021-10-22 09:04 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1993 | 1993 | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.5 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.093 |  | 2406 | LEAK |  |  | OTHER | MELT HOLE FROM CUST. FIRE PIT | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 6500 | 7180.9471084234715 | 22700 | 25078.0768248019697 | 0 | 0 |  | 4.6 | 211600 | 170475.0830564784053156146179401993355482 | 0 | 0 | 240800 | 151939.6202251190716199335548172757475083 | 202734.1069897038465156146179401993355482 | 0 | 0 | 6 | 3 | 1 | 1 | 0 | 26.5 | 27 | 30 | 192.619(C) | 1993-06-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION INDICATED THE CAUSE OF THE INCIDENT WAS DUE TO A CUSTOMER'S OUTDOOR FIRE PIT MELTING A HOLE IN THE PLASTIC NATURAL GAS SERVICE LINE. SCADA HAS NO CONTROL ON THIS DISTRIBUTION SERVICE LINE FAILURE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HEAT FROM THE CUSTOMER'S OUTDOOR FIRE PIT DAMAGED THE NATURAL GAS SERVICE LINE. | [154 empty] | BEN WARREN | DIRECTOR GAS TRANSMISSION AND DISTRIBUTION | bwarren@citizensenergygroup.com | 3176912514 |  |  |  |  | BEN WARREN | DIRECTOR GAS TRANSMISSION AND DISTRIBUTION | 3176912514 | bwarren@citizensenergygroup.com | THE FINDINGS OF THE INVESTIGATION BY THE FIRE DEPARTMENT REVEALED THE HOMEOWNER HAD INSTALLED A FIRE PIT DIRECTLY OVER THE NATURAL GAS DISTRIBUTION SERVICE LINE. THE NATURAL GAS SERVICE LINE IS A 1/2" PLASTIC DISTRIBUTION SERVICE LINE INSERTED INSIDE AN ABANDON 1 1/4" STEEL LINE. THE HEAT FROM THE FIRE, WITHIN THE FIREPIT, HEATED THE 1 1/4" STEEL CASING LINE THEREFORE CREATING A HOLE IN THE 1/2" PLASTIC SERVICE LINE THAT WAS INSERTED WITHIN THE 1 1/4" STEEL CASING LINE. THIS HOLE ALLOWED GAS TO ESCAPE INSIDE THE CASING AND TRAVEL TO THE RESIDENTIAL HOME IT WAS SERVING, 558 N. RYBOLT AVE. ACCUMULATION OF THE NATURAL GAS OCCURRED WITHIN THE HOME AND WAS IGNITED BY THE CUSTOMER WHEN HE TRIED TO LIGHT A CIGARETTE. CEG'S OWN INVESTIGATION FINDINGS WERE CONSISTENT WITH THE FIRE DEPARTMENT'S.
2026-06-30 10:38 | NO | YES | NO | 20210098 | 36039 | 2021-11-23 19:13 | ORIGINAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2021-10-28 12:50 | PACIFIC | YES | 2021 | 6997 W CHRISTINE ST | RATHDRUM | KOOTENAI | ID | 83858 | 47.8134 | -116.8803 | [5 empty] | YES |  |  |  | 2021-10-28 14:52 | 1320698 | 1320844 | NATURAL GAS |  | 110 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-10-28 12:46 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 8 | YES | 38 | 2021-10-28 12:46 | YES | OPERATOR | 2021-10-28 12:48 | 2021-10-28 10:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2016 | 2015 |  |  |  |  | 2 | ASTM D2513 | POLYPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 750000 | 828570.82020270825 | 27619 | 30512.396644238132209 | 0 | 0 | 0 | 0 |  | 5.27 | 580 | 467.275747508305647840531561461794019934 | 0 | 0 | 778199 | 349219.6136725637229281794019933554817276 | 859550.4925944546878568405315614617940199 | 0 | 0 | 1 | 1 | 1 | 15 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 2016-04-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 3.8 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2021440198 | PASSWORD |  | CONTRACT LOCATOR | YES | YES | 2 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | BRIAN SCHULTZ | PIPELINE INTEGRITY PROGRAM MANAGER | brian.schultz@avistacorp.com | 509-495-2162 |  | JOSH FORT | josh.fort@avistacorp.com | 509-495-2656 | VERN MALENSKY | MANAGER NATURAL GAS INTEGRITY AND COMPLIANCE | 509-495-2706 | vern.malensky@avistacorp.com | AT APPROXIMATELY 10:00 A.M. PDT ON OCTOBER 28, 2021, PG CONTRACTORS, A THIRD-PARTY CONTRACTOR, WAS INSTALLING TELECOMMUNICATIONS INFRASTRUCTURE USING A HORIZONTAL DIRECTIONAL DRILL WHEN THEY SEVERED A 2" POLYETHYLENE (PE) MAIN AT THE INTERSECTION OF CHRISTINE STREET AND BEECHWOOD STREET IN FRONT OF 6997 W CHRISTINE ST., RATHDRUM, IDAHO. THE PE PIPE OPERATED AT A PRESSURE OF APPROXIMATELY 55 PSIG WITH AN MAOP OF 60 PSIG, WAS AT A DEPTH OF 36 INCHES, AND LOCATE MARKS WERE PRESENT AND ACCURATE. AVISTA WAS NOTIFIED AT 10:13 A.M. PDT AND WAS ON SITE AT 10:20 A.M. PDT. THE NORTHERN LAKES FIRE DISTRICT RESPONDED AND EVACUATED 3 NEARBY RESIDENCES AT 6971, 6997 AND 7025 W CHRISTINE STREET. THE LOCATION OF THE DAMAGE REQUIRED SQUEEZING THE 2" MAIN IN THREE LOCATIONS AS IT WAS CLOSE TO A TEE. THE SQUEEZES WERE COMPLETE AT 11:43 A.M. PDT TO CONTROL THE FLOW OF GAS. THE FIRE DEPARTMENT LEFT ONCE THE SCENE WAS SECURE. UNDERGROUND BARHOLE READINGS WERE TAKEN IN FRONT OF THE THREE EVACUATED HOUSES AND SHOWED 0 PERCENT LEL. INSIDE GAS READINGS WERE TAKEN AT 6997 W CHRISTINE STREET AT APPROXIMATELY 12:10 P.M. PDT AND SHOWED READINGS BETWEEN 10% AND 70% LEL. THE GAS SERVICEMAN EXITED THE HOUSE AND LEFT THE DOORS OPEN TO AIR OUT THE HOUSE. AT APPROXIMATELY 12:30 P.M. PDT THE HOMEOWNERS AT 7025 W CHRISTINE STREET CAME HOME AND REQUESTED TO ENTER THEIR HOUSE. A GAS SERVICEMAN CHECKED EACH ROOM OF THE HOUSE WITH A COMBUSTIBLE GAS INDICATOR AND FOUND READINGS OF 0% LEL, SO THE GAS SERVICEMAN CLEARED THE HOUSE FOR THE HOMEOWNERS TO REENTER. SHORTLY THEREAFTER, THE HOMEOWNERS AT 6997 W CHRISTINE STREET REQUESTED TO GET BACK INTO THEIR HOUSE. THE GAS SERVICEMAN CHECKED EACH ROOM WITH A COMBUSTIBLE GAS INDICATOR, WHICH NOW READ 0% LEL AND HE ALLOWED THE HOMEOWNERS BACK IN THEIR HOUSE. AT THIS TIME, THE GAS AND ELECTRICITY WERE STILL SHUT OFF TO THE HOUSE AND THE ELECTRIC METER HAD TO BE RE-INSTALLED. AFTER TURNING THE ELECTRICITY BACK ON THE HOMEOWNER REPORTED POPPING NOISES COMING FROM THE FURNACE. THE GAS SERVICEMAN CHECKED NEAR THE FURNACE AND FOUND 0% LEL AND DECIDED TO TURN THE FURNACE OFF AT THE THERMOSTAT. WHILE ENTERING THE HOUSE FROM THE GARAGE, THE GAS SERVICEMAN SAW A RED GLOW ABOVE HIS HEAD WHICH WAS AN IGNITION OF GAS AT APPROXIMATELY 12:46 P.M. PDT. THE GAS SERVICEMAN EXITED THROUGH THE OPEN GARAGE DOOR AND THE MALE HOMEOWNER EXITED THROUGH THE REAR GARAGE ACCESS DOOR. INDIVIDUALS ON SCENE THEN HELPED TO GET THE FEMALE HOMEOWNER OUT OF THE UPSTAIRS OF THE HOUSE THROUGH A WINDOW. SHORTLY THEREAFTER THE BUILDING WAS CONSUMED BY FLAMES. OPERATOR PERSONNEL ON SCENE CALLED 911 IMMEDIATELY AFTER THE GAS IGNITED AND THE NORTHERN LAKES FIRE DISTRICT WAS ON SCENE AT APPROXIMATELY 12:57 P.M. PDT. THE FEMALE HOMEOWNER WAS ASSESSED BY EMTS ON SITE AND THE MALE HOMEOWNER WENT TO THE HOSPITAL TO BE TREATED FOR SECOND DEGREE BURNS ON HIS FOREARM BUT WAS NOT ADMITTED. PRELIMINARY INVESTIGATION SUGGESTS THAT THERE WAS A POCKET OF GAS INSIDE THE HOUSE IN A LOCATION THAT COULD NOT BE DETECTED BY THE GAS SERVICEMAN'S INSTRUMENT. IT WAS THAT POCKET OF GAS THAT IGNITED CAUSING THE FIRE. THE BUILDING WAS DEEMED A TOTAL LOSS WITH A VALUE EXCEEDING $122,000 RESULTING IN THIS INCIDENT BEING REPORTABLE. AVISTA DENIES LIABILITY FOR DAMAGES AND INJURIES ASSOCIATED WITH THIS INCIDENT.
2026-06-30 10:38 | NO | NO | NO | 20210099 | 37698 | 2021-11-24 21:01 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2021-10-24 21:35 | CENTRAL | YES | 2021 | 1146 N 32ND ROAD | OTTAWA | LASALLE | IL | 61373 | 41.3961 | -88.9442 |  |  |  | YES | [5 empty] | 2021-10-25 01:08 | 1320321 | 1320522 | NATURAL GAS |  | 3.75 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-10-24 21:35 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 3.75 | NO | 0 | 2021-10-24 22:18 |  |  |  | 2021-10-24 23:11 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2020 | 2020 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | BACK OF METER BLOW OUT DUE TO ELECTRICAL DISCHARGE | CLASS 1 LOCATION | 75000 | 82857.082020270825 | 150 | 165.71416404054165 | 500 | 552.3805468018055 | 0 | 0 |  | 6.53 | 24 | 19.33554817275747508305647840531561461794 | 0 | 0 | 75674 | 33952.2563235684235405315614617940199336 | 83594.5122792859296250830564784053156146 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0.25 | 0.25 | 0.3 | 192.619(A)(1) | 2020-10-16 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [186 empty] | YES | [31 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | lquezad@southernco.com | [5 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | 6305142036 | lquezad@southernco.com | ON THE DATE OF THE INCIDENT, THERE WERE THUNDERSTORMS AND HIGH WINDS. IT IS BELIEVED THAT A LIGHTNING STRIKE DAMAGED A NEARBY POWER LINE. THE STATE FIRE MARSHAL INVESTIGATED THIS FIRE. THEIR INVESTIGATION SHOWS THAT CORNBELT ELECTRIC WAS AT THIS PROPERTY ABOUT ONE HOUR BEFORE THE FIRE WORKING ON A DROPPED NEUTRAL LINE. CORNBELT MADE THE REPAIRS AND MOVED ON. THE ELECTRIC AND GAS ENTER THE BUILDING IN THE SAME AREA. FIRE MARSHAL STATED THERE WERE TWO THEORIES. 1. THE DAMAGED POWER LINE MAY HAVE STARTED THE FIRE AND DROPDOWN MAY HAVE DAMAGED THE METER SET AND CAUSED THE GAS RELEASE. 2. LIGHTNING MAY HAVE STRUCK THE METER SET AND BEGAN THE FIRE. A SUB SURFACE LEAKAGE SURVEY WAS CONDUCTED OVER THE MAIN AND SERVICE LINE AND NO LEAKS WERE FOUND BELOW GRADE. THIS SERVICE LINE HAS A PROPERTY LINE REGULATOR. A GRADE 3 LEAK WAS FOUND ON THE ABOVEGROUND PROPERTY LINE REGULATOR PIPING. THIS MINOR LEAK DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. NOTE: RECORDS INDICATE THAT THE SERVICE LINE WAS INSTALLED IN 1969, BUT THE METER SET WAS COMPLETELY REPLACED ON 10-16-20. SUPPLEMENTAL/FINAL REPORT SUBMITTED PER PHMSA AID REQUEST TO UPDATE THE INFORMATION IN A-4.
2026-06-30 10:38 | NO | NO | NO | 20210100 | 36071 | 2021-12-02 13:17 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-11-03 08:35 | EASTERN | NO | 2021 | DORMANSVILLE BLVD & CHURCH RD. | UPPER MARLBORO | PRINCE GEORGES | MD | 20774 | 38.8831 | -76.7594 | YES | YES |  |  |  | YES |  |  |  | 2021-11-03 13:54 | 1321098 | 1321235 | NATURAL GAS |  | 1150 | 2587 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-11-03 08:39 | YES | OPERATOR | 2021-11-03 08:43 | 2021-11-03 08:49 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 108 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2006 | 2006 |  |  |  |  | 8 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 3 | 2 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 235 | 259.618856996848585 | 10018 | 11067.496635720974998 | 383 | 423.123498850183013 | ADMIN FEE | 3.96 | 4554 | 3668.920265780730897009966777408637873754 | 10245 | 8253.862126245847176079734219269102990033 | 25435 | 14481.6054948145792757740863787375415282 | 23673.0213835945846690897009966777408638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 55 | 192.619(A)(2) | 2006-09-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE 8" PL NATURAL GAS LINE WAS A TWO-WAY FEED SYSTEM AND PRESSURE DID NOT DROP BELOW ALARM SET POINT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 21845297 | MARYLAND 811 |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RICHARD FITZPATRICK | SUPERVISOR PIPELINE SAFETY | richardfitzpatrick@washgas.com | 7036397825 |  | SHANNON MALONEY | smaloney@washgas.com | 7037505558 | SHANNON MALONEY | MANAGER DOT PIPELINE SAFETY | 7037505558 | smaloney@washgas.com | ON NOVEMBER 3, 2021, WASHINGTON GAS WAS NOTIFIED OF A DAMAGED FACILITY NEAR DORMANSVILLE BLVD. AND CHURCH RD. UPPER MARLBORO MD. WASHINGTON GAS DISPATCHED CREWS IN RESPONSE TO THE BROKEN LINE. ONCE ARRIVED, THE DAMAGED WAS DETERMINED TO BE A TWO-WAY FEED 8" PLASTIC MAIN. THE MAIN WAS STRUCK ON A CONSTRUCTION SITE BY A BACKHOE WITH A 48" BUCKET. NO TRAFFIC WAS AFFECTED DUE TO NEW CULVERT AND BRIDGE WAS BEING CONSTRUCTED. THE GAS MAIN WAS APPROXIMATELY 10' UNDER A CREEK BED KNOWN AS BLACK BRANCH HAD BEEN PREVIOUSLY BEEN DIVERTED DUE TO THE CONSTRUCTION OF A NEW BRIDGE. THE EXCAVATOR PLEASANTS CONSTRUCTION DID HAVE A VALID MISS UTILITY TICKET BUT FAILED TO MAINTAIN MARKS IN THE EXCAVATION AREA. WASHINGTON GAS EXCAVATED ON EACH SIDE OF THE DAMAGED FACILITY AND PERFORMED A SQEEZE OFF. THE WORK AREA WAS MADE SAFE TO ENTER TO COMMENCE REPAIRS.
2026-06-30 10:38 | NO | YES | NO | 20210101 | 36147 | 2021-12-16 14:01 | SUPPLEMENTAL FINAL | 18408 | DOMINION ENERGY SOUTH CAROLINA, INC. | 601 TAYLOR ROAD | CAYCE | SC | 29033 | 2021-11-22 12:09 | EASTERN | NO | 2021 | 301 EL BETHEL ROAD | CONWAY | HORRY | SC | 29568 | 33.8613 | -79.092 | YES | [8 empty] | 2021-11-22 18:25 | 1322715 | 1322830 | NATURAL GAS |  | 162.34 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-11-22 12:09 | YES | OPERATOR | 2021-11-22 17:31 | 2021-11-22 12:33 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 204 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2014 | 2014 |  |  |  |  | 6 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 5.5 | 5.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 156189 | 172551.530448854398479 | 0 | 0 | 0 | 0 | N/A | 8.64 | 1403 | 1130.323920265780730897009966777408637874 | 0 | 0 | 157592 | 70986.7908735354669197408637873754152824 | 173681.8543691201792098970099667774086379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 45 | 60 | 192.619(A)(2) | 2014-07-14 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE CHANGE DUE TO THE LEAK WAS NOT SUBSTANTIAL ENOUGH TO BE OBSERVED BY THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | WATER | YES | 2111022187 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | JERAMY FREE | ENGINEER III - PIPELINE COMPLIANCE | jeramy.free@dominionenergy.com | 803-260-3602 |  | DONALD WATFORD | donald.watford@dominionenergy.com | 843-745-7984 | CINDY OSTRANDER | DIRECTOR - GAS OPERATIONS | 803-817-9245 | cynthia.ostrander@dominionenergy.com | SUPPLEMENTAL REPORT CREATED TO CHANGE A4 TO 12:09 P.M. WHEN THE DAMAGE WAS DONE. ON NOVEMBER 22, 2021, AT APPROXIMATELY 12:09 P.M., DOMINION ENERGY SOUTH CAROLINA (DESC) GAS OPERATIONS RESPONDED TO A NOTIFICATION FROM A THIRD PARTY CONTRACTOR CONCERNING A NATURAL GAS LEAK NEAR 301 EL BETHEL ROAD IN CONWAY, SC. THE CONTRACTOR WAS PERFORMING A DIRECTIONAL DRILLING OPERATION TO INSTALL A WATER LINE PARALLEL TO THE DESC 6-INCH PLASTIC GAS MAIN. THE BORING CONTRACTOR HAD PROPERLY NOTIFIED SC811 AND THE GAS FACILITIES WERE ACCURATELY LOCATED AND MARKED. THE CONTRACTOR PERFORMED THE BORE, AND WHILE PERFORMING THE PULL BACK, THE BORING EQUIPMENT DRIFTED OFF THE ORIGINAL BORE PATH INTO THE NATURAL GAS LINE, CAUSING A LEAK. DESC OPERATIONS CREWS WERE ABLE TO ISOLATE THE LEAK AT APPROXIMATELY BY OPERATING TWO ISOLATION VALVES. NO CUSTOMERS' GAS SERVICE WAS LOST AND THE LEAK GARNERED AND NO MEDIA COVERAGE. THE DAMAGED GAS MAIN REQUIRED EXTENSIVE REPAIRS AND A NEW GAS MAIN WAS INSTALLED. THE TOTAL COST OF THE REPAIR WAS APPROXIMATELY $156,189, WHICH EXCEEDED THE REPORTABLE THRESHOLD OF $122,000. LDF: 322718
2026-06-30 10:38 | NO | NO | NO | 20210102 | 36161 | 2021-12-20 19:51 | ORIGINAL FINAL | 39257 | INTERIOR GAS UTILITY | 2525 PHILLIPS FIELD ROAD | FAIRBANKS | AK | 99709 | 2021-11-21 17:10 | ALASKA | NO | 2021 | 2942 TRIA ROAD | FAIRBANKS | FAIRBANKS NORTH STAR BOROUGH | AK | 99709 | 64.8038 | -147.7973 | YES |  |  | YES | [5 empty] | 2021-11-22 10:10 | 1322689 | 1322785 | NATURAL GAS |  | 559 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-11-21 17:14 | NO |  |  | 2021-11-21 17:44 |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2019 | UNKNOWN |  |  |  |  | 8 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | RUPTURE |  |  |  |  | OTHER | SPIRAL | 120 | 0.5 |  | CLASS 2 LOCATION | 10000 | 11047.61093603611 | 32000 | 35352.354995315552 | 25000 | 27619.027340090275 | 0 | 0 |  | 11.704 | 6543 | 5271.353820598006644518272425249169435216 | 0 | 0 | 73543 | 34349.2925499449685249169435215946843854 | 79290.3470920399436445182724252491694352 | 91 | 0 | 48 | 0 | 0 | 144 | 91 | 62 | 55 | 60 | 192.621 M | 1998-06-01 | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | INJECTION PUMP |  |  | YES | YES | YES | NO | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [6 empty] | YES |  | YES | YES |  |  |  | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | INCORRECT OPERATION | INCORRECT VALVE POSITION | [222 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  | YES |  |  |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [37 empty] | YES | [6 empty] | YES |  | YES |  |  | ERIK WEFLEN | MECHANICAL ENGINEER | eweflen@interiorgas.com | 9074527111 | 9074578111 |  |  |  | DAN BRITTON | GENERAL MANAGER | 9074527111 | dwbritton@interiorgas.com | THE INTERIOR GAS UTILITY (IGU) LNG STORAGE AND VAPORIZATION SITE NUMBER 3 (SS3) IN FAIRBANKS, ALASKA SENT COLD GAS AND POSSIBLY LNG TO THE DISTRIBUTION SYSTEM. WHEN THE COLD GAS OR LNG ENTERED THE DISTRIBUTION SYSTEM, IT EMBRITTLED THE 8' UNDERGROUND HDPE PIPE, WHICH SUBSEQUENTLY RUPTURED IN A SECTION OF PIPING WITHIN IGU PROPERTY. THE HIGHEST RECORDED PRESSURE DOWNSTREAM OF THE DISTRIBUTION REGULATORS AT SS3 WAS 62PSIG. AT APPROXIMATELY 4:10PM ON 11/21/2021, A TEMPERATURE SWITCH ON THE OUTLET OF THE VAPORIZER MALFUNCTIONED AND CLOSED A VALVE TO STOP THE FLOW OF LNG THROUGH THE VAPORIZER. WITH NO LNG TO VAPORIZE, THE GLYCOL HEATER TURNED OFF DUE TO LOW DEMAND. AT ABOUT 4:55PM, AN OPERATOR NOTICED THAT THE FLOW OF LNG HAD STOPPED, AND THE DISTRIBUTION PRESSURE WAS DROPPING. THE OPERATOR OPENED THE CLOSED VAPORIZER VALVE VIA REMOTE CONTROL. THE OPERATOR DID NOT NOTICE THAT THE BOILER WAS NOT FIRING AND DID NOT MONITOR THE SITE LONG ENOUGH TO VERIFY THE SYSTEM WAS STABLE AND PROPER TEMPERATURES WHERE BEING MAINTAINED. DUE TO THE MALFUNCTIONING TEMPERATURE SWITCH AND A TEMPERATURE TRANSMITTER THAT HAD NOT BEEN PROGRAMMED TO ACT AS A BACKUP TO THE TEMPERATURE SWITCH, THE CONTROL SYSTEM DID NOT STOP THE FLOW OF LNG THROUGH THE VAPORIZER, UPON A LOW GAS TEMPERATURE ON THE OUTLET OF THE VAPORIZER. THE BOILER ATTEMPTED TO FIRE ABOUT THREE MINUTES AFTER THE LNG FLOW RESUMED BUT FAILED TO STAY RUNNING. THE SYSTEM ATTEMPTED TO START A BACK-UP BOILER ABOUT 10 MINUTES LATER, ABOUT WHEN THE DISTRIBUTION LINE RUPTURED. THE STANDARD OPERATING PROCEDURES WILL BE REVISED TO NO LONGER ALLOW CONTROL CHANGES FROM VIA REMOTE CONTROL (EXCEPT FOR EMERGENCY SHUT DOWNS AND SPECIFIED EXCEPTIONS) AND INSTEAD REQUIRE THE MONITORING OPERATOR TO TRAVEL TO THE SITE TO MAKE THE NECESSARY ADJUSTMENTS AND CHANGES. THE VAPORIZER TEMPERATURE SWITCHES WILL BE RECOMMISSIONED, AND THE TEMPERATURE TRANSMITTERS WILL BE ADDED INTO THE VAPORIZER SHUTDOWN PROGRAMMING LOGIC TO ADD REDUNDANCY. ADDITIONALLY, A DOWNSTREAM TEMPERATURE TRANSMITTER LOCATED ON THE METER SKID WILL BE USED TO SHUT DOWN THE LNG PUMPS IF LOW TEMPERATURE IS DETECTED INDICATING THE VAPORIZER SHUTDOWNS FAILED TO ACTIVATE AS A RESULT OF LOW OUTLET TEMPERATURE.
2026-06-30 10:38 | NO | YES | NO | 20210104 | 36172 | 2021-12-22 13:18 | ORIGINAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2021-11-29 11:00 | MOUNTAIN | NO | 2021 | 920 11TH STREET | RAPID CITY | PENNINGTON | SD | 57701 | 44.0777 | -103.2375 | [5 empty] | YES |  |  |  | 2021-11-29 11:28 | 1323119 | 1323315 | NATURAL GAS |  | 46.28 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-11-29 11:00 | ALLOWED TO BURN OUT |  | 10.85 | YES | 4 | 2021-11-29 10:27 | YES | OPERATOR | 2021-11-29 10:27 | 2021-11-29 10:27 |  | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | INSIDE RESIDENTIAL STRUCTURE. | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1967 | UNKNOWN |  |  |  |  | 1 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | THIRD PARTY DAMAGE PULLED DISTRIBUTION MAIN APART AT AN ELBOW FITTING CONNECTION. | CLASS 3 LOCATION | 210000 | 231999.82965675831 | 8000 | 8838.088748828888 | 6500 | 7180.9471084234715 | 0 | 0 |  | 6.22 | 288 | 232.026578073089700996677740863787375415 | 0 | 0 | 224788 | 100899.4291747040350863787375415282392027 | 248250.8920920837592009966777408637873754 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 30 | 30 | 34 | 192.619(A)(1) | 1993-09-17 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2129918149 |  |  | CONTRACT LOCATOR | NO | YES | 3 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | GREG WATKINS | MANAGER POLICY AND PROCEDURE | greg.watkins@mdu.com | 2083776032 |  | GREG WATKINS | greg.watkins@mdu.com | 2083776032 | GREG WATKINS | MANAGER POLICY AND PROCEDURE | 2083776032 | greg.watkins@mdu.com | ON NOVEMBER 29, 2021 AT 9:22 A.M. MST, AN EXCAVATOR NOTIFIED MONTANA-DAKOTA UTILITIES CO. (MDU) THAT THEY DAMAGED A 1" MAIN NEAR 920 11TH STREET, RAPID CITY, SOUTH DAKOTA. AN MDU FIRST RESPONDER ARRIVED AT 10:27 A.M. MST AND AFTER CHECKING IN WITH LOCAL FIRE DEPARTMENT PERSONNEL ON SCENE, BEGAN INVESTIGATING. WHILE THE MDU EMERGENCY RESPONDERS WERE WORKING TO SECURE THE DAMAGE, THE LEAKING NATURAL GAS CAUSED BY THE EXCAVATION DAMAGE MIGRATED AND SUBSEQUENTLY IGNITED CAUSING AN EXPLOSION AND A FIRE AT 920 11TH STREET. AN MDU CREW EXCAVATED AND SQUEEZED THE 2" STEEL MAIN UPSTREAM OF THE DAMAGED 1" MAIN. THE INVESTIGATION DETERMINED THE THIRD-PARTY EXCAVATOR LOCATE TICKET EXPIRED PRIOR TO COMMENCING WORK ON THE DATE OF THE INCIDENT.
2026-06-30 10:38 | NO | YES | NO | 20210106 | 38029 | 2021-12-23 11:31 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2021-12-01 00:55 | EASTERN | NO | 2021 | 58 VERMONT STREET | BROOKLYN | KINGS | NY | 11207 | 40.6786 | -73.8959 |  |  | YES | [6 empty] | 2021-12-01 15:47 | 1323353 | 1323471 | NATURAL GAS |  | 3.95 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-01 00:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 3.95 | YES | 6 | 2021-12-01 00:55 |  |  |  | 2021-12-01 01:11 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES |  |  |  | OTHER | METER | [9 empty] | OTHER | [8 empty] | METER TAMPERING OCCURRED RESULTING IN A NATURAL GAS EXPLOSION. | CLASS 4 LOCATION | 129300 | 142845.6094029469023 | 2000 | 2209.522187207222 | 5369 | 5931.462311557787459 | 0 | 0 |  | 7.21 | 28 | 22.55813953488372093023255813953488372093 | 0 | 0 | 136697 | 61327.9388249882034959534883720930232558 | 151009.1520412467954799302325581395348837 | 0 | 0 | 3 | 2 | 0 | 3 | 0 | 0.29 | 0.29 | 0.3 | 192.623 | 2009-05-23 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.1 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO SYSTEM CHANGES, ALARMS, OR ABNORMALITIES DURING THE TIME OF THE INCIDENT, AND INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NOT NECESSARY. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | THEFT OF TRANSPORTED COMMODITY | [156 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 5169030596 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | UPDATE 5/10/2023: WE HAVE REVIEWED THIS INCIDENT IN DETAIL AND HAVE REASON TO BELIEVE THAT THERE WAS INTENTIONAL DAMAGE TO THE METERING EQUIPMENT IN AN EFFORT TO STEAL OR ATTEMPT TO STEAL, THE TRANSPORTED GAS. ALSO, COST TO CUSTOMER PROPERTY UNKNOW; THEREFORE WE APPLIED THE MINIMUM REPORTABLE ESTIMATE OF $129,300. THIS WILL BE OUR FINAL SUBMITTAL FOR THIS INCIDENT. NATIONAL GRID WAS NOTIFIED ON 12/1/2021 AT 00:54 REGARDING A FIRE/DISTURBANCE AT 58 VERMONT ST., BROOKLYN NY BY THE FDNY. FIRST RESPONDER WAS DISPATCHED AT 00:55 AND ARRIVED AT 01:11. FDNY WAS ONSITE. LOCATION WAS MADE SAFE AT 01:32 BY SHUTTING THE CURB VALVES AT 54, 56, 58 AND 60 VERMONT ST. SERVICE TO THE RESIDENCE INVOLVED IN THE FIRE, 58 VERMONT ST, WAS LATER DISCONNECTED AT THE MAIN ON 12/2 AT 10:30. TWO RESIDENTS WERE TAKEN TO A NEARBY HOSPITAL FOR OBSERVATION. THE CAUSE OF THE FIRE AND EXPLOSION IS CURRENTLY UNKNOWN AND UNDER INVESTIGATION AS OF 12/8/2021. AS OF 12/8, WE HAVE NOT BEEN GRANTED ACCESS TO THE PREMISES SINCE THE TIME OF THE INCIDENT. AS OF 12/23 WE STILL HAVE NOT BEEN GRANTED ACCESS. FOR QUESTION A4, THE TIME AN INCIDENT CRITERIA WAS MET IS ESTIMATED. THE EXACT TIMELINE FOR FIRE AND DISTURBANCE IS NOT FULLY DIFFERENTIATED. FURTHERMORE, AT THE TIME OF REPORTING, IT IS STILL NOT KNOWN WHERE THE INCIDENT INITIATED AND WHETHER IT OCCURRED ON CUSTOMER-OWNED OR COMPANY-OWNED PIPING OR EQUIPMENT FOR REPORTING PURPOSES. FOR QUESTION E3B, INFORMATION IS FOR SERVICE PIPING.
2026-06-30 10:38 | NO | YES | NO | 20210107 | 36290 | 2021-12-23 11:51 | SUPPLEMENTAL FINAL | 31588 | COSERV GAS, LTD | 7701 SOUTH STEMMONS | CORINTH | TX | 76210 | 2021-12-03 20:58 | CENTRAL | NO | 2021 | 971 HWY. 121 | ALLEN | COLLIN | TX | 75013 | 33.1412 | -96.6793 | [5 empty] | YES |  |  |  | 2021-12-03 20:56 | 1323575 | 1323797 | NATURAL GAS |  | 59.065 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-03 20:24 | OPERATOR/CONTRACTOR |  | 0 | NO | 40 | 2021-12-03 20:24 |  |  |  | 2021-12-03 21:19 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2020 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | YES |  |  |  | OTHER | METER SET | [9 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 600000 | 662856.6561621666 | 50100 | 55348.5307895409111 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 650100 | 291634.1623371094578 | 718205.1869517075111 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 50 | 60 | 192.621 M | 2020-10-28 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 285 | NO | [142 empty] | RODNEY HALE | GAS COMPLIANCE MANAGER | rhale@coserv.com | 19402180258 |  | JASON WALKER | jawalker@coserv.com | 19729787928 | JASON WALKER | DIRECTOR OF GAS OPERATIONS | 19729787928 | jawalker@coserv.com | THE DRIVER WAS TRAVELING EAST ON RIDGEVIEW DR. AND FAILED TO CONTROL HIS SPEED AND LOST CONTROL OF THE VEHICLE. THE VEHICLE STRUCK THE CENTER MEDIAN, CROSSED THE WESTBOUND LANES, AND TRAVELED INTO THE BACK ENTRYWAY OF LIFETIME FITNESS. THE VEHICLE HIT THE GAS METER AT THE BACK OF THE LIFETIME FITNESS BUILDING AT 971 HWY. 121 IN ALLEN TX. IGNITING A FIRE. THE CAR WAS ON FIRE AND SITTING ON THE CURB VALVE. THE VALVE COULD NOT BE ACCESSED TO SHUT THE GAS OFF SO THE POLYETHYLENE GAS LINE FEEDING THE METER HAD TO BE EXCAVATED AND SQUEEZED TO STOP THE FLOW OF GAS AND PUT OUT THE FIRE.* THERE ARE SEVERAL NATURAL BARRIERS THAT WOULD PREVENT SOMETHING LIKE THIS FROM EVER HAPPENING AGAIN. THE CAR HAD TO BE ON ITS SIDE TO BE ABLE TO FIT BETWEEN THE CONCRETE WALL AND THE VERY LARGE TREE PROTECTING THE METER. THE VALVE WAS RE-LOCATED ACROSS THE STREET TO ENSURE THAT THERE WILL BE ACCESSIBLE IN THE EVENT SOMETHING ELSE HAPPENS TO THE METER.
2026-06-30 10:38 | NO | YES | YES | 20210108 | 36350 | 2021-12-31 17:15 | SUPPLEMENTAL FINAL | 2456 | CLARKE - MOBILE COUNTIES GAS DIST | 2003 COLLEGE AVENUE P.O. BOX 608 | JACKSON | AL | 36545 | 2021-12-01 17:24 | CENTRAL | NO | 2021 | 1177 ABB ROAD | CHATOM | WASHINGTON | AL | 36518 | 31.4419 | -88.197 |  |  |  | YES | [5 empty] | 2021-12-01 17:43 | 1323379 |  | NATURAL GAS |  | 0.126 | 0.126 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2021-12-01 11:23 | OPERATOR/CONTRACTOR |  | 0.12 | NO | 0 | 2021-12-01 11:23 | NO |  |  | 2021-12-01 11:23 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 18 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2021 | 2021 |  |  |  |  | 2 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | OTHER | [8 empty] | CONTROLLED RELEASE / PURGING OPERATIONS. | CLASS 3 LOCATION | 0 | 0 | 134 | 148.037986542883874 | 107 | 118.209437015586377 | 0 | 0 |  | 4.525 | 1 | 0.8056478405315614617940199335548172757475 | 1 | 0.8056478405315614617940199335548172757475 | 243 | 109.42463372666028471096345514950166113 | 267.858719239533373923588039867109634552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 60 | 192.619(A)(2) | 2021-11-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.6 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 4 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | THE UTILIZED GROUNDING TECHNIQUES (TO MITIGATE STATIC ELECTRICITY) WERE INCONSISTENT WITH CMC GAS POLICY. INCONSISTENT WITH CMC GAS POLICY, TECH 1 FAILED TO EMPLOY A VENT STACK ON THE VENT OUTLET TO DIRECT THE GAS FLOW UPWARD. (SEE NARRATIVE) |  |  | YES |  |  | COMMISSIONING | YES | NO, BUT THEY WERE PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | MIKE SASSER | COMPLIANCE MANAGER | msasser@cmcgas.com | 2512462428 |  | MIKE SASSER | msasser@cmcgas.com | 2512462428 | MIKE SASSER | COMPLIANCE MANAGER | 2512462428 | msasser@cmcgas.com | REPORTABLE INCIDENT NARRATIVE ON 1 DECEMBER 2021, AT APPROXIMATELY 11:23 HOURS, A CMC GAS CREW COMMISSIONING A NEW 2-INCH MDPE MAIN OF APPROXIMATELY 6,100 LF EXPERIENCED AN UNEXPECTED INCIDENT WHERE THE VENTING GAS IGNITED, INJURING ONE EMPLOYEE. INJURIES CONSISTED OF NON-LIFE-THREATENING BURNS ON HIS UPPER BODY. A 2.0 X 0.75-INCH, HIGH-VOLUME TAP WAS INSTALLED ON THE OUTLET END OF THE PIPELINE SEGMENT. NATURAL GAS WAS INTRODUCED INTO THE PIPELINE SEGMENT FROM THE SUPPLY END OF THE PIPELINE FROM A "FARM TAP" REGULATOR STATION. GAS FLOWED, PUSHING THE AIR OUT OF THE PIPELINE FOR APPROXIMATELY 8 MINUTES. AT APPROXIMATELY THE 8-MINUTE MARK OF THE PURGE, THE PURGE TECHNICIAN (TECH 1) ON THE SITE APPROACHED THE TAP TEE WHERE GAS WAS VENTING. AS TECH 1 REACHED FOR THE TAP, AN UNEXPECTED IGNITION OF THE GAS OCCURRED. BEFORE BEING ABLE TO REMOVE HIMSELF FROM THE FLASH, TECH 1 RECEIVED MINOR BURNS ON THE FACE AND ARM AREAS. THE FIRE-WATCH TECHNICIAN (TECH 3) NOTIFIED THE TECHNICIAN OPERATING THE SUPPLY VALVE (TECH 2) OF THE INCIDENT AND REQUESTED THE SUPPLY VALVE BE CLOSED. AS THE VOLUME OF GAS IN THE PIPE DIMINISHED, THE TECH 3 EXTINGUISHED THE SMALL FLAME. APPROXIMATE 5 MINUTES ELAPSED FROM THE TIME OF IGNITION UNTIL THE FLAME WAS EXTINGUISHED. ON-SITE PERSONNEL NOTIFIED THE CONSTRUCTION AND MAINTENANCE MANAGER, WHO NOTIFIED OTHER MANAGEMENT. ON SITE PERSONNEL TRANSPORTED THE INJURED TECHNICIAN TO THE LOCAL HOSPITAL EMERGENCY ROOM, APPROXIMATELY 3 MILES AWAY. TECH 1 WAS TREATED AND TRANSPORTED TO UNIVERSITY HOSPITAL IN MOBILE, ALABAMA, WHERE HE WAS ADMITTED FOR FURTHER TREATMENT AND OBSERVATION. CMC GAS PERSONNEL PLACED A PIPE SQUEEZE DEVICE ON THE 2-INCH MDPE PIPE UNTIL THE PIPE WAS CUT AND CAPPED. UPON NOTIFICATION OF THE HOSPITALIZATION OF TECH 1 AT 17:24 HOURS, THE COMPLIANCE MANAGER NOTIFIED THE ALABAMA PUBLIC SERVICE COMMISSION, PIPELINE SAFETY DIVISION OF THE INCIDENT, AND THE NATIONAL RESPONSE CENTER. THIS CALL WAS MADE AT 17:43 HOURS. TECH 1 WAS RELEASED FROM THE UNIVERSITY HOSPITAL ON DECEMBER 8TH AND WAS SUBSEQUENTLY RELEASED TO RETURN TO WORK ON 20 DECEMBER 2021. AT THE TIME OF THIS REPORT, THE INVESTIGATION HAS REVEALED THE FOLLOWING: 1) THE BELIEVED SOURCE OF IGNITION WAS STATIC ELECTRICITY. A. AT THE TIME OF THE IGNITION, THE AMBIENT AIR RELATIVE HUMIDITY WAS REPORTED AT 20% B. AT THE TIME OF THE IGNITION, THE AMBIENT AIR TEMPERATURE WAS REPORTED AT 72 DEGREES FAHRENHEIT. 2) THE UTILIZED GROUNDING TECHNIQUES (TO MITIGATE STATIC ELECTRICITY) WERE INCONSISTENT WITH CMC GAS POLICY. 3) INCONSISTENT WITH CMC GAS POLICY, TECH 1 FAILED TO EMPLOY A VENT STACK ON THE VENT OUTLET TO DIRECT THE GAS FLOW UPWARD. 4) TECH 2 (THE VALVE OPERATOR ON THE SUPPLY END OF THE PIPELINE) WAS DETERMINED TO BE WORKING OUTSIDE HIS OPERATOR QUALIFICATION. 5) TECH 1, WHO WAS ALSO MONITORING THE PURGE OF GAS DID NOT EMPLOY A COMBUSTIBLE GAS METER (CGI) OR A PERSONAL PROTECTIVE ATMOSPHERIC METER, INCONSISTENT WITH CMC GAS POLICY. 6) TECH 1 DID NOT DON THE FIRE-RESISTANT CLOTHING AND OTHER PERSONAL PROTECTIVE EQUIPMENT (PPE) WHICH WERE PROVIDED BY CMC GAS AND IS CMC GAS STANDARD PROCEDURE. MITIGATIVE MEASURES TAKEN TO PREVENT RECURRENCE: 1) ALL RELEVANT MEMBERS OF THE 12/01/21 INCIDENT CREW HAVE BEEN DISQUALIFIED, RETRAINED, AND REQUALIFIED ON RELEVANT OQ TASKS. 2) ALL RELEVANT MEMBERS OF THE 12/01/21 INCIDENT CREW HAVE ATTENDED A POLICY, STATIC MITIGATION, AND PPE REVIEW SESSION. 3) INTERNAL DISCIPLINARY ACTIONS TAKEN AS RELEVANT.
2026-06-30 10:38 | NO | YES | NO | 20220002 | 36243 | 2022-01-07 14:08 | SUPPLEMENTAL FINAL | 22763 | WISCONSIN GAS LLC DBA WE ENERGIES | 231 W. MICHIGAN STREET | MILWAUKEE | WI | 53203 | 2021-12-11 09:02 | CENTRAL | NO | 2021 | 517 WISCONSIN STREET | WAUPACA | WAUPACA | WI | 54981 | 44.3617 | -89.0944 |  |  | YES | [6 empty] | 2021-12-11 12:37 | 1324303 | 1324403 | NATURAL GAS |  | 19 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-11 09:09 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 17 | YES | 8 | 2021-12-11 09:12 |  |  |  | 2021-12-11 10:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1991 | 1991 | MULTI-FAMILY RESIDENTIAL | NO |  | YES |  |  |  | STEEL |  | FURNACE BUTT WELDED |  | 0.113 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 400000 | 441904.4374414444 | 1700 | 1878.0938591261387 | 1500 | 1657.1416404054165 | 200000 | 220952.2187207222 | BOILER, WATER HEATER, BUILDING CONTENTS | 10 | 190 | 153.073089700996677740863787375415282392 | 0 | 0 | 603390 | 270719.5404425134283375415282392026578073 | 666544.9647513991518777408637873754152824 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1991-06-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE METERSET WAS STRUCK BY A SNOW PLOW THEREFORE NO CONTROLLER OPPORTUNITY TO INFLUENCE THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | SMALL TRUCK | PARKING LOT | 8 | NO | [118 empty] | YES | [23 empty] | LISA NYSTROM | GAS SYSTEM ANALYST | lisa.nystrom@wecenergygroup.com | 920-433-5704 |  | LISA NYSTROM | lisa.nystrom@wecenergygroup.com | 920-433-5704 | TIM STROMMEN | MANAGER GAS CODE COMPLIANCE | 414-221-5173 | tim.strommen@we-energies.com | AT 9:12 AM ON 12/11/21, WISCONSIN GAS COMPANY WAS NOTIFIED THAT A GAS METER ASSEMBLY WAS HIT AT 517 WISCONSIN STREET, WAUPACA, WI AND THAT A FIRE/EXPLOSION HAD OCCURRED. A COMPANY FIRST RESPONDER WAS DISPATCHED TO THE SCENE AND UPON ARRIVAL FOUND THAT A TRACTOR WITH A SNOW PLOW HIT THE GAS METER ASSEMBLY WHILE REMOVING SNOW, RESULTING IN THE GAS RELEASE. THE RELEASE OF GAS WAS STOPPED AT 10:35 AM BY USE OF A SERVICE CURB VALVE. NO FATALITIES OR PERSONAL INJURIES NECESSITATING IN-PATIENT HOSPITALIZATION OCCURRED; HOWEVER, IT WAS DETERMINED THAT THE GAS RELEASE CAUSED DWELLING DAMAGES IN EXCESS OF THE 191.3 REPORTING THRESHOLD OF $122,000. THE INVESTIGATION IDENTIFIED A SEVERED PIPE NIPPLE AT THE INLET TO THE METER SET REGULATOR AS THE SOURCE OF GAS RELEASE AFTER BEING HIT DURING THE SNOW PLOWING OPERATION. EIGHT RESIDENTS WERE EVACUATED FROM THE DWELLING IMMEDIATELY AFTER THE METER SET WAS STRUCK AND THE DWELLING REMAINS UNINHABITABLE DUE TO THE DAMAGES.
2026-06-30 10:38 | NO | NO | NO | 20220003 | 36421 | 2022-01-07 14:10 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2021-12-08 16:43 | EASTERN | YES | 2021 | E. 11 MILE ROAD | ROYAL OAK | OAKLAND | MI | 48067 | 42.4899 | -83.1414 | [5 empty] | YES |  |  |  | 2021-12-08 23:49 | 1324037 | 1324232 | NATURAL GAS |  | 3421 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-12-08 16:43 | NO |  |  | 2021-12-08 17:08 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2016 | UNKNOWN |  |  |  |  | 4 | D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | MECHANICAL PUNCTURE | 3 | 9 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 575 | 635.237628822076325 | 15392 | 17004.482752746780512 | 0 | 0 |  | 4.18 | 14300 | 11520.7641196013289036544850498338870432 | 0 | 0 | 30267 | 16545.6694302641129093887043189368770764 | 29160.4845011701857406544850498338870432 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 55 | 55 | 60 | 192.619(A)(2) | 2016-07-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | WATER | YES | B013270027 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON WEDNESDAY, DECEMBER 8, 2021 AT APPROXIMATELY 16:43 HOURS, CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE EXCAVATION DAMAGE FROM THE CONTRACTOR PERFORMING (BORING) WORK IN THE 300 BLOCK OF ELEVEN MILE ROAD, ROYAL OAK, (OAKLAND COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 17:08 HOURS AND CONFIRMED A DAMAGED AND BLOWING 4-INCH NATURAL GAS PIPELINE AT 315 ELEVEN MILE ROAD. DISTRIBUTION EMPLOYEES WERE DISPATCHED AT 17:02 HOURS AND ARRIVED ONSITE AT APPROXIMATELY 18:34 HOURS. THE DISTRIBUTION CREW EXCAVATED AT REMOTE LOCATIONS AND APPLIED SQUEEZERS TO CONTAIN THE BLOWING GAS. THE DAMAGED PIPELINE SEGMENT WAS CUT OUT AND REPLACED WITH APPROXIMATELY 6-FOOT OF 4-INCH MEDIUM-PRESSURE PLASTIC PIPE AND NORMAL OPERATIONS RESUMED ON THURSDAY, DECEMBER 9, 2021 AT APPROXIMATELY 14:00 HOURS. THREE COMMERCIAL CUSTOMERS EXPERIENCED A LOSS OF SERVICE AS A RESULT OF THE DAMAGE AND SUBSEQUENT REPAIR. CONSUMERS ENERGY SERVICE EMPLOYEES REMAINED ONSITE AND CONTINUOUSLY MONITORED THE LOCATION UNTIL THE GAS WAS CONTAINED AND THE PIPELINE SEGMENT WAS REPAIRED. NO FATALITIES OR INJURIES OCCURRED AS A RESULT OF THE DAMAGE.
2026-06-30 10:38 | NO | YES | NO | 20220004 | 36224 | 2022-01-08 15:17 | SUPPLEMENTAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2021-12-09 09:19 | CENTRAL | NO | 2021 | 3111 WYANDOTTE ST | KANSAS CITY | JACKSON | MO | 64111 | 39.0707 | -94.5884 |  | YES |  |  |  |  | YES |  |  | 2021-12-09 11:14 | 1324107 | 13242511324239 | NATURAL GAS |  | 9519 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2021-12-09 09:19 |  |  |  | 2021-12-09 09:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1963 | UNKNOWN |  |  |  |  | 20 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 2.5 | 2.3 | [7 empty] | CLASS 3 LOCATION | 196989 | 217625.783067881727279 | 0 | 0 | 500 | 552.3805468018055 | 0 | 0 |  | 4.1195 | 39214 | 31592.6744186046511627906976744186046512 | 0 | 0 | 236703 | 114323.4697412962090838604651162790697674 | 249770.8380332881839417906976744186046512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 63 | 100 | 192.619(A)(3) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT RESULT IN ANY ABNORMAL PIPELINE OPERATION OR PRESSURES THAT CAUSED OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 213344010 |  |  | CONTRACT LOCATOR | NO | NO |  | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  | NICOLE CHRISTIANER | nicole.christianer@spireenergy.com | 314-349-2929 | CRAIG HOEFERLIN | VP OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A THIRD-PARTY CONTRACTOR WAS PERFORMING SEWER WORK AND WHILE BREAKING OUT A SEWER BOX THE COMPANY'S 20-INCH COATED STEEL GAS MAIN WAS STRUCK RESULTING IN A LEAK. A TEMPORARY REPAIR WAS MADE BY INSTALLING A STYLE 126 REPAIR SLEEVE. A PERMANENT REPAIR WAS MADE BY INSTALLING STOPPER FITTINGS TO ISOLATE THE SECTION OF MAIN AND REPLACE 13-FEET OF 20-INCH COATED STEEL MAIN. THE COMPANY'S FACILITIES WERE ACCURATELY MARKED ON DECEMBER 2, 2021 BUT WERE NO LONGER VISIBLE THE DAY OF THE INCIDENT. THE EXCAVATOR DID NOT REQUEST A RENEWAL OF THE LOCATE MARKS. A 48 HOUR UPDATE TO THE NRC WAS MADE ON DECEMBER 9, 2021 AT 15:46. REPORT NUMBER 1324251.
2026-06-30 10:38 | NO | NO | NO | 20220005 | 36217 | 2022-01-10 09:47 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-12-16 12:13 | EASTERN | YES | 2021 | 7224 ANNAPOLIS RD | HYATTSVILLE | PRINCE GEORGE COUNTY | MD | 20784 | 38.9481 | -76.89 |  | YES | [7 empty] | 2021-12-16 14:11 | 1324714 |  | NATURAL GAS |  | 67 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-16 11:44 | OPERATOR/CONTRACTOR |  | 67 | NO | 8 | 2021-12-16 12:13 |  |  |  | 2021-12-16 12:53 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 28 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1955 | UNKNOWN |  |  |  |  | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN FREQUENCY OR SEAMLESS | UNKNOWN | [6 empty] | OTHER | [8 empty] | ELECTRICAL ARC BURNT HOLE IN THE PIPE. SEE DESCRIPTION IN NARRATIVE. | CLASS 4 LOCATION | 500 | 552.3805468018055 | 108 | 119.314198109189988 | 8400 | 9279.9931862703324 | 383 | 423.123498850183013 | ADMINISTRATION COSTS | 3.01 | 202 | 162.740863787375415282392026578073089701 | 0 | 0 | 9593 | 4345.334050170897655807308970099667774086 | 10537.5522938188863162823920265780730897 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 20 | 20 | 25 | 192.619(A)(4) | 1970-11-12 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE 8" WRPD NATURAL GAS LINE WAS A TWO-WAY FEED SYSTEM AND PRESSURE DID NOT DROP BELOW ALARM SET POINT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [147 empty] | YES | [20 empty] | MARK AIESI | SUPERVISOR DOT PIPELINE SAFETY | mark.aiesi@washgas.com | 5714054623 |  | MARK AIESI | mark.aiesi@washgas.com | 5714054623 | SHANNON MALONEY | MANAGER DOT PIPELINE SAFETY | 7037505558 | smaloney@washgas.com | ON DECEMBER 16, 2021 AT APPROXIMATELY 1213 HOURS WASHINGTON GAS WAS NOTIFIED OF A GAS FED FIRE IN FRONT OF 7224 ANNAPOLIS ROAD, HYATTSVILLE, MD. WASHINGTON GAS DISPATCHED CREWS TO THE LOCATION WHO ARRIVED AND PERFORMED AN ASSESSMENT OF SITUATION, WHICH RESULTED IN THE IDENTIFICATION OF AN 8" WRPD MAIN LINE THAT WAS FEEDING THE CONTROLLED FIRE. NO WASHINGTON GAS CREWS, OR CONTRACTORS WERE WORKING AT THIS LOCATION AT THE TIME OF IGNITION. IT WAS DETERMINED THAT A TRANSFORMER SHORTED AT SURREY LANE AND ANNAPOLIS ROAD, WHICH RESULTED IN AN ELECTRICAL DISCHARGE THROUGH AN ADJACENT METAL FENCE INTO THE GROUND. THE METAL FENCE THAT IS ESTIMATED TO BE ROUGHLY 20 YEARS OLD WAS INSTALLED DIRECTLY OVER THE 8" WRPD MAIN. EVIDENCE SUGGESTS THAT THE ELECTRICAL DISCHARGE FROM THE TRANSFORMER TRAVELED DOWN THE FENCE AND DISCHARGED AT 7224 ANNAPOLIS ROAD, RESULTING IN AN ELECTRICAL ARC TO THE PIPE. THE GAS WAS TURNED OFF UTILIZING VALVES WHICH EXTINGUISHED THE FIRE. ONCE THE AREA WAS DEEMED SAFE, CREWS STARTED PERMANENT REPAIRS TO THE PIPE, INCLUDING ADDING NEW CATHODIC PROTECTION ANODES AND A TEST STATION. THE PIPE WAS REPAIRED USING A FULL SEAL CLAMP AND WAS NOT ABLE TO BE EXAMINED FOR PIPE SPECIFICATION AND WALL THICKNESS AS A RESULT. THERE WAS ONLY MINOR PROPERTY DAMAGE, WHICH WAS TO THE CHAIN LINK FENCE THAT HAD TO BE REMOVED TO REPAIR THE MAIN.
2026-06-30 10:38 | NO | YES | NO | 20220006 | 36261 | 2022-01-20 23:52 | ORIGINAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 3500 BLAKE ST | DENVER | CO | 80205 | 2021-12-21 08:52 | MOUNTAIN | NO | 2021 | 5723 SHADY OAKS DRIVE | WINDSOR | LARIMER | CO | 80528 | 40.4833 | -104.9838 | [5 empty] | YES |  |  |  | 2022-01-06 12:58 | 1326030 | 1326116 | NATURAL GAS |  | 299 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-21 08:47 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 299 | NO | 0 | 2021-12-21 08:52 | YES | OPERATOR | 2021-12-21 08:53 | 2021-12-21 08:52 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 32 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2021 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 17 |  |  | 2708 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 700000 | 773332.7655225277 | 21219 | 23441.925645175021809 | 2000 | 2209.522187207222 | 0 | 0 |  | 5.02 | 1501 | 1209.277408637873754152823920265780730897 | 0 | 0 | 724720 | 325420.1426838287156085780730897009966777 | 800193.4907635478175631528239202657807309 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 50 | 50 | 60 | 192.619(A)(2) | 2021-01-29 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | NO | [5 empty] | YES | 25 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | MARK NOLAN | PRINCIPAL ENGINEER | mark.nolan@xcelenergy.com | 303.571.3931 |  | TAMMY BOWIE | tammy.l.bowie@xcelenergy.com | 970-225-7865 | CHRIS AKINS | MANAGER PIPELINE COMPLIANCE | 303.571.3298 | christopher.a.akins@xcelenergy.com | A CONTRACTOR FOR HOME BUILDER WAS DIGGING TO LOWER WATER PIT WHEN 4" PE MAIN WAS DAMAGED AND BLOWING GAS IGNITED. NO LOCATE REQUEST WAS MADE; EXCAVATOR WAS DIGGING OFF OLD UTILITY MARKS. THE DAMAGED HOME AND SERVICE INTERRUPTIONS OCCURRED ON HOMES THAT WERE NOT YET SOLD OR OCCUPIED. LOCAL OPERATIONS OBSERVED THE FIRE AND RESPONDED TO SCENE BEFORE BEING NOTIFIED BY OUR DISPATCH OR LOCAL FIRE DEPARTMENT. A21A IGNITION TIME IS ESTIMATED, BUT GAS HAD IGNITED PRIOR TO OUR PERSONNEL'S ARRIVAL ON SCENE. D2A PROPERTY DAMAGE IS ESTIMATED.
2026-06-30 10:38 | NO | YES | NO | 20220007 | 37504 | 2022-02-04 19:20 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2022-01-06 14:13 | PACIFIC | NO | 2022 | 4244 BULLFROG RD | CLE ELUM | KITTITAS | WA | 98922 | 47.2059 | -120.9798 |  |  |  | YES | [5 empty] | 2022-01-06 20:39 | 1326070 | 1326135 | NATURAL GAS |  | 112 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-01-06 14:13 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 9 | NO | 0 | 2022-01-06 14:41 |  |  |  | 2022-01-06 15:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2008 | 2008 | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | YES |  |  |  | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | EQUIPMENT BODY SEPARATED BY EXTERNAL LOAD | CLASS 4 LOCATION | 510450 | 542708.76639344241375 | 9457 | 10054.651393442619075 | 1583 | 1683.040409836064925 | 0 | 0 |  | 11 | 1232 | 869.752547307132459970887918486171761281 | 0 | 0 | 522722 | 225846.7018887060296045123726346433770015 | 555316.2107440282302099708879184861717613 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 50 | 60 | 192.619(A)(2) | 2008-05-02 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 8.6 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | DAMAGE FROM SNOW/ICE | [56 empty] | SNOW/ICE IMPACT OR ACCUMULATION | [5 empty] | YES |  |  |  | YES | HEAVY SNOWFALL | [213 empty] | MICHAEL KIDD | REGULATORY COMPLIANCE ANALYST | michael.kidd@pse.com | [5 empty] | YVONNE WANG | SUPERVISOR COMPLIANCE SUPPORT | 425-424-7477 | yvonne.wang@pse.com | ON JANUARY 6, 2022, CLE ELUM FIRE DEPARTMENT CALLED PSE AT 14:41 NOTIFYING OF A FIRE AT A COMMERCIAL METER SET THAT PROVIDED TWO PSIG TO A LAUNDRY BUSINESS. PSE'S GAS FIRST RESPONSE (GFR) PERSONNEL ARRIVED ONSITE AT 15:30 AND FOUND THAT THE OUTLET VALVE AT THE METER SET HAD BEEN TURNED OFF PRIOR TO THEIR ARRIVAL. THE FIRE HAD ALREADY BEEN EXTINGUISHED BY CLE ELUM FIRE DEPARTMENT. PSE'S GFR MADE THE SITUATION SAFE AND LOCKED OFF THE MSA VALVE AT 19:30 ON JANUARY 6, 2022. PSE'S CONTRACTOR INFRASOURCE (IFS) CUT AND CAPPED THE SERVICE ON JANUARY 7, 2022 AT 19:41. ONE CUSTOMER LOST SERVICE AND NO EVACUATION WAS REQUIRED. NO INJURIES OR FATALITIES OCCURRED IN CONNECTION TO THIS INCIDENT. A FIRE OF UNKNOWN SOURCE AND ORIGIN IN THE BUILDING MELTED SNOW NEAR THE PEAK OF THE BUILDING. A LARGE AMOUNT OF SNOW AND ICE SLID OFF THE ROOF AND BROKE THE RELIEF VALVE VENT PIPING ON THE GAS METERSET. GAS LEAKING FROM THE BROKEN VENT PIPE WAS IGNITED BY THE FIRE IN THE BUILDING. PSE NOTIFIED THE WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION (WUTC) ON JANUARY 6, 2022 AT 17:30 DUE TO UNINTENTIONAL IGNITION OF GAS. PSE MADE FIRST TELEPHONIC NOTICE TO DOT ON JANUARY 6, 2022 AT 20:39, NRC # 1326070 WHEN IT WAS DETERMINED THAT THE ESTIMATED PROPERTY DAMAGES EXCEEDED $ 122,000. THE SECOND TELEPHONIC NOTICE WAS MADE TO DOT WITHIN 48 HOURS ON JANUARY 7, 2022 AT 16:22, NRC # 1326135.
2026-06-30 10:38 | NO | YES | NO | 20220008 | 36717 | 2022-02-07 11:14 | SUPPLEMENTAL FINAL | 7348 | DOMINION ENERGY WEST VIRGINIA | 781 CHESTNUT RIDGE RD | MORGANTOWN | WV | 26505 | 2022-01-08 20:00 | EASTERN | NO | 2022 | 305 POWELL STREET | GLENVILLE | GILMER | WV | 26351 | 38.9327 | -80.8371 |  | YES | [7 empty] | 2022-01-08 21:10 | 1326175 | 1326260 | NATURAL GAS |  | 7446 | 4265 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-08 11:00 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-08 12:00 | 2022-01-08 12:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1947 | UNKNOWN |  |  |  |  | 3 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 116531 | 123895.377131147493225 | 0 | 0 | 66638 | 70849.30311475407105 | 0 | 0 |  | 3.361 | 25026 | 17667.5545851528384279475982532751091703 | 14335 | 10120.0509461426491994177583697234352256 | 222530 | 101709.1035508387920483697234352256186317 | 222532.2857771970519023653566229985443959 | 51 | 0 | 111 | 0 | 0 | 111 | 51 | 2.18 | 0.5 | 0.75 | 192.623 | 1947-11-08 | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONS PERSONNEL WERE ALREADY MONITORING SYSTEM PRESSURES DUE TO COLD WEATHER AND WERE AWARE OF THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [40 empty] | YES |  | YES | [30 empty] | CHELSEA MINUTELLI | GAS PIPELINE COMPLIANCE ANALYST | chelsea.m.minutelli@dominionenergy.com | 3046769284 |  | CHELSEA MINUTELLI | chelsea.m.minutelli@dominionenergy.com | 3046769284 | CAROL HAGER | MANAGER- GAS OPERATIONS PIPELINE INTEGRITY | 3304379557 | carol.m.hager@dominionenergy.com | ON 1/8/2022, DEWV PERSONNEL WERE MONITORING SYSTEM PRESSURES BECAUSE OF COLD WEATHER. IN THE COURSE OF DOING THIS, THEY IDENTIFIED A PRESSURE INCREASE FROM 8 OUNCES TO 10 OUNCES AT 11:00 HOURS; AND ANOTHER INCREASE FROM 10 OUNCES TO 35 OUNCES AT 12:00 HOURS. THE PRESSURE RETURNED TO 8 OUNCES AT 13:00 HOURS, WHICH IS BELIEVED TO BE FROM AN INCREASE IN TEMPERATURE RELIEVING MOISTURE AND ICE FROM THE REGULATORS. DURING THE EVENT, A LEAK WAS DISCOVERED ON A MAINLINE. THREE REGULATING STATIONS THAT FEED THE SYSTEM WERE SHUT IN, CREATING AN OUTAGE FOR 162 CUSTOMERS. THE MAINLINE LEAK WAS REPAIRED, THE SYSTEM WAS LEAK SURVEYED WITH NO ADDITIONAL HAZARDOUS LEAKS FOUND, AND SAFETY CHECKS AND RESTORATION OF CUSTOMERS WERE INITIATED BEGINNING ON THE MORNING OF 1/9/2022.
2026-06-30 10:38 | NO | NO | NO | 20220009 | 36309 | 2022-02-08 12:13 | ORIGINAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | 3600 MIDTOWN DR. | TAMPA | FL | 33607 | 2021-02-23 11:55 | EASTERN | NO | 2021 | GATEWAY BLVD. & WESLEY CHAPEL BLVD. | WESLEY CHAPEL | PASCO | FL | 33544 | 28.2382 | -82.3616 |  |  |  | YES | [5 empty] | 2022-02-08 08:10 | 1328385 |  | NATURAL GAS |  | 357 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-02-23 11:55 |  |  |  | 2021-02-23 11:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 80 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2004 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | UNKNOWN | MECHANICAL PUNCTURE | 1 | 4 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 31000 | 34247.593901711941 | 42478 | 46928.041734094188058 | 0 | 0 |  | 9 | 3213 | 2588.546511627906976744186046511627906977 | 0 | 0 | 76691 | 35070.3496205901609351627906976744186047 | 83764.182147434036034744186046511627907 | 50 | 0 | 821 | 0 | 0 | 821 | 50 | 45 | 45 | 60 | 192.619(A)(2) | 2004-12-29 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A 3RD PARTY LINE STRIKE TO OPERATOR'S SYSTEM, AND AS SUCH, THE CONTROLLER(S) OR CONTROL ROOM WERE NOT THE CAUSE OF OR A CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 028100002 | SUNSHINE STATE ONE CALL OF FLORIDA |  | FACILITY OWNER | YES | YES | 18 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | rharris@tecoenergy.com | [5 empty] | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | 4074206667 | rharris@tecoenergy.com | THIRD PARTY CONTRACTOR STRUCK PEOPLES GAS SYSTEM'S MAIN DURING HDD OPERATION. UPON ARRIVAL ON SCENE AFTER THE REPORT OF THE DAMAGE, THE OPERATOR DID NOT IDENTIFY ANY PHYSICAL EVIDENCE THAT THE THIRD PARTY PERFORMED SPOT DIGGING TO IDENTIFY THE UTILITIES. PIPELINE WAS TOO DEEP TO DIG UP AND SQUEEZE, SO OPERATOR TURNED OFF CRITICAL VALVE STOPPING FLOW OF GAS. PRETESTED PIPELINE WAS INSTALLED, REPAIRS FINALIZED, AND RESTORATION COMPLETED.
2026-06-30 10:38 | NO | YES | NO | 20220010 | 36314 | 2022-02-08 16:05 | ORIGINAL | 12672 | MONROE NATURAL GAS DEPT, CITY OF | 300 W. CROWELL STREET | MONROE | NC | 28112 | 2022-01-04 17:15 | EASTERN | NO | 2022 | INTERSECTION OF ROCKY RIVER RD AND SECREST SHORT CUT RD. | MONROE | UNION | NC | 28110 | 35.0571 | -80.5936 | YES | [8 empty] | 2022-01-04 18:00 | 1325889 | 1326041, 1326048 | NATURAL GAS |  | 4266.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-04 15:09 | YES | OPERATOR | 2022-01-04 15:13 | 2022-01-04 15:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 127 | NO | YES |  |  |  |  | YES | CASED, BORED/DRILLED | [5 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2006 | 2004 |  |  |  |  | 6 | API 5L GRADE B | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 0.2 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 52266 | 55569.03983606555235 | 0 | 0 | 0 | 0 |  | 16.8755 | 71999 | 50828.988355167394468704512372634643377 | 0 | 0 | 124265 | 63961.1510146276364108005822416302765648 | 106398.028191232946818704512372634643377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 265 | 275 | 192.619(A)(1) | 2006-03-30 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 5.8 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BORING | WATER | YES | C213551031 | N/A |  | FACILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | DARWIN DE LOS SANTOS | NATURAL GAS ENGINEERING AND COMPLIANCE MANAGER | ddelossantos@monroenc.org | 7042824697 | 704-283-6492 | ROBERT MILLER | rmiller@monroenc.org | 704-282-4638 | DAVID LUCORE | DIRECTOR OF ENERGY SERVICES | 704-282-4602 | dlucore@monroenc.org | ON 01/04/2022 AT 3:09 PM - CDM SMITH STRUCK THE CITY OF MONROE'S 6-INCH STEEL 275 PSIG GAS MAIN WHILE MAKING A BORE ACROSS THE INTERSECTION OF ROCKY RIVER ROAD AND SECREST SHORTCUT ROAD IN MONROE NC. THE BORE WAS FOR THE INSTALLATION OF A 42 INCH WATER MAIN WITHIN A 54" CASING. THE GAS MAIN WAS PROPERLY LOCATED AND THE CONTRACTOR FAILED TO PERFORM DUE DILIGENCE IN ACCORDANCE WITH NORTH CAROLINA GENERAL STATUTES CHAPTER 87 ARTICLE 8A - UNDERGROUND UTILITY SAFETY AND DAMAGE PREVENTION ACT. THE GAS MAIN WAS RUPTURED BY THE AUGER BORE MACHINE CAUSING THE RELEASE OF NATURAL GAS AND REQUIRING THE REPAIR OF THE GAS LINE. REPAIRS TO THE CITY OF MONROE NATURAL GAS MAIN WERE FINALIZED ON 01/06/2022 AT 3:30 AM. ON 1/04/2022 AT 05:15 PM THE CITY OF MONROE DETERMINED THAT THE INCIDENT REPORTING THRESHOLD WAS GOING TO BE MET BEFORE THE FACILITIES COULD BE REPAIRED. THEREFORE A DETERMINATION OF FILING THE INITIAL INCIDENT WITH NRC WAS MADE. THE NRC NOTIFICATION WAS MADE AT APPROXIMATELY 6:00 PM ON 1/4/2022. THE ACTUAL INCIDENT THRESHOLD OF 3,000 MCF WAS NOT MET UNTIL APPROXIMATELY 1/05/2022 AT APPROXIMATELY 05:26 AM. CDM WAS NEGLIGENT IN THE FOLLOWING REQUIREMENTS: NC ARTICLE 8A - UNDERGROUND UTILITY SAFETY AND DAMAGE PREVENTION ACT - 87-122. EXCAVATOR RESPONSIBILITIES C) AN EXCAVATOR SHALL COMPLY WITH THE FOLLOWING: (3) PLAN THE EXCAVATION OR DEMOLITION TO AVOID DAMAGE TO OR MINIMIZE INTERFERENCE WITH FACILITIES IN OR NEAR THE CONSTRUCTION AREA. (9) AN EXCAVATOR SHALL NOT PERFORM ANY EXCAVATION OR DEMOLITION WITHIN THE TOLERANCE ZONE UNLESS THE EXCAVATOR COMPLIES WITH ALL OF THE FOLLOWING CONDITIONS: A. THE EXCAVATOR SHALL NOT USE MECHANIZED EQUIPMENT, EXCEPT, NONINVASIVE EQUIPMENT SPECIFICALLY DESIGNED OR INTENDED TO PROTECT THE INTEGRITY OF THE FACILITY, WITHIN THE MARKED TOLERANCE ZONE OF AN EXISTING FACILITY UNTIL: 1. THE EXCAVATOR HAS VISUALLY IDENTIFIED THE PRECISE LOCATION OF THE FACILITY OR HAS VISUALLY CONFIRMED THAT NO FACILITY IS PRESENT UP TO THE DEPTH OF EXCAVATION; 2. THE EXCAVATOR HAS TAKEN REASONABLE PRECAUTIONS TO AVOID ANY SUBSTANTIAL WEAKENING OF THE FACILITY'S STRUCTURAL OR LATERAL SUPPORT, OR BOTH, OR PENETRATION OR DESTRUCTION OF THE FACILITIES OR THEIR PROTECTIVE COATINGS: B. THE EXCAVATOR SHALL MAINTAIN CLEARANCE BETWEEN A FACILITY AND THE CUTTING EDGE POINT OF ANY MECHANIZED EQUIPMENT, TAKING INTO ACCOUNT THE KNOWN LIMIT OF CONTROL OF THE CUTTING EDGE OR POINT, AS MAY BE REASONABLY NECESSARY TO AVOID DAMAGE TO THE FACILITY. THE CITY OF MONROE ACCURATELY MARKED THE 6-INCH STEEL GAS LINE. CDM SMITH DID NOT COMPLY WITH THE REQUIREMENTS WITHIN THE TOLERANCE ZONE. CDM SMITH DID NOT VISUALLY INSPECT THE GAS FACILITY AT THE DEPTH OF THE EXCAVATION. CDM SMITH IS RESPONSIBLE FOR THE DAMAGE DUE TO NEGLIGENCE AND NON-COMPLIANCE WITH THE NC UNDERGROUND UTILITY SAFETY AND DAMAGE PREVENTION ACT.
2026-06-30 10:38 | NO | NO | NO | 20220011 | 36473 | 2022-02-14 15:41 | SUPPLEMENTAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2022-01-28 06:38 | EASTERN | NO | 2022 | FERN HOLLOW BRIDGE | PITTSBURGH | ALLEGHENY | PA | 15221 | 40.4396 | -79.8995 | YES | [8 empty] | 2022-01-28 07:50 | 1327481 | 1327626 | NATURAL GAS |  | 871 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-28 06:38 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-28 07:30 | 2022-01-28 07:05 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | OTHER | PIPE THRU BRIDGE SUPPORT AND UNDERGROUND |  |  | YES | YES | CASED | [9 empty] | INVESTOR OWNED |  | MAIN |  | 1973 | UNKNOWN |  |  |  |  | 16 | API-5L-B | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 12 | 16 |  | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 22321 | 23731.614016393433475 | 0 | 0 |  | 10.3951 | 9054 | 6391.834061135371179039301310043668122271 | 0 | 0 | 31375 | 14842.171917460093858908296943231441048 | 30123.4480775288046540393013100436681223 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 45 | 45 | 50 | 192.619(A)(1) | 1972-10-29 | PRESSURE DID NOT EXCEED MAOP | OTHER | SCENTINEL T50 | 0.4 |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PEOPLES PIPELINE WAS DAMAGED BY THE BRIDGE COLLAPSE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE NTSB IS NOT LOOKING AT THE PIPELINE AS CASUAL OR CONTRIBUTORY IN THE COLLAPSE OF THE BRIDGE. PEOPLES PIPELINE WAS DAMAGED BY THE BRIDGE COLLAPSE. | [154 empty] | WAYNE DADIG | MANAGER COMPLIANCE | wayne.dadig@peoples-gas.com | 412-352-1576 |  | WAYNE DADIG | manager compliance | 412-352-1576 | EDWARD A. PALOMBO | VICE PRESIDENT RELIABILITY | 412 258-4453 | edward.a.palombo@peoples-gas.com | THE NTSB IS NOT LOOKING AT THE PIPELINE AS CAUSAL OR CONTRIBUTORY IN THE COLLAPSE OF THE BRIDGE AS THE EVIDENCE GATHERED TO DATE SUGGESTS THE PIPELINE WAS DAMAGED BY THE COLLAPSE. WHEN ALSO CONSIDERING THE RESPONSE TO THE RUPTURE STABILIZED THE SITUATION BEFORE ANY FIRE OR EXPLOSION EVENTS, THE NTSB SEES NO NEED TO CONDUCT ANY FURTHER EXAMINATION OF THE PIPE OR RELATED MATERIALS AND WILL NOT BE SECURING ANY SUCH MATERIALS FOR LATER TESTING. TEN PEOPLE WERE INJURED AS A RESULT OF THE BRIDGE COLLAPSE. NO INJURIES RELATED TO THE PIPELINE. THE PIPELINE WAS DAMAGED AT BOTH SIDES OF THE FERN HOLLOW BRIDGE: WEST SIDE ( 40.439536, -79.901115 ) AND EAST SIDE ( 40.439621, -79.899509 ).
2026-06-30 10:38 | YES | NO | NO | 20220013 | 42414 | 2022-02-17 21:08 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2022-01-18 11:10 | EASTERN | YES | 2022 | 869 FOX STREET | BRONX | BRONX COUNTY | NY | 10469 | 40.8186 | -73.8956 |  | YES |  | YES |  | YES |  |  |  | 2022-01-18 12:54 | 1326802 | 1326954; 1326860 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-01-18 11:10 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 0 | 2022-01-19 10:39 |  |  |  | 2022-01-18 11:19 | 2022-01-18 11:19 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | UNKNOWN-NO UTILITY INVOLVEMENT | UNKNOWN | UNKNOWN | [7 empty] | OTHER | UNKNOWN-NO UTILITY INVOLVEMENT | [9 empty] | LEAK |  |  | OTHER | UNKNOWN-NO UTILITY INVOLVEMENT | [5 empty] | CLASS 4 LOCATION | 50000 | 53159.83606557375 | 0 | 0 | 2824 | 3002.4675409836054 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 52824 | 22805.24655737705784 | 56162.3036065573554 | 0 | 0 | 18 | 0 | 10 | 18 | 0 | 0.25 | 0.25 | 0.5 | 192.619(A)(2) | 1910-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO JURISDICTIONAL INVOLVEMENT | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | RYAN BOULA | GAS EMERGENCY RESPONSE CENTER-DEPARTMENT MANAGER | boular@coned.com | 646-941-0423 | 718-904-4607 | RYAN BOULA | boular@coned.com | 646-941-0423 | RYAN BOULA | GAS EMERGENCY RESPONSE CENTER-DEPARTMENT MANAGER | 646-941-0423 | boular@coned.com | ON 1/18/22 AT 11:10, CON EDISON'S GERC RECEIVED A REPORT FROM THE FDNY OF AN ACTIVE BUILDING FIRE AND EXPLOSION AT 850 FOX STREET IN THE BRONX, WITH FDNY PERSONNEL ON LOCATION. NATURAL GAS WAS NOT REPORTED TO BE INVOLVED. CON EDISON GDS, GAS CONSTRUCTION, AND GAS ERG AND SUPERVISION WERE DISPATCHED TO THE LOCATION BY THE GERC. CON EDISON GAS ENGINEERING WAS NOTIFIED AND DEVELOPED AN ISOLATION PLAN INVOLVING CLOSURE OF DISTRIBUTION MAIN VALVE (MV) 94461 AND EXCAVATION OF A FIRE BANK AT INTERVALE AVENUE AND FOX STREET, OVER A 4-INCH LPPE GAS MAIN (INSTALLED IN 1988). CON EDISON GAS CONTROL WAS NOTIFIED AND REPORTED NORMAL OPERATING CONDITIONS AT NEARBY GAS REGULATOR STATION GR-128. AT 11:19, GDS ARRIVED AND BEGAN INVESTIGATING. GDS CORRECTED THE ADDRESS TO 869 FOX STREET AND CONFIRMED THAT A BUILDING EXPLOSION HAD OCCURRED AT THAT LOCATION. GDS ALSO REPORTED HAVING NO ACCESS TO THE HOS VALVE OR OUTDOOR METER SET AT 869 FOX STREET, WHICH IS SUPPLIED BY A 1 1/4-INCH LPPE GAS SERVICE LINE (INSTALLED IN 1986). GERC PROVIDED GDS WITH THE LOCATION OF MV 94461 (AT THE INTERSECTION OF TIFFANY STREET & FOX STREET). AT 11:48, GDS CLOSED MV 94461 TO BEGIN ISOLATING AND SHUTTING DOWN THE GAS MAIN. CON EDISON GAS CONSTRUCTION CREWS ARRIVED AND BEGAN EXCAVATING A FIRE BANK OVER THE 4-INCH LPPE GAS MAIN AT THE SOUTHEAST CORNER OF INTERVALE AVENUE AND FOX STREET. GDS CONDUCTED A SPECIAL SURVEY OF THE AREA AND DID NOT DETECT ANY NATURAL GAS LEAKS OR ODORS. ALL SUBSURFACE STRUCTURES AND TEST POINTS CHECKED DURING THE SPECIAL SURVEY WERE FOUND CLEAR OF NATURAL GAS READINGS. THE SPECIAL SURVEY WAS CONDUCTED WHILE THE GAS MAIN AND SERVICE LINES ON THE BLOCK WERE IN SERVICE AND BEFORE THEY WERE SHUT DOWN. GDS ALSO TOOK PRESSURE AND ODORANT READINGS AT 858 FOX STREET; BOTH WERE WITHIN ACCEPTABLE RANGE (7.9 INCHES WC FOR PRESSURE; 0.29% GAS-IN-AIR FOR ODORANT). AT 13:03, CON EDISON GAS CONSTRUCTION CREWS INSTALLED A SQUEEZE-OFF ON THE 4-INCH LPPE GAS MAIN IN THE FIRE BANK EXCAVATION, SHUTTING DOWN THE MAIN AND INTERRUPTING GAS SERVICE TO 18 SINGLE-FAMILY BUILDINGS. GAS CONSTRUCTION CREWS THEN CUT AND CAPPED THE SERVICE LINES SUPPLYING 865, 867 AND 869 FOX STREET. AT 18:48, GDS OPENED MV 94461, REINTRODUCING GAS INTO THE MAIN UP TO THE SQUEEZE-OFF. GDS CONDUCTED A DP-IR SURVEY OVER THE MAIN AND SERVICES LINES AND DID NOT DETECT ANY LEAKS. AT 19:08, GDS REMOVED THE SQUEEZE-OFF AND PERFORMED AN ADDITIONAL DP-IR SURVEY OF THE MAIN AND SERVICE LINES WITHOUT DETECTING ANY LEAKS. RESTORATION WAS COMPLETED AT 20:52. ON 1/18/22 AT 17:40, NYPD ARSON AND EXPLOSION SQUAD DETECTIVE DIMARE REPORTED THAT THE SOURCE OF THE EXPLOSION WAS UNKNOWN AND UNDER INVESTIGATION. ON 1/19/22 AT 10:39, FDNY CHIEF SAROCCO REPORTED THAT NATURAL GAS WAS BELIEVED TO BE INVOLVED WITH THE EXPLOSION. THERE IS, HOWEVER, NO INDICATION OF CON EDISON JURISDICTIONAL PIPING BEING INVOLVED AT THIS TIME. THE EXPLOSION RESULTED IN TEN INJURIES AND ONE FATALITY, AND GREATER THAN $50,000 IN PROPERTY DAMAGE. PHSMA, DPS STAFF, AND NYCDEP WERE NOTIFIED AND UPDATED. NTSB INQUIRED AND WAS UPDATED. MEDIA WAS ON LOCATION. THE FDNY INVESTIGATION DETERMINED THAT THE FIRE ORIGINATED INSIDE OF THE PREMISES. THE COMPANY’S INVESTIGATION DETERMINED THAT THERE WERE NO LEAKS OR ISSUES WITH ITS JURISDICTIONAL PIPING AND DPS HAS CONCLUDED ITS INVESTIGATION WITH NO FINDINGS OF CON EDISON JURISDICTIONAL INVOLVEMENT. THIS FINAL UPDATE IS SUBMITTED TO CLOSE OUT THE INCIDENT REPORT AS THE EVENT DID NOT INVOLVE JURISDICTIONAL PIPING.
2026-06-30 10:38 | NO | YES | NO | 20220015 | 36773 | 2022-02-23 19:59 | SUPPLEMENTAL FINAL | 6243 | HAWAII GAS | 515 KAMAKEE STREET (P.O. BOX 3000) | HONOLULU | HI | 96802-3000 | 2022-01-24 11:15 | HAWAII-ALEUTIAN | NO | 2022 | WAIAKAMILO ROAD (BETWEEN HART ST & KALANI ST) | HONOLULU | HONOLULU | HI | 96817 | 21.3224 | -157.8782 | YES | [8 empty] | 2022-01-24 12:30 | 1327229 | 1327369 and 1327376 | SYNTHETIC GAS |  | 550 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 100 | 2022-01-24 09:02 | YES | OPERATOR | 2022-01-24 10:19 | 2022-01-24 09:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1940 | UNKNOWN |  |  |  |  | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.625 | [6 empty] | MECHANICAL PUNCTURE | 3 | 1 | [7 empty] | CLASS 4 LOCATION | 100000 | 106319.6721311475 | 25000 | 26579.918032786875 | 20000 | 21263.9344262295 | 0 | 0 |  | 46.67 | 25669 | 18121.4919941775836972343522561863173217 | 0 | 0 | 170669 | 77358.3310664089769286754002911208151383 | 172285.0165843414586972343522561863173217 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31 | 33 | 50 | 192.619(C) | 1999-03-31 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | AUGER | SEWER (SANITARY/STORM) | YES | 22000022 |  |  | UNKNOWN/OTHER | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [167 empty] | YES |  |  | CHRISTOPHER HALL | IMP ENGINEER | chall@hawaiigas.com | 808-594-5553 |  | CHRIS HALL | chall@hawaiigas.com | 808-594-5553 | KEVIN NISHIMURA | VICE PRESIDENT OPERATIONS | 808-594-5573 | knishimu@hawaiigas.com | INCIDENT SUMMARY ON MONDAY, JANUARY 24, 2022, FRANK COLUCCIO CONSTRUCTION ("FCC") WAS PERFORMING A SEWER INSTALLATION ON A PORTION OF WAIAKAMILO ROAD IN HONOLULU, HAWAII, WITH AN AUGER. AT APPROXIMATELY 9:02 A.M., ON THE PORTION OF WAIAKAMILO ROAD BETWEEN HART STREET AND KALANI STREET, THE AUGER STRUCK A HAWAI'I GAS ("HG") UNDERGROUND 8-INCH PIPELINE ("SUBJECT SEGMENT"). THE AUGER CAUSED AN APPROXIMATELY 3-INCH LONG FRACTURE ALONG THE TOP OF THE PIPELINE. THE SUBJECT SEGMENT BEGAN TO LEAK GAS. HG'S FIRST RESPONDER ARRIVED ON SITE AT APPROXIMATELY 9:15 A.M. AND CONFIRMED THE DAMAGE TO THE SUBJECT SEGMENT. DUE TO THE MAGNITUDE OF THE LEAK, HG CALLED THE HONOLULU FIRE DEPARTMENT ("HFD") AT APPROXIMATELY 10:19 A.M. TO ASSIST IN SECURING THE ROADWAY AND TO HELP MONITOR THE HOT ZONE. HG'S MAINTENANCE CREW ARRIVED ON SITE AT APPROXIMATELY 10:30 A.M. AND BEGAN ASSESSING REPAIRS. AT APPROXIMATELY 11:15 A.M., HFD BEGAN EVACUATING NEARBY COMMERCIAL BUILDINGS. HG WAS ABLE TO STOP THE FLOW OF GAS TO THE SUBJECT SEGMENT AT APPROXIMATELY 5:35 P.M., JANUARY 24, 2022. FINAL REPAIRS WERE COMPLETED AT APPROXIMATELY 11:00 P.M., JANUARY 24, 2022. HAWAI'I GAS INVOLVEMENT PRIOR TO INCIDENT HG INSTALLED THE SUBJECT SEGMENT IN 1940. THE SUBJECT SEGMENT IS AN 8-INCH BARE STEEL PIPE. HG MAPS AND RECORDS CONTAIN NO INDICATION THAT THE SUBJECT SEGMENT WAS REPAIRED, ALTERED OR EXCAVATED SINCE ITS INSTALLATION. ON MONDAY, JANUARY 3, 2022, FCC SUBMITTED ONE CALL TICKET NUMBER 22000022 TO THE HAWAII ONE CALL CENTER INDICATING THAT FCC WOULD BE EXCAVATING "ON WAIAKAMILO ROAD BETWEEN DILLINGHAM BOULEVARD AND HART STREET (EWA SIDE OF ROAD)" ("EXCAVATION AREA"). IN RESPONSE TO TICKET NO. 22000022, HG REVIEWED GIS MAPS OF THE EXCAVATION AREA AND DETERMINED THAT AN UNDERGROUND MAIN LINE WAS LOCATED WITHIN THAT AREA. ON JANUARY 10, 2022, HG PERSONNEL ATTEMPTED TO PERFORM TONING ON THE UNDERGROUND MAIN LINE IN THE EXCAVATION AREA BUT NOTED THAT THE LOCATION OF THE UNDERGROUND MAIN LINE HAD ALREADY BEEN MARKED BY ANOTHER PARTY IN YELLOW PAINT. PLEASE CONTACT HG FOR ADDITIONAL NARRATIVE DETAIL. ALSO, PLEASE NOTE THAT THIS INVESTIGATION IS STILL ONGOING. UPDATE 6/10/2022 UPON COMPLETION OF THE INVESTIGATION BY HG, IT WAS DETERMINED THAT TONING OF THE SUBJECT SEGMENT WAS PERFORMED INADEQUATELY BY HG. AS INDICATED IN THE "INCIDENT SUMMARY" SECTION ABOVE, THE UNDERGROUND MAIN LINE HAD ALREADY BEEN MARKED BY ANOTHER PARTY IN YELLOW PAINT AND HG FAILED TO CONFIRM THE MARKINGS WERE CORRECT WHEN RESPONDING TO TICKET NO. 22000022. AS A RESULT OF THE INVESTIGATION, HG HAS INCORPORATED THE FOLLOWING MITIGATIVE ACTIONS INTO ITS TONING OPERATIONS AS OF MAY 2022: 1. REVISE "HG ONE CALL PIPE LOCATION GUIDELINES" DOCUMENT. A. ALL PAINTED UTILITY MARKINGS BY HG WILL HAVE A UNIQUE HG IDENTIFIER. B. ALL EXISTING UTILITY MARKINGS (WHETHER BY HG OR 3RD PARTY) SHALL BE REVERIFIED IN RESPONSE TO AN 811 TICKET. 2. UPDATE TRAINING REQUIREMENTS FOR ALL HG EMPLOYEES WHO CONDUCT UTILITY LOCATIONS. A. INITIAL TRAINING REQUIREMENTS (OQ & "HG ONE CALL PIPE LOCATION GUIDELINES" DOCUMENT REVIEW). B. REFRESHER TRAINING REQUIREMENTS (PIPE LOCATION REFRESHER TRAINING TO BE PROVIDED IN 2022 AND EVERY 3 YEARS AFTER OR WHEN PROBABLE CAUSE IS DETERMINED BY HG MANAGEMENT). C. DOCUMENTATION RETENTION REQUIREMENTS. HG IS CONFIDENT THE MITIGATIVE ACTIONS LISTED ABOVE WILL HELP TO FURTHER REDUCE TONING RELATED INCIDENTS GOING FORWARD. PLEASE CONTACT HG FOR ADDITIONAL NARRATIVE DETAIL.
2026-06-30 10:38 | NO | YES | YES | 20220016 | 36388 | 2022-02-25 10:24 | ORIGINAL FINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2022-01-27 10:58 | EASTERN | YES | 2022 | 217 BOSWELL RD | BALTIMORE | BALTIMORE COUNTY | MD | 21229 | 39.2819 | -76.7044 | [7 empty] | YES | TWO LEAKING CAST IRON JOINTS WERE ENCAPSULATED AND RENEWED ONE CAST IRON SERVICE AT INCIDENT | 2022-01-27 19:17 | 1327461 | N/A | NATURAL GAS |  | 0.003 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2022-01-27 10:28 | ALLOWED TO BURN OUT |  | 0 | YES | 0 | 2022-01-27 10:59 |  |  |  | 2022-01-27 11:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1920 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 12000 | 12758.3606557377 | 1200 | 1275.83606557377 | 0 | 0 | EMERGENCY RESPONSE PERSONNEL AND EQUIPMENT | 4.45 | 0 | 0 | 0 | 0 | 13200 | 5698.721311475412 | 14034.19672131147 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 10 | 10 | 10 | 192.623 | 1920-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | LEAKING CAST IRON JOINT | [11 empty] | YES | GAS FROM A LEAKING CAST IRON JOINT IGNITED CAUSING A MANHOLE COVER TO LIFT STRIKING A BALTIMORE CITY WELDING CONTRACTOR. |  | YES |  |  |  | OTHER | PACKING MATERIAL USED TO SEAL CAST IRON JOINTS DRIED RELEASING NATURAL GAS | NO | [86 empty] | JEFFREY WEATHERHOLTZ | MANAGER - GAS ENGINEERING AND STANDARDS | jeffrey.weatherholtz@bge.com | 410-470-8858 | 410-470-9549 |  |  |  | DANIEL A NORDEN | MANAGER - GAS ENGINEERING AND ASSET PERFORMANCE | 410-470-6435 | daniel.a.norden@bge.com | ON 1/27/2022, A CITY OF BALTIMORE CONTRACTOR WAS WELDING ON A WATER MAIN ON FREDERICK AVENUE NEAR THE INTERSECTION OF BOSWELL ROAD. WHILE PERFORMING THE WELDING OPERATION, AN IGNITION OCCURRED WHICH CAUSED A NEARBY MANHOLE COVER TO RAISE AND STRIKE A NEARBY CONTRACTOR, CAUSING INJURY TO THE CONTRACTOR'S FOOT AND REQUIRING OVERNIGHT IN-PATIENT HOSPITALIZATION. NATURAL GAS WAS CONFIRMED IN THE LOCALIZED AREA AND SURVEYS WERE IMMEDIATELY CONDUCTED TO FIND THE SOURCE OF THE LEAK. AN ADJACENT MEDIUM PRESSURE 12" CAST IRON NATURAL GAS MAIN WAS FOUND TO HAVE TWO LEAKY JOINTS AND THEY WERE SUBSEQUENTLY REPAIRED AS WELL AS RENEWING AN INTERCONNECTED NATURAL GAS SERVICE LINE. POST-INCIDENT SURVEYS WERE COMPLETED, AND NO READINGS WERE DETECTED SUCH THAT THE JOB COULD BE CLOSED OUT.. NOTE : PART A 21C IS NOTED AS 0.0 HOWEVER ACTUAL (MCF) IS 0.003.TO MATCH PART A 7. THIS ONLINE FORM WILL NOT ACCEPT THAT NUMBER.
2026-06-30 10:38 | NO | YES | NO | 20220017 | 36393 | 2022-02-25 16:16 | ORIGINAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2022-01-27 08:10 | CENTRAL | NO | 2022 | 8500 E PARMER LANE | MANOR | TRAVIS | TX | 78653 | 30.3511 | -97.5885 | YES | [8 empty] | 2022-01-27 08:32 | 1327404 | 1327531 | NATURAL GAS |  | 25858 | 0.71 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-27 01:30 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-27 00:42 | 2022-01-27 01:30 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2016 | 2015 | [7 empty] | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.237 | [6 empty] | OTHER | [8 empty] | THIRD PARTY VEHICLE STRUCK ABOVE GROUND STATION PIPING AND SHEERED FABRICATION AT 2 CIRCUMFERENTIAL WELDS BETWEEN PIPE AND REDUCERS. | CLASS 1 LOCATION | 0 | 0 | 250000 | 265799.18032786875 | 1115 | 1185.464344262294625 | 0 | 0 |  | 5.78 | 149459 | 105513.267831149927219796215429403202329 | 4 | 2.82387190684133915574963609898107714702 | 400578 | 194347.4831573484555124454148471615720524 | 372500.7363751878131839519650655021834061 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 707 | 707 | 778 | 192.621 M | 2016-01-11 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE TO THE REGULATOR STATION BY THIRD-PARTY VEHICLE INITIATED SCADA ALARMS IN CONTROL ROOM. CONTROLLER FOLLOWED PROCEDURES TO INVESTIGATE ALARMS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | SMALL TRUCK | ROADWAY | 60 | YES |  | YES | [116 empty] | YES | [23 empty] | AMY MARK | REGULATORY COMPLIANCE SPECIALIST | amy.mark@onegas.com | 512-407-1571 |  | BRYAN WEEKS | bryan.weeks@onegas.com | 512-407-1529 | BRYAN WEEKS | DIRECTOR OF ENGINEERING | 512-407-1529 | bryan.weeks@onegas.com | THIRD-PARTY VEHICLE RAN OFF THE ROADWAY TRAVELING WESTBOUND ON EAST PARMER LANE AT A HIGH SPEED AND CRASHED THROUGH FENCING, CONCRETE-FILLED STEEL BOLLARD POSTS WITH WELDED STEEL CROSSBARS, AND THE TEXAS GAS SERVICE (TGS) REGULATOR STATION AT SUBJECT LOCATION BEFORE DAMAGING AND COMING TO REST AGAINST ATMOS ENERGY'S METERING STATION, WHICH FEEDS TGS'S STATION AND DISTRIBUTION SYSTEM. THE VEHICLE'S IMPACT CAUSED THE PIPING TO SEPARATE, LEADING TO AN UNINTENTIONAL RELEASE OF GAS FROM THE INLET AND OUTLET SIDES OF TGS'S REGULATOR STATION. AFTER DAMAGING THE ATMOS ENERGY METERING STATION, THE VEHICLE CAME TO REST ON TOP OF THE ATMOS ENERGY PIPING. ATMOS ENERGY'S MEASUREMENT INSTRUMENTATION WAS DAMAGED AND COULD NOT PROVIDE A VOLUME OF GAS THAT FLOWED THROUGH THE STATION DURING AND AFTER THE INCIDENT. TGS HAS NO KNOWLEDGE OF THE DAMAGE ESTIMATES FOR ATMOS FACILITIES OR THE VEHICLE AT FAULT FOR THE INCIDENT.
2026-06-30 10:38 | NO | YES | NO | 20220018 | 36409 | 2022-03-02 10:16 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2022-02-01 07:42 | EASTERN | YES | 2022 | CUMBERLAND HILL RD BET AUGUSTINE ST AND FOUNDERS DR | WOONSOCKET | PROVIDENCE | RI | 02895 | 41.9925 | -71.4864 | [6 empty] | YES |  |  | 2022-02-02 19:28 | 1327936 | 1328004 | NATURAL GAS |  | 8500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 60 | 2022-02-02 11:00 | YES | OPERATOR | 2022-02-01 11:00 | 2022-02-01 11:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 25 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN - POSSIBLE OXYACETYLENE | 0.375 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 27 | 0.1 |  | CLASS 4 LOCATION | 0 | 0 | 300000 | 318959.0163934425 | 50000 | 53159.83606557375 | 0 | 0 |  | 7.21 | 61285 | 43265.2474526928675400291120815138282387 | 0 | 0 | 411285 | 186339.1038489990312954876273653566229985 | 415384.0999117091175400291120815138282387 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 47.9 | 50 | 60 | 192.621 M | 1970-08-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT CAUSE WAS A CRACK IN A WELD. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | MATERIAL FAILURE OF PIPE OR WELD | BUTT WELD | [146 empty] | BUTT WELD |  |  | PIPE | [28 empty] | YES | [11 empty] | YES |  |  |  | NO | [55 empty] | YES | [30 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | JOSEPH F. CURLEY | joseph.curley@nationalgrid.com | 4013329815 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | THIS EVENT WAS DISCOVERED IN RESPONSE TO AN ODOR CALL FROM A COMMERCIAL LOCATION AT FORTIN DRIVE IN WOONSOCKET, RI RECEIVED AT APPROX. 11:00 AM ON 2/1/2022. TWO RESPONDERS INITIALLY RESPONDED AND REQUESTED ADDITIONAL SUPPORT TO LOCATE THE LEAK WITH BLOWING GAS AT CUMBERLAND HILL ROAD. ADDITIONAL SUPPORT ARRIVED TO HELP LOCATE THE LEAK AS WELL AS MUTUAL AID PERSONNEL. ADDITIONAL CREWS WORKED OVERNIGHT INTO THE NEXT DAY TO CONTINUE WORK IN LOCATING THE LEAK. ENGINEERING REVIEWED FACILITY MAPS TO DETERMINE THE APPROPRIATE ISOLATION VALVES TO SHUT OFF GAS SUPPLY AND INITIATE REPAIRS WHILE CREWS WORKED TO LOCATE THE IDENTIFIED VALVES; HOWEVER, SIGNIFICANT SNOWFALL FROM 01/28 THROUGH 1/30/22 HINDERED THE CREWS' EFFORTS. DUE TO THE SCOPE OF THE PROJECTED CUSTOMER IMPACT, A DECISION WAS MADE TO ISOLATE THE AFFECTED MAIN USING WELDED STOPPLE FITTINGS. AT 8:00 PM ON 2/2/2022 THE LEAK WAS SECURED. TWO BUILDINGS WERE EVACUATED, WITH AN ESTIMATED 50-60 PEOPLE IN THESE COMMERCIAL PROPERTIES AS ESTIMATED BY THE FD. APPROXIMATELY 5'6" OF 12" STEEL PIPE WERE REPLACED WITH PLASTIC. WE ARE REPORTING THIS INCIDENT SOLELY BASED ON THE VOLUME OF GAS RELEASED. NO INJURIES WERE INVOLVED IN THIS INCIDENT AND RESPONSE AND RESTORATION COSTS ARE RELATED TO THE REPAIR OF THE MAIN AND RESTORATION OF TWO CUSTOMERS THAT WERE SHUT OFF DURING THE RESPONSE.
2026-06-30 10:38 | NO | YES | NO | 20220019 | 36639 | 2022-03-03 13:41 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2022-02-16 10:20 | EASTERN | NO | 2022 | 944 MCELHANEY ROAD | TRAVELERS REST | GREENVILLE | SC | 29690 | 34.9544 | -82.4665 | [6 empty] | YES |  |  | 2022-02-16 15:27 | 1329042 | 1329121 | NATURAL GAS |  | 8710 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-02-16 10:20 | NO |  |  | 2022-02-16 11:39 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | UNKNOWN |  |  |  |  | 8 | M10048 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 226000 | 240282.45901639335 | 70000 | 74423.77049180325 | 0 | 0 |  | 4 | 34840 | 24595.9243085880640465793304221251819505 | 0 | 0 | 330840 | 147821.240365571432780203784570596797671 | 339302.1538167846640465793304221251819505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 250 | 192.619(A)(2) | 1962-06-25 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | UTILITY | BORING | WATER | YES | 2112131188 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | THE USE OF MECHANIZED EQUIPMENT IN THE TOLERANCE ZONE & EXCAVATOR FAILED TO SUPPORT AND PROTECT FACILITIES. WATER COMPANY CONTRACTOR WAS ON A SITE TO INSTALL WATER SERVICE TO A CUSTOMER. TAPPING WHAT THEY BELIEVED WAS THE WATER MAIN, WAS INSTEAD AN 8" HIGH PRESSURE GAS MAIN. THE WATER CONTRACTOR STOPPED WHEN GAS WAS RELEASED AND REPORTED A GAS LEAK.
2026-06-30 10:38 | NO | YES | NO | 20220022 | 36437 | 2022-03-08 09:39 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-02-08 07:45 | CENTRAL | NO | 2022 | 11699 NW H K DODGEN LOOP | TEMPLE | BELL | TX | 76504 | 31.1412 | -97.3446 | YES | [5 empty] | YES |  |  | 2022-02-08 18:41 | 1328466 | 1328674 | NATURAL GAS |  | 5036 | 18 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-02-08 07:45 | YES | OPERATOR | 2022-02-08 08:05 | 2022-02-08 08:05 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 65 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1985 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 11 | 1 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 104000 | 110572.4590163934 | 0 | 0 | 0 | 0 |  | 8.17 | 41144 | 29046.3464337700145560407569141193595342 | 147 | 103.777292576419213973799126637554585153 | 145291 | 68639.8388097454056477438136826783114993 | 139722.5827427398337700145560407569141194 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 168 | 168 | 200 | 192.619(A)(2) | 1985-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2252816180 | TEXAS811 |  | CONTRACT LOCATOR | NO | YES | 20 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | DALE GAMBRELL | COMPLIANCE SUPERVISOR | dale.gambrell@atmosenergy.com | 512-844-8270 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-957-3295 | marlo.sutton@atmosenergy.com | AT 07:45 ON FEBRUARY 8, 2022, A THIRD PARTY CONTRACTOR DAMAGED A 6" ATMOS DISTRIBUTION LINE WITH A TRACKHOE AT 11699 NW H K DODGEN LOOP IN TEMPLE TX, CAUSING A RELEASE OF GAS. THE DAMAGE CAUSED AN INTERRUPTION IN SERVICE FOR 1 CUSTOMER; CNG WAS BROUGHT IN TO SHORE UP SERVICE FOR OTHER CUSTOMERS. GAS LOSS EXCEEDED THE REPORTING THRESHOLD. SERVICE WAS RESTORED AT 03:32 ON FEBRUARY 9, 2022. IT WAS DETERMINED THAT THE PIPELINE WAS NOT MARKED BY THE LOCATOR.
2026-06-30 10:38 | NO | YES | NO | 20220024 | 37266 | 2022-03-25 16:52 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-02-08 14:27 | EASTERN | NO | 2022 | PORTAGE | KALAMAZOO | KALAMAZOO | MI | 49001 | 42.2816 | -85.5722 | [5 empty] | YES |  | YES | SQUEEZE-OFF ISOLATION NORTH END PIPELINE SEGMENT & BAGGING OFF ISOLATION SOUTH END PIPELINE SEGMENT | 2022-02-25 09:33 | 1329679 | 1329801 | NATURAL GAS |  | 2277 | 0.007 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-02-08 14:27 | NO |  |  | 2022-02-08 14:44 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 48 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1901 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 332405 | 353411.906147540847375 | 318 | 338.09655737704905 | 0 | 0 |  | 4.48 | 10201 | 7201.579330422125181950509461426491994178 | 0 | 0 | 342924 | 149508.8137026034382276710334788937409025 | 360951.5820353400216069505094614264919942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 192.623 | 1901-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | EROSION OF SUPPORT DUE WATER AND ROADWAY CONSTRUCTION IN THE AREA RESULTING IN LESS THAN ADEQUATE COMPACTION AND SUPPORT OF THE NATURAL GAS PIPELINE. | [154 empty] | CARMELLA KING |  | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON TUESDAY, FEBRUARY 8, 2022, AT APPROXIMATELY 14:27 HOURS CONSUMERS ENERGY WAS NOTIFIED BY OUR LEAK SURVEY CONTRACTOR (PERFORMING A DISCRETIONARY LEAK SURVEY) OF A POSSIBLE LEAK AT/NEAR 1004 PORTAGE ROAD, (KALAMAZOO COUNTY) KALAMAZOO, MI. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ON-SITE AT APPROXIMATELY 14:44 HOURS AND CONFIRMED READS WHICH REQUIRED AN IMMEDIATE RESPONSE. A DISTRIBUTION CREW (CREW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 16:39 HOURS. THE CREW HAD RECENTLY COMPLETED A LEAK REPAIR ON A 6" CAST IRON PIPELINE AND BASED ON A PRELIMINARY INVESTIGATION AT THE SITE THOUGHT THE SOURCE COULD POTENTIALLY BE RESIDUAL GAS FROM THE INITIAL REPAIR. EXTRACTION EQUIPMENT WAS MOBILIZED TO REMOVE RESIDUAL GAS BUILD UP WHILE GSW'S AND THE CREW CONTINUED PINPOINTING TO DETERMINE IF THE SOURCE COULD BE ADDITIONAL LEAKS ON THE PIPELINE. OVER SEVERAL WEEKS, MULTIPLE LEAKS WERE DISCOVERED ON THE CAST IRON PIPELINE. THE FAILURE INVESTIGATION DETERMINED, THE RECENT (2021) WATER AND ROAD CONSTRUCTION LED TO REDUCED COMPACTION AND SUPPORT OF THE CAST IRON PIPELINE CAUSING MULTIPLE LEAKS OVER TIME. ALL IDENTIFIED LEAKS WERE REPAIRED, AND EXTRACTION EQUIPMENT WAS SIMULTANEOUSLY USED TO REMOVE RESIDUAL GAS FROM THE SOIL. CONSUMERS ENERGY PERSONNEL MONITORED THE SITE UNTIL ALL GAS READS WERE ZERO. A PIPELINE REPLACEMENT PROJECT, WHICH WOULD HAVE INCLUDED RETIRING THE 6-INCH CAST IRON PIPELINE WAS SCHEDULED FOR 2023. HOWEVER DUE TO THE AGE AND CONDITION OF THE PIPELINE A PORTION OF THE REPLACEMENT PROJECT WAS EXPEDITED, AND CONSTRUCTION STARTED IN APRIL. FEBRUARY 25, 2022 CE RETIRED APPROXIMATELY 1100' OF THE CAST IRON PIPELINE THAT WAS COMPROMISED BECAUSE OF THE WATER AND ROAD CONSTRUCTION ACTIVITIES THAT OCCURRED IN 2021.
2026-06-30 10:38 | NO | YES | NO | 20220025 | 36533 | 2022-03-31 18:46 | ORIGINAL FINAL | 11032 | SPIRE MISSOURI INC. EAST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2022-03-01 10:37 | CENTRAL | NO | 2022 | 3 MILLERS CT | O'FALLON | SAINT CHARLES | MO | 63366 | 38.7758 | -90.7291 | [5 empty] | YES |  |  |  | 2022-03-01 12:33 | 1329957 | 1330159 | NATURAL GAS |  | 104.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-01 11:54 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 45 | YES | 3 | 2022-03-01 10:37 | NO |  |  | 2022-03-01 10:59 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2002 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 2 | 0.5 | [7 empty] | CLASS 3 LOCATION | 663261 | 705176.920573770219975 | 0 | 0 | 500 | 531.5983606557375 | 0 | 0 |  | 6.12 | 641 | 452.525473071324599708879184861717612809 | 0 | 0 | 664402 | 286928.3211001743040551237263464337700146 | 706161.0444074972820747088791848617176128 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 39.77 | 40 | 60 | 192.621 M | 2002-12-02 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT RESULT IN ANY ABNORMAL PIPELINE OPERATION OR PRESSURES THAT CAUSED OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 220521245 |  |  | CONTRACT LOCATOR | YES | YES | 9 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  | NICOLE CHRISTIANER | nicole.christianer@spireenergy.com | 314-349-2929 | CRAIG HOEFERLIN | VP OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A THIRD-PARTY TELECOMMUNICATIONS EXCAVATOR STRUCK A 2-INCH PLASTIC GAS MAIN WHILE BORING. THE EXCAVATOR HAD VALID LOCATES AND THE MAIN WAS MARKED WITHIN TOLERANCE BUT THE EXCAVATOR FAILED TO POT-HOLE THE BORE CROSSING. THE COMPANY IDENTIFIED GAS READINGS IN TWO HOMES UPON ARRIVAL AND EVACUATED BOTH RESIDENCES. WHILE CREWS WERE WORKING TO SHUT DOWN THE MAIN 3 MILLERS CT EXPLODED AND SUBSEQUENTLY CAUGHT FIRE. CREWS IMMEDIATELY SHUT DOWN THE MAIN FOLLOWING THE EXPLOSION. THE EXPLOSION CAUSED DAMAGE TO SEVERAL NEARBY HOMES AND THE FIRE SPREAD TO 5 MILLERS CT. THE DAMAGED GAS MAIN WAS REPLACED WITH A 15-FOOT SEGMENT OF 2-INCH PLASTIC. GAS SERVICE WAS INTERRUPTED AT 21 HOMES AND 2 HOMES WERE CONDEMNED. A 48 HOUR UPDATE TO THE NRC WAS MADE ON MARCH 3, 2021 AT 13:38. REPORT NUMBER 1330159.
2026-06-30 10:38 | NO | YES | NO | 20220026 | 36557 | 2022-04-06 09:33 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2022-03-10 09:18 | CENTRAL | NO | 2022 | ENTIRE CITY | SEGUIN | GUADALUPE | TX | 78155 | 29.5701 | -97.9641 |  | YES |  | YES | [5 empty] | 2022-03-10 09:18 | 1330725 | 1331011 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-03-08 10:30 | NO |  |  | 2022-03-08 13:00 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | LOSS OF GAS SUPPLY FROM SUPPLIER | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | LOSS OF GAS SUPPLY FROM SUPPLIER | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 1121224 | 1192081.6806557372454 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1121224 | 484056.29573770510184 | 1192081.6806557372454 | 0 | 0 | 4300 | 0 | 0 | 4300 | 0 | 0 | 0 | 0 | 192.619(A)(1) | 2022-03-08 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | OTHER | NOTIFICATION FROM SUPPLIER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOSS OF GAS SUPPLY FORM SUPPLIER | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | LOSS OF GAS SUPPLY FROM SUPPLIER | [47 empty] | LESLIE J DAVENPORT | COMPLIANCE COORDINATOR LL | leslie.davenport@centerpointenergy.com | 713-967-7325 |  | MICHAEL MAXWELL | mike.d.maxwell@centerpointenergy.com | 830-643-6914 | RANDALL SANDERS | REGIONAL OPERATIONS DIRECTOR TEXAS | 713-207-5728 | randall.x.sanders@centerpointenergy.com | LOSS OF GAS SUPPLY FROM ENTERPRISE PIPELINE TO CENTERPOINT ENERGY DISTRIBUTION SYSTEM IN SEGUIN, & MCQUEENEY, TEXAS, FORCED CENTERPOINT ENERGY TO PERFORM RE-LITE OF APPROXIMATELY 4300 CUSTOMERS.
2026-06-30 10:38 | NO | YES | NO | 20220027 | 36876 | 2022-04-06 09:44 | SUPPLEMENTAL FINAL | 13302 | NATIONAL GAS & OIL CORP | 1500 GRANVILLE ROAD | NEWARK | OH | 43055 | 2022-02-23 15:22 | EASTERN | YES | 2022 | 811 BLACKS RD SE | HEBRON | LICKING | OH | 43025 | 39.9878 | -82.5205 |  |  | YES | YES | [5 empty] | 2022-02-23 15:22 | 1329557 |  | NATURAL GAS |  | 7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-02-23 13:45 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 7 | YES | 1 | 2022-02-23 14:10 | YES | OPERATOR | 2022-02-23 13:51 | 2022-02-23 14:17 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | COOPERATIVE |  | SERVICE RISER |  | 1998 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | 277236 | 294756.4062295080831 | 0 | 0 | 5000 | 5315.983606557375 | 0 | 0 |  | 39 | 273 | 192.729257641921397379912663755458515284 | 0 | 0 | 282509 | 122004.261131076000166113537117903930131 | 300265.1190937073794973799126637554585153 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 44 | 44 | 60 | 192.619(A)(1) | 1998-04-24 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 7 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A SMALL LEAK OF THIS KIND WAS NOT DETECTABLE ON SUCH A LARGE SYSTEM THAT IS MONITORED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | [56 empty] | TREES/VEGETATION ROOTS | [5 empty] | NO | [188 empty] | YES | [29 empty] | CHRISTOPHER STORTS | COMPLIANCE ENGINEER | cstorts@theenergycoop.com | 740-348-1203 | 740-348-1131 |  |  |  | CHRISTOPHER STORTS | COMPLIANCE ENGINEER | 740-348-1203 | cstorts@theenergycoop.com | ON WEDNESDAY, FEBRUARY 23, 2022, A HOMEOWNER REPORTED AN EXPLOSION AND CALLED 911. NATIONAL GAS & OIL COOPERATIVE WAS NOTIFIED APPROXIMATELY 10 MINUTES LATER. WHEN COOPERATIVE EMPLOYEES ARRIVED AT THE SCENE, THE SERVICE LINE CURB VALVE WAS SHUT AND THE FIRE DEPARTMENT EXTINGUISHED THE FLAMES. READINGS INDICATED THAT NATURAL GAS WAS PRESENT IN THE GROUND AROUND THE HOMEOWNER'S NATURAL GAS RISER. THE HOMEOWNER'S NATURAL GAS SERVICE LINE WAS TESTED AND LEAKAGE WAS FOUND AT THE RISER HEAD. ON TUESDAY, MARCH 22, 2022 AFTER ALL INSURANCE PARTIES AND FIRE AND EXPLOSION INVESTIGATORS COULD BE PRESENT, THE HOMEOWNER'S RISER WAS REMOVED AND THE SERVICE LINE CAPPED AT THE BASE OF THE RISER AND RETESTED. THE SERVICE LINE HELD THE PRESSURE TEST WITHOUT THE RISER. THE HOMEOWNER'S RISER WAS REMOVED AND SENT TO AN INDEPENDENT LABORATORY PLANNED FOR FURTHER INVESTIGATION (PLANNED FOR APRIL 21, 2022). THIS RISER WAS INSTALLED BY THE HOMEOWNER OR THE HOMEOWNER'S CONTRACTOR OR REPRESENTATIVE, NOT BY THE NATIONAL GAS & OIL COOPERATIVE. THE ROOT CAUSE OF THE EXPLOSION WAS DUE TO A PULLED RISER. A TREE ROOT APPROXIMATELY 6 FEET AWAY FROM THE BEND IN THE RISER GREW ACROSS THE SERVICE LINE. OVER TIME, THE ROOT PULLED THE SERVICE LINE MOST OF THE WAY OUT OF THE RISER CONNECTION, CAUSING A LEAK. THE HOUSE AT 811 BLACKS RD SE HAS BEEN TORE DOWN DUE TO THE DAMAGES CAUSED BY THE EXPLOSION. THE PUBLIC UTILITIES COMMISSION OF OHIO HAS COMPLETED THEIR INVESTIGATION AND WE, NATIONAL GAS AND OIL COOPERATIVE, ARE WAITING ON A COPY OF THEIR REPORT AS OF 7/19/2022.
2026-06-30 10:38 | NO | YES | NO | 20220028 | 36650 | 2022-04-08 10:32 | SUPPLEMENTAL FINAL | 4473 | ATMOS ENERGY CORPORATION - WEST TEXAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-03-10 14:50 | CENTRAL | NO | 2022 | 3307 89TH STREET | LUBBOCK | LUBBOCK | TX | 79412 | 33.513 | -101.8861 | [5 empty] | YES |  |  |  | 2022-03-10 16:55 | 1330768 | 1330843 | NATURAL GAS |  | 685 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-10 15:47 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 250 | YES | 7 | 2022-03-10 15:09 | YES | OPERATOR | 2022-03-10 15:09 | 2022-03-10 15:09 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2015 | [5 empty] | 2.375 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 7938 | 8439.65557377048855 | 13455 | 14305.311885245896125 | 166000 | 176490.65573770485 | DAMAGE TO RESIDENCE. | 5.63 | 3857 | 2722.91848617176128093158660844250363901 | 6 | 4.23580786026200873362445414847161572052 | 191256 | 83122.6361463478962318922852983988355167 | 201962.7774907532579646652110625909752547 | 0 | 0 | 7 | 0 | 0 | 12 | 0 | 40 | 40 | 44 | 192.619(A)(2) | 2015-03-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 1 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | OTHER | [12 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 2256245020 | TX811 |  | CONTRACT LOCATOR | YES | YES | 40 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [143 empty] | YES | [26 empty] | MIKE CULP | COMPLIANCE MANAGER | mike.culp@atmosenergy.com | 8062206849 |  | MIKE CULP | mike.culp@atmosenergy.com | 8062206849 | MIKE CULP | COMPLIANCE MANAGER | 8062206849 | mike.culp@atmosenergy.com | CITY OF LUBBOCK, TX WHILE REPAIRING A SEWER SERVICE LINE TO THE ASSOCIATED ADDRESS, CUT A 2" NATURAL GAS LINE WITH A BACKHOE. THE GAS LINE WAS CORRECTLY MARKED WITH PAINT AND FLAGS BEFORE START OF EXCAVATION. ATMOS ENERGY WAS NOTIFIED OF THE DAMAGED LINE AT 15:09 AND ARRIVED ON SCENE AT 15:16. REMOTE EXCAVATIONS SITES WERE USED TO SQUEEZE THE PE LINE AND SHUT THE FLOW OF GAS OFF, AREA WAS MADE SAFE AT 16:37. ATMOS ENERGY'S INVESTIGATION OF THIS INCIDENT IS CURRENTLY ONGOING.
2026-06-30 10:38 | NO | YES | NO | 20220029 | 36565 | 2022-04-08 11:56 | ORIGINAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2022-03-09 16:22 | PACIFIC | NO | 2022 | 3817 N CRESTLINE ST | SPOKANE | SPOKANE | WA | 99207 | 47.6928 | -117.3791 | YES | [8 empty] | 2022-03-09 16:37 | 1330648 | 1330830 | NATURAL GAS |  | 45 | 22 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2022-03-03 18:08 | NO |  |  | 2022-03-03 19:03 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 34 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1956 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.25 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 2000 | 2126.39344262295 | 177000 | 188185.819672131075 | 0 | 0 |  | 4.63 | 208 | 146.841339155749636098981077147016011645 | 102 | 72.00873362445414847161572052401746724891 | 179310 | 77456.3534731668033915574963609898107715 | 190531.0631875342287845705967976710334788 | 41 | 1 | 1127 | 0 | 0 | 1127 | 42 | 55 | 55 | 60 | 192.619(C) | 1956-06-15 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A PIPE LEAK THAT REQUIRED A SYSTEM OUTAGE TO REPAIR | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2018-08-15 | NO | [12 empty] | NO | YES | CITY STREET | [12 empty] | UNKNOWN/OTHER | BACKHOE/TRACKHOE | UNKNOWN/OTHER | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER |  | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | JOSHUA FORT | SR. GAS ENGINEER | josh.fort@avistacorp.com | 509-495-2656 |  | TIM HARDING | tim.harding@avistacorp.com | 509-495-2784 | BRIAN SCHULTZ | MANAGER - NAT. GAS COMPLIANCE AND INTEGRITY | 509-495-2162 |  | brian.schultz@avistacorp.com | THE SPOKANE CITY WATER DEPARTMENT RESPONDED TO A LEAKING WATER SERVICE AT 3817 N CRESTLINE ST. PRIOR TO EXCAVATING, THE WATER CREW SMELLED NATURAL GAS IN THE AREA THEY WERE GOING TO DIG. THEY CONTACTED AVISTA TO REPORT THE GAS ODOR. AN AVISTA FIRST RESPONDER ARRIVED AND DETERMINED THAT AN AVISTA CONSTRUCTION CREW WOULD NEED TO INVESTIGATE THE LEAK. THE AREA WAS EXCAVATED AND THE LEAK LOCATION WAS FOUND TO BE ON THE BOTTOM OF THE STEEL GAS MAIN. THE LEAK WAS COMING FROM A CRACK OR SMALL HOLE INSIDE THE DENT. THIS DENT WAS LIKELY CAUSED BY EXCAVATION DAMAGE SOMETIME IN THE PAST. TO REPAIR THE LEAK, THE CREW NEEDED TO WELD A STEEL FITTING OVER THE DENT. PRIOR TO WELDING ON THE FITTING, THE CREW ATTEMPTED REDUCE THE GAS FLOW FROM THE LEAK BY INSERTING A PLUG. UNFORTUNATELY THIS CAUSED THE LEAK RATE TO INCREASE AND IT WAS DECIDED THAT THE SYSTEM SHOULD BE SHUT DOWN TO SAFELY WELD ON THE REPAIR FITTING. TEN VALVES IN THE SYSTEM WERE CLOSED AT MIDNIGHT ON 3/4/22. THIS CAUSED AN OUTAGE FOR 1169 CUSTOMERS. THE STEEL MAIN REPAIR WAS COMPLETE AT 01:00 3/4/22. ALL GAS METERS IN THE SYSTEM WERE SHUT OFF, THE SYSTEM WAS PURGED OF ANY AIR, AND CUSTOMER RELIGHTS STARTED AT 14:00 ON 3/4/22. RELIGHTS WERE COMPLETE AT 17:00 ON 3/5/22 WITH THE EXCEPTION OF SOME CUSTOMERS WHOSE HOMES WE WERE UNABLE TO ENTER. ON 3/9/22 IS WAS DETERMINED THAT THE INCIDENT COST HAD EXCEEDED THE FEDERAL THRESHOLD AND IT WAS REPORTED TO PHMSA (NRC).
2026-06-30 10:38 | NO | YES | NO | 20220030 | 39125 | 2022-04-12 21:21 | SUPPLEMENTAL FINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2022-03-13 01:55 | EASTERN | YES | 2022 | 908 COLLEGE AVENUE | HOUGHTON | HOUGHTON | MI | 49931 | 47.1221 | -88.5626 |  | YES |  |  |  | YES |  |  |  | 2022-03-13 09:05 | 1330926 | NA | NATURAL GAS |  | 69.457 | 0.113 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-13 01:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 30 | 2022-03-13 01:55 |  |  |  | 2022-03-13 03:19 | 2022-03-13 03:49 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1966 | UNKNOWN |  |  |  |  | 2 | API 5L, SEAMLESS STEEL, GRADE B | UNKNOWN | STEEL |  | SEAMLESS |  | 0.17 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 500000 | 531598.3606557375 | 166100 | 176596.9754098359975 | 710001 | 754870.735327868561475 | 0 | 0 |  | 5.82 | 404 | 285.211062590975254730713245997088791849 | 1 | 0.705967976710334788937409024745269286754 | 1376506 | 594324.9887046319100344541484716157205241 | 1463351.98842400974456451965065502183406 | 12 | 0 | 6 | 0 | 0 | 5 | 10 | 55 | 55 | 60 | 192.619(A)(2) | 1966-10-11 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RATE OF GAS VOLUME RELEASED WOULD NOT HAVE TRIGGERED ANY ALARMS OR AOCS THROUGH THE SCADA SYSTEM, AND THEREFORE THE CONTROLLERS WOULD NOT HAVE TAKEN ACTION. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2021-07-20 | NO |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | MIB82061284 | GLADSTONE MICHIGAN | NO | FACILITY OWNER | UNKNOWN/OTHER | YES | 188 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | JENNIFER POND | MANAGER OF CODES AND STANDARDS | jennifer.pond@semcoenergy.com | 8102422381 |  | MIKE KOSHT | michael.kosht@semcoenergy.com | (906) 250-7196 | PHIL LENN | DIRECTOR OF OPERATIONS SUPPORT | 8106503774 | phil.lenn@semcoenergy.com | ON MARCH 13, 2022, AT 1:58, AM, SEMCO ENERGY GAS COMPANY RECEIVED A CALL FROM THE MICHIGAN STATE POLICE INDICATING 908 COLLEGE AVE., IN HOUGHTON, MI HAD EXPLODED. THE SEMCO TECHNICIAN ARRIVED ON SITE 21 MINUTES AFTER THE INITIAL CALL, (INDICATED TIME IS 3:19 AM DUE TO DAYLIGHT SAVINGS TIME CHANGING AT 2:00 AM ON MARCH 13TH). WHEN THE SEMCO TECHNICIAN ARRIVED, THE HOUGHTON FIRE DEPT. WAS ATTENDING TO A FIRE AT THE STRUCTURE. ONCE THE FIRE WAS UNDER CONTROL, THE TECHNICIAN WAS ABLE TO SECURE GAS AT THE GAS METER SET. THROUGH THE LEAK INVESTIGATION PROCESS, THE TECHNICIAN DETERMINED THERE WAS A PROBABLE UNDERGROUND LEAK BASED ON LEL READINGS FOUND AT THE REAR OF THE RESIDENCE. THE TECHNICIAN CONTINUED THE LEAK INVESTIGATION AND FOUND GAS READINGS AT SURROUNDING BUILDINGS AND EVACUATED BUILDINGS ON COLLEGE AVE. AND ON E LAKESHORE. GAS FLOW WAS THEN SHUTOFF IN THE AREA IN WHICH READINGS WERE FOUND AND GAS WAS PURGED IN THOSE AREAS TO REDUCE GAS TO SAFE LEVELS. AN INVESTIGATION INTO THE SOURCE OF THE GAS LEAK WAS CONDUCTED IN THE SPRING WHEN GROUND CONDITIONS PERMITTED. A CAMERA WAS USED TO EVALUATE THE INSIDE OF THE PIPE THAT WAS SHUT DOWN DUE TO THE LEAK. THAT PROCESS INDICATED A DEFORMATION, WHICH THEN LED TO AN EXCAVATION TO EVALUATE. THE 2 IN. STEEL GAS MAIN WAS FOUND TO BE DAMAGED AT THE CROSSING OF A SANITARY SEWER LINE. THE DAMAGE ON THE PIPE WAS CONSISTENT WITH THE DIMENSIONS OF AN EXCAVATOR BUCKET. A METALLURGICAL EXAMINATION OF THE PIPE REPORTED THE DAMAGE CONSISTED OF OVERALL BENDING DEFORMATION, FLATTENING OF THE PIPE, AND DAMAGE TO THE PROTECTIVE COATING ON THE EXTERIOR OF THE PIPE. THIS DAMAGE WEAKENED THE PIPE MAKING IT MORE SUSCEPTIBLE TO FRACTURE OR CRACKING FROM EXTERNAL FORCES SUCH AS FREEZE/THAW CYCLES. GAS LEAKED FROM A CRACK IN THE PIPE AND MIGRATED THROUGH THE FROZEN GROUND AND INTO THE HOUSE AT 908 COLLEGE AVE. THE METALLURGICAL EXAMINATION ALSO REPORTED THE FRACTURE IN THE GAS MAIN WAS BRITTLE AND DID NOT EXHIBIT WALL THINNING OR CORROSION TO SUGGEST THE CRACK OR A PARTIAL CRACK ORIGINATED YEARS PRIOR TO THE EXPLOSION. DURING THE INVESTIGATION AND EXCAVATION OF THE DAMAGED PIPE, THE INITIAL OBSERVATION BEFORE THE PIPE WAS EXPOSED INDICATED A HOLLOWING OF THE SOIL NEAR THE FOUND CRACK, AND NO EVIDENCE OF DRY DIRT OR HARDENING OF THE SOIL CONSISTENT WITH A LONGSTANDING GAS LEAK. PHOTOS OBTAINED THROUGH A FOIA REQUEST INDICATED THE NATURAL GAS MAIN WAS LOCATED AND MARKED BY SEMCO, A FACT CONSISTENT WITH SEMCO'S LOCATING RECORDS. BASED ON THE RECORDS AND PHOTOS OBTAINED, IT IS REASONABLE TO BELIEVE THE EXCAVATOR DUG WITHOUT HAND EXPOSING THE GAS MAIN, AND AFTER THE MICHIGAN ONE CALL TICKET HAD EXPIRED. PHOTOS SHOWING THE TIME STAMP INDICATE THE DAMAGE LIKELY OCCURRED BETWEEN AUGUST 27TH AND AUGUST 28TH, 2008. THE EXCAVATOR ALSO APPEARED TO HAVE DAMAGED CONDUIT FOR A TELECOMMUNICATIONS LINE. SEMCO ENERGY WAS NEVER NOTIFIED OF THE DAMAGE TO THE PIPE DURING THE SEWER CONSTRUCTION. BASED ON THE INFORMATION GATHERED DURING THE INVESTIGATION, METALLURGICAL EVALUATION, AND INFORMATION REQUESTS, SEMCO CONSIDERS THE INVESTIGATION TO BE COMPLETED.
2026-06-30 10:38 | NO | NO | NO | 20220031 | 37336 | 2022-04-13 10:55 | SUPPLEMENTAL FINAL | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | NY | 12601 | 2022-03-14 16:20 | EASTERN | YES | 2022 | 449 FIRST ST. | NEWBURGH | ORANGE | NY | 12550 | 41.5027 | -74.0278 |  |  | YES | [6 empty] | 2022-03-14 18:31 | 1331058 | 1331191 | NATURAL GAS |  | 7.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-14 16:20 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 7.4 | YES | 6 | 2022-03-14 16:32 |  |  |  | 2022-03-14 16:32 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1951 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | CONTRACTOR HIRED BY RESIDENTIAL CUSTOMER CUT PRESSURIZED 1 1/4" STEEL PIPE IN THE BASEMENT OF THE HOUSE CAUSING A LEAK. THE SERVICE PIPE TO THE BUILDING FOUNDATION IS 2" AND THE PIPE REDUCES TO 1 1/4" NEAR THE FOUNDATION WALL. | CLASS 3 LOCATION | 0 | 0 | 9073 | 9646.383852459012675 | 13610 | 14470.10737704917475 | 0 | 0 |  | 9.1644 | 68 | 48.00582241630276564774381368267831149927 | 0 | 0 | 22751 | 9831.832033669796354599708879184861717613 | 24164.4970519244901906477438136826783115 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.31 | 0.31 | 0.5 | 192.623 | 1951-11-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | OTHER | CONTRACTOR HIRED BY RESIDENTIAL CUSTOMER CUT PRESSURIZED 1 1/4" STEEL SERVICE IN THE BASEMENT OF THE HOUSE CAUSING A LEAK. THE CONTRACTOR INTENDED TO CUT THE PIPE. | [155 empty] | JERRY AMATO JR. | DIRECTOR OF GAS COMPLIANCE | jamato@cenhud.com | 845.486.5642 |  | JERRY AMATO | jamato@cenhud.com | 845-486-5642 | ERIC KISZKIEL | MANAGER OF GAS OPERATIONS AND ENGINEERING | 845-486-5472 | ekiszkiel@cenhud.com | AT 4:25 PM ON 3/14/2022, CENTRAL HUDSON WAS NOTIFIED BY THE CITY OF NEWBURGH OF A POSSIBLE GAS EXPLOSION AT 449 FIRST ST. IN NEWBURGH. THE FIRST CENTRAL HUDSON RESPONDER ARRIVED ON SITE AT 4:32 PM AND A SECOND CENTRAL HUDSON RESPONDER ARRIVED AT 4:33 PM. THE BUILDING WAS ON FIRE WHEN THE RESPONDERS ARRIVED. ADDITIONAL SUPPORTING PERSONNEL INCLUDING SUPERVISORS AND GAS CONSTRUCTION CREW WERE EN ROUTE. APPROXIMATELY 6 PEOPLE WERE EVACUATED BY THE FIRE DEPARTMENT. THE BUILDING AT 449 FIRST ST. WAS PRESENTLY BEING RENOVATED AND WAS FED BY A 4 INCH LOW PRESSURE CAST IRON MAIN AND 197 FT. LONG 2 INCH STEEL SERVICE. A CURB VALVE WAS PRESENT ON THE SERVICE. THERE WERE THREE GAS METERS LOCATED INSIDE THE BUILDING'S BASEMENT WITH VALVES THAT WERE CLOSED AND LOCKED ON OCTOBER 25TH 2021. A CENTRAL HUDSON REPRESENTATIVE ON SCENE ADVISED THE FIRE DEPARTMENT TO CONTAIN THE HOUSE FIRE BUT TO ALLOW THE NATURAL GAS TO BURN TO PREVENT A SECOND IGNITION. A POLICE OFFICER INFORMED AN ONSITE CENTRAL HUDSON SUPERVISOR OF A REPORT OF THE CUSTOMER'S CONTRACTOR CUTTING THE SERVICE LINE OR CUSTOMER PIPE INSIDE THE BUILDING. A COMMERCIAL REPRESENTATIVE STOPPED THE FLOW OF GAS TO THE HOUSE BY CLOSING THE CURB VALVE ON THE SERVICE AT APPROXIMATELY 5:00 PM. ELECTRIC TAPS FOR THIS ADDRESS WERE CUT AT APPROXIMATELY 5:05PM. BY THIS TIME, ADDITIONAL CH EMPLOYEES HAD ARRIVED ON THE SCENE TO ASSIST IN THE EMERGENCY RESPONSE. THE CENTRAL HUDSON SUPERVISOR INFORMED THE FIRE DEPARTMENT THAT THEY MAY PROCEED WITH EXTINGUISHING THE HOUSE FIRE. AFTER THE BUILDING WAS MADE ACCESSIBLE BY THE FIRE DEPARTMENT, ONE CENTRAL HUDSON PERSONNEL AND CITY OF NEWBURGH FIRE INVESTIGATOR INVESTIGATED THE BASEMENT OF THE HOUSE AND CONFIRMED THAT THE SERVICE PIPE AND CUSTOMER PIPE HAD BEEN CUT AND DISASSEMBLED IN MULTIPLE LOCATIONS INCLUDING AT LEAST ONE LOCATION OF UPSTREAM OF THE THREE LOCKED GAS METERS. CENTRAL HUDSON AND CONTRACTOR CREWS LEAK SURVEYED THE ENTIRE PROPERTY AND THE SURROUNDING AREA. NO NATURAL GAS LEAKS WERE FOUND AT 449 FIRST ST. THE AREA OF 244 VAN NESS ST. WAS ALSO LEAK SURVEYED, AS THE SERVICE TO 449 FIRST ST. WAS FED FROM THAT ROAD. NO LEAKS WERE FOUND AT EITHER ADDRESS. GAS ODORANT READINGS WERE TAKEN IN THE SURROUNDING AREA TO VERIFY APPROPRIATE ODORIZATION OF GAS. THE NATURAL GAS SERVICE TO 449 FIRST ST. WAS PERMANENTLY RETIRED THAT EVENING AND THE AREA WAS DECLARED SAFE AT 9:40 PM.
2026-06-30 10:38 | NO | YES | NO | 20220032 | 36654 | 2022-04-21 15:15 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2022-03-24 01:15 | EASTERN | NO | 2022 | HIGHWAY 9 | BOILING SPRINGS | SPARTANBURG | SC | 29316 | 35.059 | -81.9935 | [5 empty] | YES |  |  |  |  | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 0.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-03-24 01:52 | NO |  |  | 2022-03-24 01:52 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | IN A CREEK. | 72 | NO | YES | [6 empty] | YES | BORED/DRILLED | FAWN BRANCH TRIBUTARY 2 | 1 | BELOW WATER, PIPE IN BORED/DRILLED CROSSING | INVESTOR OWNED |  | MAIN |  | 2014 | UNKNOWN |  |  |  |  | 6 | MDPE | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 344000 | 365739.6721311474 | 7200 | 7655.01639344262 | 0 | 0 |  | 0.1 | 0 | 0 | 0 | 0 | 351200 | 151620.524590163992 | 373394.68852459002 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 68 | 70 | 192.619(A)(2) | 2014-07-10 | PRESSURE DID NOT EXCEED MAOP | OTHER | INJECTION |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | DUE TO LOCATION OF PIPE UNDER CREEK, DAMAGED PORTION OF PIPE WAS DEACTIVATED AND LEFT IN PLACE. | [45 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | A PASSERBY IN A VEHICLE CALLED STATING THAT THEY SMELLED GAS. ONCE INVESTIGATED, GAS WAS FOUND BLOWING THROUGH THE WATER IN THE CREEK. DUE TO THE NATURE OF THE PIPE BEING LOCATED IN THE CREEK AND BENEATH A CONCRETE BOX CULVERT, THE PIPE WAS NOT EXPOSED AND WAS LEFT IN PLACE. THE TRUE CAUSE OF THE LEAK, HOLE SIZE, AND GAS VOLUMES COULD NOT BE DETERMINED. NEW PIPE WILL BE BORED UNDER CREEK FOR REPAIR. THE NRC WAS NOT NOTIFIED AT THE TIME OF INCIDENT BECAUSE THE ESTIMATED COST WAS BELIEVED TO BE BELOW THE 122K THRESHOLD.
2026-06-30 10:38 | NO | YES | NO | 20220033 | 36728 | 2022-04-25 13:28 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2022-04-05 01:55 | CENTRAL | YES | 2022 | 4809 TROUP HWY | TYLER | SMITH | TX | 75703 | 32.2986 | -95.2662 |  |  |  | YES | [5 empty] | 2022-04-05 05:25 | 1332738 | 1332887 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-04-05 01:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.5 | NO | 0 | 2022-04-05 01:55 |  |  |  | 2022-04-05 02:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1994 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | OTHER | REGULATOR BODY | [9 empty] | OTHER | [8 empty] | DURING A LOCAL STORM A PONTOON BOAT BELONGING TO TYLER CAR & TRUCK CENTER, ROLLED INTO METER SET AND TYLER CAR & TRUCK CENTER BUILDING, RESULTING IN DAMAGE TO REGULATOR ALLOWING GAS TO BE RELEASED. | CLASS 3 LOCATION | 125000 | 132899.590163934375 | 300 | 318.9590163934425 | 676 | 718.7209836065571 | 0 | 0 |  | 4.72 | 5 | 3.52983988355167394468704512372634643377 | 0 | 0 | 125981 | 54389.3987524757406985735080058224163028 | 133940.8000038179262739446870451237263464 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 50 | 60 | 192.619(A)(1) | 1970-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [56 empty] | HIGH WINDS | [5 empty] | YES |  |  |  | YES | THUNDER STORMS/HIGH WINDS | [178 empty] | YES |  |  | YES | [31 empty] | LESLIE DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-9325 |  | JASON SURRATT | jason.surratt@centerpointenergy.com | 7775006234 | RANDALL SANDERS | DIRECTOR OF OPERATIONS TX. REGION | 713-207-5708 | randall.x.sanders@centerpointenergy.com | DURING A LOCAL THUNDER STORM A PONTOON BOAT ON TRAILER OWNED BY TYLER CAR & TRUCK CENTER, ROLLED INTO METER SET AND TYLER CAR & TRUCK CENTER BUILDING, RESULTING IN DAMAGE TO REGULATOR ALLOWING GAS TO BE RELEASED. RESULTING IN IGNITION OF GAS DAMAGING BUILDING AND CONTENTS. (PART A, LINE #4 RESPONSE OF 0525AM WAS THE TIME OF CONFIRMED DISCOVERY THAT IT MET CRITERIA) DUE TO RESTRICTED ACCESS. DUE TO RESTRICTED ACCESS CONFIRMED DISCOVERY WAS NOT UNTIL 0525 AM THAT MORNING.
2026-06-30 10:38 | YES | NO | NO | 20220037 | 36688 | 2022-05-20 16:22 | ORIGINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2022-04-22 04:18 | CENTRAL | YES | 2022 | 302 MAPLE | ONAWA | MONONA | IA | 51040 | 42.0212 | -96.0879 | [5 empty] | YES |  |  |  | 2022-04-22 06:06 | 1334144 | 1334323 | NATURAL GAS |  | 8.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-04-22 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 8.5 | NO | 1 | 2022-04-22 04:18 |  |  |  | 2022-04-22 00:50 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2000 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.5 | 2406 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 7 |  |  | 2406 | OTHER | [8 empty] | LEAK CAUSED BY FIRE DAMAGE TO METER AND REGULATOR. | CLASS 4 LOCATION | 11200 | 11907.80327868852 | 3000 | 3189.590163934425 | 15000 | 15947.950819672125 | 0 | 0 |  | 8.14 | 69 | 48.71179039301310043668122270742358078603 | 0 | 0 | 29269 | 12645.9347841649414323144104803493449782 | 31094.0560526880831004366812227074235808 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 25 | 25 | 66.6 | 192.619(A)(1) | 2000-01-30 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [143 empty] | YES | [24 empty] | ANTHONY ENGLING | SUPERVISOR PIPE LINE SAFETY PROFESSIONAL | tony.engling@blackhillscorp.com | 15635854014 | 563-583-0850 | GARY HOGAN | gary.hogan@blackhillscorp,com | 1-402-221-2536 | TONY JOHN ENGLING | SUPERVISOR PIPE LINE SAFETY PROFESSIONAL | 15635854014 | tony.engling@blackhillscorp.com | ON 4/22/2022 AT 04:18 CENTRAL TIME BLACK HILLS ENERGY WAS NOTIFIED BY EMERGENCY RESPONDERS OF A RESIDENTIAL FIRE AND REQUESTED BHE TO RESPOND. THE LOCATION IS 302 MAPLE IN ONAWA IOWA. UPON ARRIVAL THE TECHNICIAN FOUND THE HOME ENGULFED IN FLAMES. THE FIRE HAD CAUSED DAMAGE TO THE METER AND REGULATOR. THE SERVICE LINE WAS EXCAVATED AT THE STREET AT A SAFE DISTANCE FROM THE FIRE AND CUT OFF AND CAPPED.
2026-06-30 10:38 | NO | YES | YES | 20220039 | 36740 | 2022-06-10 09:02 | ORIGINAL FINAL | 12878 | MOUNTAINEER GAS CO | 501 56TH ST. SE | CHARLESTON | WV | 25304 | 2022-05-13 20:10 | EASTERN | YES | 2022 | 611 WHITESTICK ST. | MABSCOTT | RALEIGH | WV | 25871 | 37.7758 | -81.2121 | [7 empty] | YES | FULL-CIRCLE BAND LEAK CLAMP | 2022-05-13 20:13 | 1335962 | 1336073 | NATURAL GAS |  | 14.887 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2022-05-13 14:10 | YES | OPERATOR | 2022-05-13 14:50 | 2022-05-13 14:10 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1972 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | ALDYL-A | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 600 | 637.918032786885 | 500 | 531.5983606557375 | 0 | 0 |  | 6.739 | 100 | 70.5967976710334788937409024745269286754 | 0 | 0 | 1200 | 532.389803612761771470160116448326055313 | 1240.113191113655978893740902474526928675 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 30 | 30 | 40 | 192.619(A)(4) | 2016-08-24 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PUNCTURE DIDN'T REDUCE SYSTEM PRESSURE ENOUGH TO CAUSE AN ALARM AT GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | WATER | YES | 2213316772 | N/A |  | FACILITY OWNER | NO | NO |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | EMERGENCY 1 CALL TICKET BUT DID NOT WAIT FOR MARKS | [169 empty] | PHILIP KINGREY | MANAGER ENGINEERING AND COMPLIANCE | philipkingrey@mgcwv.com | 3043892714 | 3049259605 | JOHN LIVELY | johnlively@mgcwv.com | 3046674669 | THOMAS WESTFALL | VICE PRESIDENT GAS SUPPLY AND TECHNICAL SERVICES | 3045395740 | thomaswestfall@mgcwv.com | BECKLEY WATER COMPANY WERE MAKING A WATER LEAK REPAIR AND CALLED IN AN EMERGENCY ONE-CALL TICKET. THEY DID NOT WAIT FOR UNDERGROUND UTILITIES TO BE LOCATED BEFORE DIGGING AND PUNCTURED MOUNTAINEER GAS COMPANY'S 2" PLASTIC NATURAL GAS DISTRIBUTION PIPELINE OPERATING NEAR 30 PSIG. BECKLEY WATER COMPANY NOTIFIED MOUNTAINEER GAS COMPANY'S DISPATCH CENTER. MOUNTAINEER EMPLOYEES WERE DISPATCHED TO THE SCENE. WHILE INSTALLING A FULL CIRCLE BAND CLAMP, TWO OF THEM WERE OVERCOME WITH GAS AND REMOVED FROM THE LEAK AREA BY PERSONNEL ONSITE. MOUNTAINEER NOTIFIED 911 AND EMERGENCY MEDICAL PERSONNEL RESPONDED TO THE SCENE TO PROVIDE MEDICAL TREATMENT. ONE EMPLOYEE WAS TAKEN TO THE HOSPITAL IN AN AMBULANCE AND THE OTHER WAS TAKEN TO THE HOSPITAL BY ANOTHER EMPLOYEE. BOTH EMPLOYEES WERE GIVEN A MEDICAL ASSESSMENT AT THE HOSPITAL, ONE WAS ADMITTED TO INPATIENT HOSPITALIZATION FOR OBSERVATION, AND THE OTHER WAS RELEASED.
2026-06-30 10:38 | NO | NO | NO | 20220040 | 37711 | 2022-06-10 14:10 | SUPPLEMENTAL FINAL | 12582 | ATMOS ENERGY CORPORATION - MISSISSIPPI | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-05-12 14:30 | CENTRAL | YES | 2022 | 100333 IMC ROAD | ABERDEEN | MONROE | MS | 39730 | 33.7684 | -88.5722 | YES | [5 empty] | YES |  |  | 2022-05-12 14:42 | 1335844 | 1335944 | NATURAL GAS |  | 5914 | 379 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-05-12 08:45 | YES | OPERATOR | 2022-05-12 08:45 | 2022-05-12 09:10 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | 1969 |  |  |  |  | 8 | API 5LX-1968 | REPUBLIC STEEL | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.188 | [6 empty] | LEAK |  |  | OTHER | 2-INCH NIPPLE SHEARED OFF PIPE | [5 empty] | CLASS 1 LOCATION | 0 | 0 | 10001 | 10633.030409836061475 | 12575 | 13369.698770491798125 | 0 | 0 |  | 7.3268 | 43331 | 30590.2983988355167394468704512372634643 | 2777 | 1960.473071324599708879184861717612809316 | 68684 | 36256.9624530508066694614264919941775837 | 56553.5006504879760483260553129548762736 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 250 | 350 | 385 | 192.619(A)(2) | 1969-11-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OTHER THAN PROVIDING ALERTS TO OPERATIONS AS THE EVENT OCCURRED, THE CONTROL ROOM HAD NO INVOLVEMENT IN THIS INCIDENT. | [12 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  | YES | PRIVATE EASEMENT | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 22042814572130 |  |  | CONTRACT LOCATOR | YES | YES | 11 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | DEAN MORRIS | MANAGER OF COMPLIANCE | dean.morris@atmosenergy.com | 6015925360 |  | WADE SHULTICE | wade.shultice@atmosenergy.com | 6622512018 | JAMES E. MCKENZIE | VICE PRESIDENT TECHNICAL SERVICES | 6016249408 | james.mckenzie@atmosenergy.com | ATMOS ENERGY'S SECOND-PARTY CONTRACTOR WAS IN THE PROCESS OF REPLACING A CRITICAL VALVE ON AN 8-INCH HIGH PRESSURE DISTRIBUTION LINE NEAR ABERDEEN, MS. THE PROJECT WAS BEING WORKED UNDER MISSISSIPPI ONECALL LOCATE TICKET #2204814572130, AND PROPER LOCATE PRACTICES WERE USED PRIOR TO BEGINNING THE PROJECT USING ALL AVAILABLE INFORMATION ON THE ASSETS IN THE AREA AND LOCATE TECHNOLOGY. UNKNOWN TO ATMOS ENERGY OR THE SECOND PARTY CONTRACTOR, THERE WAS AN UNLOCATABLE AND UNMAPPED 2-INCH NIPPLE AND VALVE LOCATED IN THE VERTICAL POSITION ON THE CARRIER PIPE, AND THIS UNMAPPED AND UNLOCATABLE ASSET WAS DAMAGED DURING EXCAVATION ACTIVITIES. THE CONTRACTOR RESPONDED TO THE DAMAGE USING APPROPRIATE EMERGENCY RESPONSE PRACTICES. IN ORDER TO ELIMINATE THE HAZARDOUS CONDITION, A STOPPLE FITTING WAS WELDED ONTO THE CARRIER PIPE AND TAPPED. DURING THE REPAIR, THE UNINTENTIONAL LOSS OF GAS EXCEEDED THE REPORTABLE THRESHOLD, AND ATMOS ENERGY REPORTED THE DAMAGE AS AN INCIDENT.
2026-06-30 10:38 | NO | YES | NO | 20220044 | 36927 | 2022-07-05 18:18 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2021-01-27 12:00 | EASTERN | YES | 2021 | LOCKHART ROAD | BELPRE | WASHINGTON | OH | 45714 | 39.2913 | -81.5726 | [7 empty] | YES | DEO DETERMINED THIS LEAK TO BE NON-HAZARDOUS BASED ON THE SIZE AND REMOTE LOCATION OF THE LEAK. |  | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 3.75 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-10-23 10:00 | NO |  |  | 2020-10-23 12:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | LEGACY PIPELINE BY-PASS/FITTING | 2004 | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | 0 | 0 | 1321100 | 1459499.8807597304921 | 500 | 552.3805468018055 | 0 | 0 |  | 2.65 | 10 | 8.05647840531561461794019933554817275748 | 0 | 0 | 1321610 | 592874.9031703371047335548172757475083056 | 1460060.31778493761321461794019933554817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 160 | 175 | 192.619(A)(2) | 2004-06-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM DID NOT DETECT THE INCIDENT DUE TO MINIMAL SIZE OF LEAK AND MINIMAL RELEASE OF GAS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | A029702031 | OHIO811 |  | CONTRACT LOCATOR | UNKNOWN/OTHER | NO |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | DATA NOT COLLECTED | [169 empty] | ALLISON S WALTERS-THOMPSON | MANAGER GAS OPERATIONS | a.walters-thompson@dominionenergy.com | 2167899152 |  | AMY KONCELIK | amy.l.koncelik@dominionenergy.com | 3308109842 | ALLISON WALTERS-THOMPSON | MANAGER GAS OPERATIONS | 2167899152 | a.walters-thompson@dominionenergy.com | 2ND PARTY CONTRACTOR HIT AN UNMARKED DEO HP LINE STUB THAT HAD BEEN ORIGINALLY USED AS A BY-PASS CREATING A MINIMAL LEAK IN A REMOTE HEAVY TERRAIN AREA.
2026-06-30 10:38 | NO | YES | NO | 20220045 | 36950 | 2022-07-07 14:10 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2022-06-07 17:07 | PACIFIC | YES | 2022 | 7015 TELEGRAPH ROAD | COMMERCE | LOS ANGELES | CA | 90040 | 33.987 | -118.1346 | YES | [8 empty] | 2022-06-07 17:53 | 1338079 | 1338306 | NATURAL GAS |  | 2357 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-06-07 09:05 | YES | OPERATOR | 2022-06-07 09:08 | 2022-06-07 09:05 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 93 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1953 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.24 | [6 empty] | RUPTURE |  |  |  |  | LONGITUDINAL |  | 31.5 | 1.5 |  | CLASS 3 LOCATION | 0 | 0 | 250000 | 265799.18032786875 | 150000 | 159479.50819672125 | 0 | 0 |  | 6 | 14142 | 9983.799126637554585152838427947598253275 | 0 | 0 | 414142 | 180819.6599613430393013100436681222707424 | 435262.4876512275545851528384279475982533 | 55 | 36 | 12 | 0 | 0 | 12 | 91 | 223.58 | 115 | 125 | 192.619(C) | 1953-10-01 | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NONE |  | 8.9 |  | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 18 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [61 empty] | YES | [5 empty] | YES | [5 empty] | MIGUEL GAMBOA | PIPELINE SAFETY AND COMPLIANCE ADVISOR | mgamboa@socalgas.com | 818-618-2564 |  | MIGUEL GAMBOA | mgamboa@socalgas.com | 818-618-2564 | MIGUEL GAMBOA | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 818-618-2564 | mgamboa@socalgas.com | ON 06-07-2022, SOCALGAS CREWS RESPONDED TO AN OVERPRESSURE ON A DISTRIBUTION MAIN IN THE CITY OF COMMERCE. THE OVERPRESSURE OCCURRED DURING THE PROCESS OF CONDUCTING AN IN-LINE INSPECTION RUN. THERE WERE NO INJURIES OR FATALITIES FROM THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE DOT AND THE CPUC DUE TO ESTIMATED PROPERTY DAMAGE EXCEEDING $122,000. 8/5/22 UPDATE - AFTER FURTHER INVESTIGATION, IT WAS DETERMINED THAT DURING THE ILI PIGGING OPERATION, EXCESS LIQUID DEBRIS LOCATED IN TRANSMISSION PIPELINE L-2000 WERE INADVERTENTLY DIRECTED INTO THE DISTRIBUTION SYSTEM, CAUSING A REGULATOR STATION TO STAY OPEN AND OVER PRESSURIZE A DISTRIBUTION PIPELINE. ALL REPAIRS TO THE PIPELINE HAVE BEEN COMPLETED AND NO FURTHER GAS LEAKAGE WAS FOUND. THE REGULATOR STATION WAS REBUILT, TESTED AND ALL LIQUIDS REMOVED. THERE HAVE BEEN NO FURTHER CONCERNS.
2026-06-30 10:38 | NO | NO | NO | 20220047 | 36836 | 2022-07-07 16:07 | ORIGINAL FINAL | 18508 | SOUTHERN INDIANA GAS & ELECTRIC CO | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2022-05-23 15:30 | CENTRAL | YES | 2022 | 2710 WINDEMERE | EVANSVILLE | VANDERBURGH | IN | 47725 | 38.0637 | -87.5149 | [5 empty] | YES |  |  |  | 2022-05-23 18:25 | 1336798 |  | NATURAL GAS |  | 73.612 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-05-23 15:30 | OPERATOR/CONTRACTOR |  | 73.6 | NO | 12 | 2022-05-23 15:35 |  |  |  | 2022-05-23 16:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1997 | UNKNOWN |  |  |  |  | 2 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 60000 | 63791.8032786885 | 8000 | 8505.5737704918 | 500 | 531.5983606557375 | 10000 | 10631.96721311475 | CURRENT ESTIMATED 2.B IS FOR CAPPING ENDS. 10K WOULD BE IF ENDS WERE RECONNECTED | 5.175 | 381 | 268.973799126637554585152838427947598253 | 0 | 0 | 78881 | 34109.1840861908640393013100436681222707 | 83729.9164220774250545851528384279475983 | 0 | 0 | 2 | 0 | 0 | 5 | 0 | 58 | 58 | 60 | 192.619(A)(2) | 1997-03-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS INITIATED BY A THIRD PARTY EXCAVATOR HITTING A PLASTIC DISTRIBUTION MAIN WHICH IGNITED ALMOST IMMEDIATELY. GAS CONTROL WAS NOT INVOLVED, COULD NOT HAVE RESPONDED TO OR MINIMIZED THE LOSS OR DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ELECTRIC | NO |  |  |  | CONTRACT LOCATOR | YES | YES | 2 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | SCOTT CHANDLER | LEAD OPERATION SPECIALIST | scott.chandler@centerpointenergy.com | 812-491-4117 |  | SCOTT CHANDLER | scott.chandler@centerpointenergy.com | 812-491-4117 | SHERRI BELL | MANAGER PIPELINE SAFETY AND COMPLIANCE | 812-491-4806 | sherri.bell@centerpointenergy.com | DCI WAS CONTRACTED BY CENTERPOINT INDIANA-ELECTRIC TO INSTALL UNDERGROUND ELECTRIC LINES AND A NEW JUNCTION BOX IN THE GREEN SPACE ACROSS FROM 2710 WINDEMERE DRIVE, EVANSVILLE, INDIANA 47725 (VANDERBURGH COUNTY). DCI HAD SUBCONTRACTED THE EXCAVATION WORK OUT TO EARLEY ELECTRIC. ON MAY 23, 2022, LESTER KNEPP WITH EARLEY ELECTRIC WAS OPERATING A CATERPILLAR 304E MINI EXCAVATOR TO EXPOSE UNDERGROUND ELECTRIC LINES ALONG THE SOUTH SIDE OF WINDEMERE DRIVE. DCI HAD CALLED FOR LOCATES BY CALLING INDIANA 811 AND GOT A LOCATE TICKET # 2205092040 ON MAY 9, 2022. EARLEY ELECTRIC AND MR. KNEPP WERE UNDER THE MISTAKEN IMPRESSION THEY COULD EXCAVATE UNDER DCI'S LOCATE AND THEREFORE DID NOT CALL FOR THEIR OWN LOCATE TICKET. AT APPROXIMATELY 1530HR., MR. KNEPP, WHILE OPERATING THE MINI EXCAVATOR, HIT A 2' PE UNDERGROUND GAS MAIN OWNED AND OPERATED BY SOUTHERN INDIANA GAS AND ELECTRIC COMPANY D.B.A CENTERPOINT ENERGY INDIANA ' SOUTH. THE GAS MAIN WAS OPERATING AT APPROXIMATELY 58 PSIG. EARLEY ELECTRIC EMPLOYEE AARON SCHROER WITNESSED THE EVENT, STATING MR. KNEPP UPON HITTING THE MAIN, EXITED THE EXCAVATOR LEAVING IT RUNNING. ACCORDING TO MR. SCHROER, THE GAS WAS BLOWING FOR ABOUT 25 SECONDS BEFORE IT IGNITED. MR. SCHROER NOTIFIED 911 IMMEDIATELY AT APPROXIMATELY 1530HRS. MR. SCHROER STATED THEY DID NOT NOTICE THE GAS LOCATE MARKS THAT WERE PART OF DCI'S MAY 9TH LOCATE TICKET. THE LOCATE WAS PERFORMED ON MAY 10, 2022. LOCATE PICTURES FROM THAT DATE SHOW THE GAS FACILITY WERE PROPERLY FLAGGED AND MARKED. AT THE TIME OF THE EVENT, GAS FACILITY LOCATE FLAGS HAD BEEN REMOVED AND MARKS WERE FAINT. CENTERPOINT DISPATCH WAS NOTIFIED BY 911 DISPATCH APPROXIMATELY 1535HRS. CENTERPOINT GAS CREW WAS NOTIFIED AT 1543HRS. AND ARRIVED ON SCENE AT 1615HRS. THE GAS FROM THE MAIN WAS STILL BURNING. THE PE MAIN WAS DUEL FED SO THE CENTERPOINT GAS CREW DUG UP AND EXPOSED THE MAIN ON THE EAST AND WEST SIDE OF THE DAMAGE. THE GAS CREW PERFORMED SQUEEZE OFF OPERATIONS STOPPING THE FLOW OF GAS AND EXTINGUISHING THE FIRE AT 1700HRS. PRIOR TO SQUEEZING OFF, TWO CUSTOMERS WERE TAKEN OUT OF SERVICE SO THAT GAUGES COULD BE INSTALLED. AT THE TIME OF INSTALLATION, THE EAST GAUGE READ 25PSIG WHERE THE WEST SIDE READ 4PSIG. AFTER SQUEEZE OFF, PRESSURE ON BOTH SIDES RETURN TO NEAR NORMAL PRESSURES. CENTERPOINT DISPATCH SENT OUT AN EMAIL ALERTING STAKEHOLDER, INCLUDING MEMBERS OF THE INDIANA UTILITY REGULATORY COMMISSION, PIPELINE SAFETY DEPARTMENT OF THE INITIAL REPORT FROM 911 AT 1545HRS. CENTERPOINT PIPELINE SAFETY AND COMPLIANCE DEPARTMENT WAS IN CONTACT WITH MEMBERS OF THE INDIANA UTILITY REGULATORY COMMISSION, PIPELINE SAFETY DEPARTMENT SHORTLY THEREAFTER. INDIANA UTILITY REGULATORY COMMISSION, PIPELINE SAFETY DEPARTMENT, CHIEF ENGINEER RICH MEDCALF ARRIVED ON SCENE AND INVESTIGATED. LOCAL NEWS MEDIA COVERAGE AS WELL AS MEMBERS OF THE PUBLIC POSTED VIDEO OF THE FIRE ON SOCIAL MEDIA SITES. ON BOTH SIDES OF THE DAMAGE, THE MAIN WAS CUT AND CAPPED OFF A SHORT DISTANCE FROM WHERE IT WAS SQUEEZED OFF. IT HAS YET TO BE DETERMINED IF OR WHEN THE MAIN WILL BE RESTORED TO DUAL FED STATUS. CENTERPOINT PIPELINE SAFETY AND COMPLIANCE DEPARTMENT LEAD OPERATION SPECIALIST DECIDED TO CONTACT THE NRC, DESPITE THE EVENT NOT MEETING REPORT CRITERIA, DUE TO THE AMOUNT OF ATTENTION AND VIDEO.
2026-06-30 10:38 | NO | NO | NO | 20220050 | 37104 | 2022-07-15 16:00 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2022-06-16 05:34 | EASTERN | YES | 2022 | 10611 14 MILE RD NE | ROCKFORD | KENT | MI | 49341 | 43.1764 | -85.4072 | [5 empty] | YES |  |  |  | 2022-06-16 11:25 | 1338925 | 1339649 | NATURAL GAS |  | 25 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-06-16 09:12 | OPERATOR/CONTRACTOR |  | 0 | NO | 7 | 2022-06-16 05:38 |  |  |  | 2022-06-16 06:17 |  | NO | PRIVATE PROPERTY | TRANSITION AREA | OTHER | BOTH UNDERGROUND AND ABOVEGROUND |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1981 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.625 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 10 |  |  | 3408 | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 50000 | 53159.83606557375 | 0 | 0 | 26452 | 28123.6796721311367 | 0 | 0 | PROPERTY DAMAGE COST UNKNOWN. FIRE DAMAGE FROM ELECTRIC SURGE EST. $50,000 | 4.3 | 108 | 76.24454148471615720524017467248908296943 | 0 | 0 | 76560 | 33068.0537747870409531877729257641921397 | 81359.760279189602857205240174672489083 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1981-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 100 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [134 empty] | YES | [8 empty] | YES | [24 empty] | JUSTIN C MORRIS | ENGINEER | justin.morris@dteenergy.com | 2484621760 |  |  |  |  | JUSTIN C MORRIS |  | 2484621760 | justin.morris@dteenergy.com | AT 05:38, FIRE DEPT NOTIFIED DTE GAS OF A RESIDENTIAL FIRE. FIRST CREW ARRIVED AT 06:17. INITIAL FIRE WAS CAUSED BY LIGHTNING OR DOWNED POWER LINE. BETWEEN 07:30 AND 11:00, SEVERAL SMALL GAS LEAKS WERE DISCOVERED. NRC WAS NOTIFIED AT 11:25, AND MICHIGAN PUBLIC SERVICE COMMISION AT 11:36. MULTIPLE HOUSES ALONG 14 MILE NE BECAME ENERGIZED BY THE LIGHTNING STRIKE OR DOWNED POWER LINE. THE ELECTRICAL SURGE LOCALLY ENERGIZED CABLES WITHIN HOMES, CAUSING FIRE DAMAGE. THE ELECTRICAL SURGE ALSO LOCALLY AFFECTED GAS SERVICE TRACER WIRES. TRACER WIRE DAMAGE TO PLASTIC GAS SERVICES RESULTED IN PINHOLE TYPE LEAKS. THE THREE AFFECTED SERVICE LINES THAT WERE COMPROMISED BY HOUSE FIRE AND SURGES TO TRACER WIRES WERE FULLY RENEWED WITHIN 24 HOURS. THE THREE AFFECTED RESIDENTIAL ADDRESSES WERE 10509 14 MILE RD NE, 10567 14 MILE RD NE, AND 10611 14 MILE RD NE. ALL THREE SERVICES WERE 5/8" HD PLASTIC INSTALLED IN 1981 OR 1988. TOTAL GAS LOSS IS MINIMAL DUE TO SIZE OF LEAKS AND ESTIMATED AT 25 MCF. AT 10611 14 MILE, A SMALL, PINHOLE LEAK WAS FOUND BURNED INTO THE SERVICE APPROXIMATELY 30' FROM THE HOME, BUT THE FIRE WAS ON THE INSIDE OF THE HOUSE, NOT THE OUTSIDE. AT 10567 14 MILE, THIS HOUSE HAD ALUMINUM SIDING THAT BECAME ENERGIZED. THE ELECTRICITY ARC'D FROM THE SIDING TO THE TRACER WIRE WHICH THEN WENT BELOW GRADE AND BURNED A SMALL HOLE IN THE SERVICE LINE. FIRE WAS ON OUTSIDE OF HOUSE INCLUDING METER MANIFOLD. AT 10509 14 MILE, SERVICE WAS ALSO RENEWED AS PRECAUTION. ALL THREE RESIDENCES HAD SERVICES RENEWED.
2026-06-30 10:38 | NO | YES | NO | 20220051 | 37524 | 2022-07-15 16:38 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-01-14 16:00 | CENTRAL | YES | 2022 | 9301 WHITE SETTLEMENT | WHITE SETTLEMENT | TARRANT | TX | 76108 | 32.7605 | -97.4754 | [6 empty] | YES |  |  | 2022-06-15 12:41 | 1338839 | 1339031 | NATURAL GAS |  | 15.369 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-14 16:00 | YES | OPERATOR | 2022-01-14 16:08 | 2022-01-14 16:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1955 | UNKNOWN |  |  |  |  | 16 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 129307 | 137478.778442622897825 | 32882 | 34960.03459016392095 | 0 | 0 |  | 7.874 | 121 | 85.42212518195050946142649199417758369723 | 0 | 0 | 162310 | 70090.0183836829435234788937409024745269 | 172524.2351579687692844614264919941775837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 60 | 192.619(A)(2) | 1955-08-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | SEWER (SANITARY/STORM) | YES | 2251192444 | TEXAS 811 |  | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | JULIE CAMPBELL | COMPLIANCE ANALYST | julie.campbell@atmosenergy.com | 214-535-6117 |  | ROBERT WILLIAMS | robert.williams@atmosenergy.com | 8172072998 | JEFF KNIGHTS | SR VP TECHNICAL SERVICES | 214-206-2701 | jeff.knights@atmosenergy.com | ON JANUARY 14, 2022, A THIRD-PARTY CONTRACTOR WAS DIRECTIONAL DRILLING AND BORED INTO ATMOS ENERGY'S 16-INCH STEEL GAS MAIN AT 9301 WHITE SETTLEMENT ROAD. THE INTERMEDIATE PRESSURE MAIN IS A TWO-WAY FEED. THE TECHNICIAN ARRIVED ON THE SCENE AND CONFIRMED THE LEAK AT 4:00 PM. ASSISTANCE WAS REQUESTED AT 4:20 PM. AT 4:08 PM THE TECH NOTED THAT FIRE DEPARTMENT WAS ON SITE INDICATING THEY WERE CONTACTED PRIOR TO THAT TIME. THIS IS THE TIME PROVIDED IN PART A QUESTION 15. OTHER NOTES INDICATE THE POLICE DEPARTMENT WAS ALSO ON THE SCENE, HOWEVER THERE IS NOT A TIME GIVEN. FIRE AND POLICE REMAINED ON SCENE TO PROVIDE TRAFFIC AND PERIMETER ASSISTANCE. STOPPLE FITTINGS WERE APPLIED TO CONTROL THE RELEASE OF GAS AND A SPLIT-WELD SLEEVE WAS INSTALLED TO REPAIR THE LEAK. THESE PERMANENT REPAIRS WERE COMPLETED ON JANUARY 15, 2022, AT 6:30 AM. ON JUNE 15, 2022 AT APPROXIMATELY 12:06 PM, IT WAS DETERMINED THAT REPAIRS COSTS HAD MET THE REPORTING THRESHOLD. A REPORT WAS MADE TO NRC WITHIN THE HOUR. REGARDING PART C QUESTION 5 - THE DIAMETER OF THE PUNCTURE IS 0.226 INCHES, BUT THE FORM ONLY ALLOWS WHOLE NUMBERS. SUPPLEMENTED TO PROVIDE ANSWERS IN PART C, QUESTION 2A AND PART E, QUESTION 3B. 12/19/2022 - FURTHER SUPPLEMENTED TO CHANGE THE SUB-CAUSE FROM FACILITY MARKING OR LOCATION NOT SUFFICIENT TO INCORRECT FACILITY RECORDS/MAPS.
2026-06-30 10:38 | NO | YES | YES | 20220053 | 37368 | 2022-07-21 19:22 | SUPPLEMENTAL FINAL | 180 | SPIRE ALABAMA INC. | 605 RICHARD ARRINGTON JR BLVD N | BIRMINGHAM | AL | 35203 | 2022-06-20 11:15 | CENTRAL | YES | 2022 | 198 BRICK PLANT RD | CORDOVA | WALKER | AL | 35550 | 33.7578 | -87.2124 | YES | [8 empty] | 2022-06-20 13:24 | 1339286 | 1339308, 1339472 | NATURAL GAS |  | 575 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2022-06-20 11:15 | ALLOWED TO BURN OUT |  | 575 | NO | 0 | 2022-06-20 11:15 | NO |  |  | 2022-06-20 12:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 34 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1.8 | 7 | [7 empty] | CLASS 1 LOCATION | 60000 | 63791.8032786885 | 23000 | 24453.524590163925 | 2000 | 2126.39344262295 | 119000 | 126520.409836065525 | RELIGHTS AND RECONNECTS | 13.07 | 7515 | 5305.349344978165938864628820960698689956 | 0 | 0 | 211515 | 92391.9990693679194759825327510917030568 | 222197.48049251906593886462882096069869 | 66 | 1 | 400 | 0 | 1 | 400 | 67 | 138 | 138 | 150 | 192.619(A)(4) | 1987-01-01 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER RESPONDED TO THE SCADA INFORMATION AND MADE THE APPROPRIATE NOTIFICATIONS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE EASEMENT | YES | [9 empty] | OCCUPANT | UNKNOWN/OTHER | DRAINAGE | NO |  |  |  | UNKNOWN/OTHER | NO | YES | 27 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [143 empty] | YES | [26 empty] | RANDY WILSON | DIRECTOR PIPELINE SAFETY AND COMPLIANCE | randy.wilson@spireenergy.com | 205-337-1337 |  | RANDY WILSON | randy.wilson@spireenergy.com | 205-337-1337 | CRAIG HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A 4" HIGH PRESSURE STEEL MAIN WAS DAMAGED BY A FRONT END LOADER AND THE RELEASED GAS IGNITED. THE FIRE TOTALLY DESTROYED THE CONSTRUCTION EQUIPMENT, A MOTOR VEHICLE, AND SURROUNDING BRUSH. THE FRONT END LOADER OPERATOR WAS SEVERELY BURNED IN THE INCIDENT AND WAS HOSPITALIZED. THE EXCAVATOR DID NOT MAKE ANY NOTIFICATION TO THE ONE CALL CENTER FOR LINE LOCATES. HOWEVER, PIPELINE MARKER SIGNS WERE NEAR THE LOCATION THAT WAS DAMAGED. THE PIPELINE WAS SHUT DOWN TO STOP THE FIRE AND ALLOW FOR REPAIRS. 467 CUSTOMERS WERE WITHOUT SERVICE UNTIL REPAIRS WERE COMPLETED. CONFIRMATION OF THE INCIDENT CONDITION BEING MET OF INJURY LIKELY REQUIRING HOSPITALIZATION WAS DETERMINED AT 12:48 PM. THIS WAS WHEN THE OPERATOR OF THE FRONT-END LOADER WAS TRANSPORTED BY AMBULANCE TO THE HOSPITAL WITH INJURIES EXPECTED TO REQUIRE ADMITTANCE. THE NRC NOTIFICATION WAS THEN MADE SHORTLY THEREAFTER AT 1:24 PM.
2026-06-30 10:38 | NO | NO | NO | 20220054 | 36918 | 2022-07-29 12:17 | ORIGINAL FINAL | 18408 | DOMINION ENERGY SOUTH CAROLINA, INC. | 601 TAYLOR ROAD | CAYCE | SC | 29033 | 2022-07-07 16:00 | EASTERN | YES | 2022 | 4920 AUGUSTA RD | LEXINGTON | LEXINGTON | SC | 29073 | 33.9787 | -81.1941 | YES | [5 empty] | YES |  |  | 2022-07-07 18:03 | 1340874 | 1340979 | NATURAL GAS |  | 2451 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-07-07 15:30 | YES | OPERATOR | 2022-07-07 18:03 | 2022-07-07 15:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 3 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 12872 | 13685.4681967213062 | 9356 | 9947.2685245901601 | 189 | 200.944180327868775 | ADMINISTRATIVE | 12.38 | 30343 | 21421.186317321688500727802037845705968 | 0 | 0 | 52760 | 27124.0174544825483571906841339155749636 | 45254.867218961023575727802037845705968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 48 | 60 | 192.621 M | 2000-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ACTIONS WERE NOT REQUIRED IN THE IDENTIFICATION OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 2207050401 |  |  | CONTRACT LOCATOR | YES | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | MARK NOAH | MANAGER - COMPLIANCE AND INTEGRITY | mark.noah@dominionenergy.com | 704-810-3224 |  | ASHLEY FORTE | ashley.forte@dominionenergy.com | 803-217-6105 | CYNTHIA OSTRANDER | DIRECTOR - GAS OPERATIONS | 803-217-9245 | cynthia.ostrander@dominionenergy.com | ON JULY 7, 2022, AT APPROXIMATELY 3:30 PM, DOMINION ENERGY SOUTH CAROLINA (DESC) RESPONDED TO A BROKEN GAS MAIN NEAR THE INTERSECTION OF I-20 AND US-1 (AUGUSTA RD), IN LEXINGTON, SC. SHORTLY AFTER THE DESC FIRST RESPONDER ARRIVED, THE FIRE DEPARTMENT ARRIVED AND TOOK CONTROL OF THE AREA. THE THIRD PARTY EXCAVATOR, A SUBCONTRACTOR OF THE COMPANY DOING WORK ON THE INTERSTATE, HAD GOUGED THE 6-IN STEEL, MEDIUM PRESSURE MAIN. THE EXCAVATOR DID NOT HAVE A CLEAR LOCATE TICKET. IN ADDITION, THE EXCAVATOR STATED THEY ASSUMED THE MAIN WAS ABANDONED. THE CONTRACTOR HAD SPOTTED THE MAIN AND FULLY EXPOSED IT BEFORE PROCEEDING TO PULL IT OUT OF THE GROUND. A NEARBY VALVE WAS CLOSED TO REDUCE THE LEAK RATE, THOUGH THE LINE STILL LEAKED AS IT WAS TWO-WAY FED. THE LEAK WAS STOPPED BY INSTALLING A STOPPER FITTING AT APPROXIMATELY 11:30 PM. THE DAMAGED PORTION OF PIPE WAS ALREADY SCHEDULED TO BE ABANDONED AT A LATER DATE. AFTER THE LEAK WAS STOPPED AND REPAIRS WERE MADE ON JULY 8, THIS SECTION OF PIPELINE WAS ABANDONED. DUE TO THE LOCATION OF THE DAMAGE, AND THE AMOUNT OF GAS THAT WAS ESCAPING THE DECISION WAS MADE TO SHUT DOWN AUGUSTA RD AND I-20 (BOTH DIRECTIONS OF TRAFFIC). THE INTERSTATE WAS SHUT DOWN DUE TO CARS DRIVING BY AND SPREADING THE PLUME OF GAS. GAS BLEW FOR APPROXIMATELY 8 HOURS AND THE INTERSTATE WAS SHUT DOWN FOR APPROXIMATELY 7 HOURS. DESC MANAGEMENT DECIDED TO MAKE A PHMSA NOTIFICATION DUE TO THE CONCERN THAT OUR ESTIMATED LOST GAS WOULD EXCEED 3,000 MCF AND THAT THIS EVENT WOULD BE CONSIDERED SIGNIFICANT IN NATURE. THOUGH THIS THRESHOLD WAS NOT EXCEEDED, THE INCIDENT WAS SIGNIFICANT IN THE JUDGMENT OF DESC, BECAUSE OF THE DURATION OF STOPPING TRAFFIC FLOW ON A MAJOR ARTERY AND SIGNIFICANT GOVERNMENT AND MEDIA ATTENTION. NOTE: E.3.B DATE MAOP ESTABLISHED IS ESTIMATED AS JAN 1, 2000. DECADE OF INSTALLATION IS KNOWN, BUT NOT EXACT DATE OF THE PIPELINE TEST. LDF: 517493
2026-06-30 10:38 | YES | NO | NO | 20220055 | 39865 | 2022-07-29 13:42 | SUPPLEMENTAL FINAL | 12876 | DOMINION ENERGY UTAH/WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2022-07-03 12:05 | MOUNTAIN | YES | 2022 | 2126 S CREEKSIDE DR | WELLSVILLE | CACHE | UT | 84339 | 41.6944 | -111.8696 |  |  |  | YES | [5 empty] | 2022-07-03 14:16 | 1340511 | 1340630 | NATURAL GAS |  | 152.3 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-07-03 12:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 152.3 | NO | 0 | 2022-07-03 12:05 |  |  |  | 2022-07-03 12:20 | 2022-07-03 13:04 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2021 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | YES | NO | NO |  |  |  | OTHER | ALUMINUM METER/REGULATOR | [9 empty] | OTHER | [8 empty] | MELTED METER AND REGULATOR | CLASS 3 LOCATION | 283786 | 301720.34475409824435 | 1950 | 2073.23360655737625 | 0 | 0 | 0 | 0 |  | 8.045 | 1225 | 864.810771470160116448326055312954876274 | 0 | 0 | 286961 | 124062.6510778629337105094614264919941776 | 304658.3891321257807164483260553129548763 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 43 | 43 | 60 | 192.619(A)(2) | 2021-03-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.1 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [143 empty] | YES | [24 empty] | STEVE BURSETT | SUPERVISOR GAS OPERATIONS | steve.bursett@dominionenergy.com | 801-548-7520 |  | STEVE BURSETT | steve.bursett@dominionenergy.com | 801-548-7520 | RYAN JAMISON | MANAGER GAS OPERATIONS | 801-574-0111 | ryan.jamision@dominionenergy.com | ON JULY 3, 2022, DOMINION ENERGY UTAH (DEU) WAS NOTIFIED OF A HOUSE FIRE AT 2126 CREEKSIDE DRIVE, WELLSVILLE, UTAH. DEU SENT A TECHNICIAN TO THE SITE. UPON ARRIVAL, THE TECHNICIAN NOTED THE METER WAS DAMAGED AND MELTED DUE TO THE FIRE. THE SERVICE LINE WAS EXPOSED BY EXCAVATION AND SQUEEZE BARS WERE USED TO STOP THE FLOW OF GAS TO THE METER. THE FIRE DEPARTMENT NOTED THAT THE DAMAGE TO THE STRUCTURE WAS ESTIMATED TO BE $283,786. DEU CREWS LEAK SCREENED THE AREA WITH NO LEAKS FOUND. DEU RETIRED THE SERVICE LINE TO THE RESIDENCE. THIS EVENT IS BELIEVED TO BE A FIRE FIRST EVENT. THE EXAMINATIONS CONDUCTED BY DEU'S RETAINED CONSULTANT S-E-A, DESCRIBED BELOW, SUBSTANTIATE OUR DETERMINATION. S-E-A SITE INVESTIGATION: ONSITE INVESTIGATION CONDUCTED AUGUST 16, 2022 S-E-A OBSERVED FIRE PATTERNS ON THE EXTERIOR OF THE STRUCTURE INDICATED THAT THE FIRE INITIATED NEAR, OR ON-GRADE, ON THE SOUTHEAST CORNER OF THE RESIDENCE. FIRE THEN SPREAD VERTICALLY AND TO THE WEST, ENTERING THE ATTIC NEAR THE CENTER OF THE RESIDENCE. THE RESIDENCE WAS ENCIRCLED BY LANDSCAPING WOOD CHIPS, WHICH EXTENDED APPROXIMATELY 3 FEET FROM THE EXTERIOR WALLS OF THE RESIDENCE. THE REMAINING PORTIONS OF THE DOMINION ENERGY EQUIPMENT WERE THE STEEL PIPE STUB UP TO THE METER SET AND THE DISCHARGE PIPING FROM THE METER SET. THE REGULATOR AND FLOW METER THEMSELVES HAD MELTED DURING THE FIRE AND DOMINION ENERGY EMPLOYEES FOUND THE REMAINS POOLED ON THE GROUND SHORTLY AFTER THE FIRE. BASED ON S-E-A'S EXAMINATION OF ALL AVAILABLE EVIDENCE, THE ONLY HEAT SOURCE FOR IGNITION OF THE FIRE WAS AN IMPROPERLY DISPOSED OF CIGARETTE. THE NATURAL GAS CONTAINED WITHIN THE ASSOCIATED UNDERGROUND SERVICE LATERAL, STUB-UP PIPING, AND METER SET CANNOT SELF-IGNITE, AND NO OTHER COMPETENT HEAT SOURCE WAS IDENTIFIED THAT MAY HAVE ORIGINATED FROM THE DOMINION ENERGY SUPPLIED EQUIPMENT. DOMINION ENERGY SERVICE LINE PRESSURE TEST PRESSURE TEST CONDUCTED AUGUST 19, 2022 FOLLOWING THE ONSITE INVESTIGATION, A PRESSURE TEST OF THE AFFECTED SERVICE LINE WAS CONDUCTED. AN AIR TEST WAS PERFORMED WITH THE RISER INCLUDED. PRESSURE WAS UNABLE TO BUILD AS THE AIR LEAKED CONTINUOUSLY FROM THE RISER. THE RISER WAS THEN EXCAVATED, REMOVED, AND BAGGED FOR EVIDENCE USING THE CHAIN OF CUSTODY PROCEDURE. THE SERVICE LINE WAS CAPPED AT THE POINT THE RISER WAS CUT FROM. AIR WAS INTRODUCED AT A PRESSURE OF 45 PSIG. THE SERVICE LINE WAS TESTED AT 45 PSIG FOR 15 MINUTES WITH NO PRESSURE LOSS INDICATING NO LEAKS ON THE SERVICE LINE. S-E-A LABORATORY EXAMINATION OF RISER PIPE - LEAK TEST CONDUCTED FEBRUARY 24, 2023: S-E-A DETERMINED THAT THE SOURCE OF THE LEAK WAS FROM MELTED POLYETHYLENE PIPING UPSTREAM OF THE STEEL BARB FITTING THAT WAS SUBJECTED TO HEAT FROM THE FIRE. AFTER THE BREACH, THE GAS ESCAPED THROUGH THE FLEXIBLE STEEL SLEEVE. THERE IS NO AVAILABLE EVIDENCE TO SUPPORT AN OPINION THAT A TEAR IN THE CORROSION PROTECTION, PRIOR TO THE FIRE, WAS CAUSAL TO THIS INCIDENT. - DESTRUCTIVE TEST CONDUCTED JUNE 13, 2023: S-E-A CONCLUDED THAT THE POLYETHYLENE MATERIAL DEPOSITED IN THE AREA PAST THE BARB FITTING RESULTED FROM THE POLYETHYLENE MELTING DURING THE FIRE AND THE CONTINUOUS GAS PRESSURE CAUSED THE SOFT POLYETHYLENE TO FLOW THROUGH THE BARB FITTING. UPON SECTIONING THE PORTION OF RISER PIPE NEAR THE BARB FITTING, EVIDENCE SHOWED THAT THE BARB FITTING WAS FULLY INSERTED INTO THE POLYETHYLENE PIPE, MEANING IT WAS CORRECTLY INSTALLED DURING THE MANUFACTURING PROCESS. AFTER COMPLETION OF BOTH LABORATORY EXAMINATIONS, THERE IS NO EVIDENCE AVAILABLE TO S-E-A TO SUPPORT AN OPINION THAT THE RISER PIPE WAS CAUSAL TO THE INCIDENT.
2026-06-30 10:38 | NO | YES | YES | 20220056 | 36988 | 2022-08-18 11:36 | ORIGINAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2022-07-19 18:00 | CENTRAL | NO | 2022 | 401 MORGAN AVENUE | CHESTERTON | PORTER | IN | 46304 | 41.609 | -87.0563 | [6 empty] | YES |  |  | 2022-07-19 18:19 | 1341980 | 1342191 | NATURAL GAS |  | 2.89 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2022-07-19 09:45 | NO |  |  | 2022-07-19 09:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1928 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | SERVICE TEE | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.555 | 28 | 19.76710334788937409024745269286754002911 | 0 | 0 | 28 | 16.09898107714701601164483260553129548763 | 19.76710334788937409024745269286754002911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 60 | 192.619(A)(3) | 1970-12-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ISSUE DID NOT INVOLVE PRESSURE REGULATION. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  |  | YES | THE INTERNAL COMPONENTS OF THE SERVICE TEE, WHICH WAS INSTALLED IN 1928, WERE NOT PRESENT. WHEN THE CAP ON THE TEE WAS REMOVED TO ACCESS THE COMPONENTS THAT WOULD SHUT OFF THE FLOW OF GAS TO THE SERVICE, THE GAS ESCAPED UNEXPECTEDLY AND CUT THE EMPLOYEES LEATHER-GLOVED HAND. | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [44 empty] | YES |  |  |  |  | RICK SMITH | MGR PIPELINE SAFETY AND COMPLIANCE | ricksmith@nisource.com | 219-252-4057 |  | RIC SMITH | ricksmith@nisource.com | 219-252-4057 | RICK SMITH | MGR PIPELINE SAFETY AND COMPLIANCE | 219-252-4057 | ricksmith@nisource.com | THE INTERNAL COMPONENTS OF THE SERVICE TEE, WHICH WAS INSTALLED IN 1928, WERE NOT PRESENT. WHEN THE CAP ON THE TEE WAS REMOVED TO ACCESS THE COMPONENTS THAT WOULD SHUT OFF THE FLOW OF GAS TO THE SERVICE, THE GAS ESCAPED UNEXPECTEDLY AND CUT THE EMPLOYEES LEATHER-GLOVED HAND. THE EMPLOYEE RECEIVED A SMALL LACERATION, BUT WAS CONCERNED IT MAY HAVE HAD GAS BLOWN INTO THE LACERATION UNDER THE SKIN. PER OUR PROCEDURES, THE EMPLOYEE WENT TO THE EMERGENCY ROOM TO HAVE THE INJURY LOOKED AT. THERE WAS NO DOCTOR PRESENT, SO HE WAS ADMITTED BASED ON THE ADMITTING NURSES RECOMMENDATION. THE EMPLOYEE RECEIVED BASIC FIRST AID, BUT WAS NOT SEEN BY A DOCTOR FOR 33HRS. UPON SEEING THE PHYSICIAN, IT WAS INDICATED THERE WAS NO EXPOSURE AND THAT THE EMPLOYEE SHOULD NOT HAVE BEEN ADMITTED. THE EMPLOYEE WAS RELEASED AND RETURNED TO WORK THE FOLLOWING DAY. THIS IS THE FINAL REPORT.
2026-06-30 10:38 | NO | YES | NO | 20220057 | 37046 | 2022-08-29 19:12 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2022-08-04 02:29 | PACIFIC | YES | 2022 | 667 NORTH F STREET | UPLAND | SAN BERNARDINO | CA | 91786 | 34.1016 | -117.6501 | [5 empty] | YES |  |  |  | 2022-08-04 02:29 | 1343499 | 48hr update NRC# 1343678 | NATURAL GAS |  | 8.7 | 426.9 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-07-30 09:59 | NO |  |  | 2022-07-30 10:43 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 | YES | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | STUB | 1930 | UNKNOWN | [7 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 14580 | 15501.4081967213055 | 344432 | 366198.9731147539572 | 0 | 0 |  | 6.3303 | 55 | 38.82823871906841339155749636098981077147 | 2702 | 1907.525473071324599708879184861717612809 | 361769 | 156578.306147898977889432314410480349345 | 383646.7350232656557131004366812227074236 | 6 | 0 | 130 | 0 | 0 | 130 | 6 | 45 | 45 | 60 | 192.621 M | 1930-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A WATER INTRUSION INCIDENT | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | WATER INTRUSION CAUSED BY A WATER MAIN LEAK | [136 empty] | YES | [17 empty] | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | jjcervantes@socalgas.com | 310-970-4854 | 909-335-7895 | JAMES CERVANTES | jjcervantes@socalgas.com | 310-970-4854 | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 310-970-4854 | jjcervantes@socalgas.com | ON 07/30/2022 SOCALGAS CREWS RESPONDED TO AN UNDER PRESSURE CONDITION AT 220 A STREET, UPLAND, SAN BERNARDINO. ON INVESTIGATION COMPLETED TO DATE REGARDING THE UNDER PRESSURE CONDITION, SOCALGAS IDENTIFIED A LEAKING 3" WATER MAIN AT THE CROSS POINT OF A 3/4" STEEL GAS STUB THAT AFFECTED MULTIPLE SERVICES AND THE MAIN. THIS INCIDENT WAS REPORTED TO THE CPUC DUE TO UNDER-PRESSURE. THIS WAS REPORTED TO THE DOT DUE TO GAS RELEASE AND DAMAGE EXCEEDING $129,300.
2026-06-30 10:38 | NO | YES | NO | 20220058 | 37803 | 2022-09-02 13:00 | SUPPLEMENTAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2022-07-16 04:00 | EASTERN | YES | 2022 | 55 RT 24 | CHESTER TOWNSHIP | MORRIS | NJ | 07930 | 40.7793 | -74.7203 |  |  |  | YES | [5 empty] | 2022-08-15 04:03 | 1344582 | 1344584 | NATURAL GAS |  | 514 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-07-16 04:00 | OPERATOR/CONTRACTOR |  | 514 | NO | 0 | 2022-07-16 04:00 |  |  |  | 2022-07-16 04:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1983 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 225000 | 239219.262295081875 | 25000 | 26579.918032786875 | 0 | 0 |  | 5.31 | 2729 | 1926.586608442503639010189228529839883552 | 0 | 0 | 252729 | 109499.4035602644359534206695778748180495 | 267725.7669363112536390101892285298398836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 192.619(A)(1) | 1983-08-11 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | A JCP&L POWER LINE CAME DOWN 2 MILES AWAY FROM THE PSE&G POINT OF IGNITION. TEN OTHER IGNITIONS OF VARIOUS TYPES (NO OTHER GAS) OCCURRED IN THE 2 MILE AFFECTED ZONE. THE CAUSE FOR THE POWER LINE DROP HAS NEVER BEEN DETERMINED. | [154 empty] | ROGER GUNNELS | PRINCIPAL REGULATORY SPECIALIST | roger.gunnels@pseg.com | 9739871589 |  | ROGER GUNNELS | roger.gunnels@pseg.com | 9739871589 | CHRIS LAROSSA | MANAGER REGULATORY POLICY AND PROCEDURE | 973-896-7617 | christopher.larossa@pseg.com | ON SATURDAY JULY 16TH PSE&G RECEIVED NOTIFICATION THAT A DOWNED JCP&L ELECTRIC WIRE THAT FOUND ITS WAY TO NEARBY METAL GUARD RAIL AND RESULTED IN THE IGNITION OF A 6 INCH 60 LB. STEEL MAIN LOCATED AT 55 RT 24 IN CHESTER TOWNSHIP. THE LOCATION OF THE IGNITION INVOLVES A BRIDGE. THE MAIN WAS THROTTLED AND TEMPORARY BYPASS WAS INSTALLED TO CONTINUE TO SERVICE CUSTOMERS. THE LOCATION OF THE DOWNED WIRE WAS 2 MILES AWAY FROM THE IGNITION LOCATION. THE CAUSE FOR HOW THE WIRE CAME INTO CONTACT WITH THE GUARD RAIL IS UNKNOWN AT THIS TIME. THERE ARE NO INDICATIONS AT THIS TIME THAT ANY TYPE OF DAMAGE WAS INVOLVED. A PERMANENT REPAIR PLAN IS BEING DEVELOPED AT THIS TIME.
2026-06-30 10:38 | NO | YES | NO | 20220059 | 37563 | 2022-09-02 13:54 | SUPPLEMENTAL FINAL | 21349 | VIRGINIA NATURAL GAS | 544 S. INDEPENDENCE BLVD | VIRGINIA BEACH | VA | 23452 | 2022-09-01 09:50 | EASTERN | YES | 2022 | 1601 GREEN MOUNTAIN PARKWAY | WILLIAMSBURG | JAMES CITY | VA | 23185 | 37.2083 | -76.5973 | [7 empty] | YES | DRESSER REPAIR SLEEVE | 2022-09-01 09:59 | 1346111 |  | NATURAL GAS |  | 1557 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-08-31 11:12 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-08-31 11:31 | 2022-08-31 11:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 56 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1960 | UNKNOWN |  |  |  |  | 16 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 75000 | 79739.754098360625 | 50000 | 53159.83606557375 | 0 | 0 |  | 6.9676 | 10849 | 7659.046579330422125181950509461426491994 | 0 | 0 | 135849 | 60202.9441382108205967976710334788937409 | 140558.636743264797125181950509461426492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 137 | 150 | 192.619(A)(4) | 1960-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS NOT LARGE ENOUGH TO BE IDENTIFIED BY THE SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | B224300196 |  |  | CONTRACT LOCATOR | NO | NO |  | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [143 empty] | YES | [26 empty] | MICHAEL SMITH | DIRECTOR- COMPLIANCE AND SYSTEM INTEGRITY | mlsmi@southernco.com | 5408943733 |  | MICHAEL SMITH | mlsmi@southernco.com | 5408943733 | MICHAEL SMITH | DIRECTOR- COMPLIANCE AND SYSTEM INTEGRITY | 5408943733 | mlsmi@southernco.com | VIRGINIA NATURAL GAS (COMPANY) WAS MADE AWARE OF A LEAK ON AUGUST 31, 2022, NEAR THE INTERSECTION OF POCAHONTAS TRAIL AND GREEN MOUNT PARKWAY AT 1601 GREEN MOUNT PARKWAY IN WILLIAMSBURG, VA. SHIRLEY CONTRACTING COMPANY (CONTRACTOR) WAS CONSTRUCTING A NEW ROAD AND SHOULDER FOR VDOT FROM THE INTERSECTION OF POCAHONTAS TRAIL AND GREEN MOUNT PARKWAY FOR A DISTANCE OF APPROXIMATELY 900 FEET EAST OF THAT INTERSECTION. THE CONTRACTOR WAS EXCAVATING DIRECTLY ABOVE THE COMPANY'S 16-INCH STEEL PIPELINE WHEN IT SCRAPED THE PIPELINE CAUSING COATING DAMAGE, DENTING, AND RIPPING OFF AN EXISTING TAP CAUSING THE LEAK. THE FACILITY WAS MARKED CORRECTLY, BUT PARTS OF THE MARKS WERE DESTROYED BY THE CONTRACTOR DURING CONSTRUCTION. THE CONTRACTOR SHOULD HAVE CONTACTED VA811 TO GENERATE A 3-HOUR TICKET TO REMARK THE FACILITY BEFORE CONTINUING ITS WORK. THE COMPANY WORKED WITH THE LOCAL FIRE DEPARTMENT AND LAW ENFORCEMENT TO SHUT DOWN ROUTE 60 AND REDUCED THE PRESSURE ON THE PIPELINE FROM APPROXIMATELY 150 PSI TO 100 PSI UNTIL REPAIRS COULD BE MADE. THE COMPANY UTILIZED A REPAIR SLEEVE TO REPAIR THE LEAK.
2026-06-30 10:38 | NO | YES | YES | 20220060 | 38223 | 2022-09-17 19:04 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2022-09-15 20:05 | PACIFIC | YES | 2022 | 6500 URSULA PL S. | SEATTLE | KING | WA | 98108 | 47.5459 | -122.3103 | YES | [8 empty] | 2022-09-15 18:47 | 1347398 | 1347652 | NATURAL GAS |  | 0.01 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2022-09-15 14:24 | ALLOWED TO BURN OUT |  | 0.01 | NO | 0 | 2022-09-15 14:24 | NO |  |  | 2022-09-15 14:24 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1956 | UNKNOWN | [7 empty] | OTHER | WELD BETWEEN A FLANGE AND EXISTING RISER | [9 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 115000 | 122267.622950819625 | MEDICAL EXPENSES ONLY, NO DAMAGE TO PSE OR OTHER PROPERTY REQUIRING REPAIR. | 8.94 | 0 | 0 | 0 | 0 | 115000 | 49647.95081967215 | 122267.622950819625 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 135 | 250 | 192.619(A)(3) | 2014-05-17 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | YES | 6 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | UNINTENTIONAL IGNITION WHILE WELDING ON AN OUT OF SERVICE REGULATOR STATION, AND OUR WORKING ASSUMPTION IS THAT IT WAS GAS AND WE ARE TAKING CORRECTIVE ACTIONS ON THAT BASIS. | YES |  |  |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [40 empty] | YES | [8 empty] | JUSTIN WAHLBORG | SR. COMPLIANCE PROGRAM MANAGER | justin.wahlborg@pse.com | 4257661811 |  |  |  |  | ZAKARIA MOHAMED | MANAGER COMPLIANCE | 4252476751 | zakaria.mohamed@pse.com | PUGET SOUND ENERGY (PSE) AND INFRASOURCE (IFS) WERE PERFORMING REPLACEMENT WORK ON A REGULATOR STATION FACILITY. THE FACILITY WAS ISOLATED FROM THE SURROUNDING SYSTEM BY CLOSING THE INLET AND OUTLET VALVES AND HAD BEEN BLOWN DOWN AND PURGED OUT OF SERVICE USING NITROGEN. THE IFS CREW WAS WORKING REBUILDING A STATION REGULATOR RUN BY ON WELDING A FLANGE ONTO AN OPEN PIPE RISER WHEN UNINTENTIONAL IGNITION OCCURRED. TWO CREW MEMBERS WERE TRANSPORTED TO THE HOSPITAL: AN IFS WELD HELPER WAS TREATED IN THE ER AND RELEASED, AND A PSE PRESSURE CONTROL TECHNICIAN WAS ADMITTED TO THE HOSPITAL AT 20:05 FOR BURN TREATMENT. OUR INVESTIGATION WAS INCONCLUSIVE, BUT OUR WORKING ASSUMPTION IS THAT ONE OF THE CLOSED VALVES BYPASSED A SMALL AMOUNT OF GAS. THE CONSTRUCTION PROCEDURE THAT WAS BEING FOLLOWED DURING THE PROJECT CONTAINED SEVERAL ISOLATION AND MONITORING STEPS: - THE VALVES ISOLATING THE WORK AREA FROM THE ACTIVE SYSTEM WERE SUBJECTED TO A "SHUT IN TEST" AND PASSED THE TEST. - THE PIPING IN THE WELD AREA HAD BEEN INERTED USING NITROGEN, BUT THE IGNITION OCCURRED SEVERAL HOURS AFTER INTERTING PROCESS HAD BEEN COMPLETED. - THE CREW WAS MONITORING FOR GAS READS IN THE INERTED PIPE RISERS AS PART OF THE WELDING PROCESS AND CONFIRMED 0% GAS READS. INVESTIGATION AFTER THE INCIDENT FOUND GAS READS ON THE INERTED SIDE OF THE CLOSED STATION OUTLET VALVE. THE VALVE WAS GREASED TO BRING THESE READS TO 0% GAS. AS PART OF THE FOLLOW UP FROM A SAFETY DEPARTMENT LED ROOT CAUSE ANALYSIS, PSE IS REVISING ENERGY CONTROL PROCEDURES TO ADDRESS THE POSSIBILITY THAT GAS MIGHT LEAK BY A CLOSED VALVE. PSE IS ALSO ADDRESSING MANAGEMENT OF CHANGE FOR WRITTEN CONSTRUCTION PROCEDURE UPDATES, SINCE LAST MINUTE CHANGES NEEDED TO BE MADE TO THE PROCEDURE DOCUMENT FOR THE REGULATOR STATION CONSTRUCTION PROJECT BASED ON PIPING CONDITIONS FOUND IN THE FIELD.
2026-06-30 10:38 | NO | YES | NO | 20220061 | 37148 | 2022-09-22 12:57 | ORIGINAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2022-08-24 13:00 | EASTERN | YES | 2022 | I40 & ROCK QUARRY RD | RALEIGH | WAKE | NC | 27610 | 35.7472 | -78.594 | [6 empty] | YES |  |  | 2022-08-24 19:04 | 1345455 | 1345507 | NATURAL GAS |  | 1886 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-08-24 13:05 | NO |  |  | 2022-08-24 13:31 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 120 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2020 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 210000 | 223271.31147540975 | 15000 | 15947.950819672125 | 0 | 0 |  | 5.75 | 10845 | 7656.222707423580786026200873362445414847 | 0 | 0 | 235845 | 103372.7754313122281659388646288209606987 | 246875.4850025054557860262008733624454148 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 55 | 55 | 60 | 192.621 M | 2020-03-18 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA WAS NOT REQUIRED TO IDENTIFY THE FAILURE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | YES | INTERSTATE HIGHWAY | [12 empty] | CONTRACTOR | AUGER | FENCING | NO | [5 empty] | YES | 10 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | MARK NOAH | MANAGER - INTEGRITY AND COMPLIANCE | mark.noah@dominionenergy.com | 704-810-3224 |  | CURTIS RICE | curtis.rice@dominionenergy.com | 919-836-2448 | SCOTT SWINDLER | DIRECTOR - GAS OPERATIONS | 704-810-3230 | scott.swindler@dominionenergy.com | ON AUGUST 24TH, 2022, AT APPROXIMATELY 1:00 PM, DOMINION ENERGY NORTH CAROLINA (DENC) RESPONDED TO A RUPTURED GAS MAIN NEAR THE INTERSECTION OF I-40 AND ROCK QUARRY ROAD, IN RALEIGH, NC. WHEN THE DENC FIRST RESPONDER ARRIVED, EMERGENCY RESPONDERS HAD ALREADY TAKEN CONTROL OF THE AREA. THE THIRD-PARTY EXCAVATOR, A SUBCONTRACTOR OF THE COMPANY DOING WORK ON THE INTERSTATE, HAD PIERCED THE 12-IN STEEL, DISTRIBUTION PRESSURE MAIN WHILE INSTALLING SOUND BARRIER PANELS ALONG THE INTERSTATE ROW. THE EXCAVATOR DID NOT HAVE A LOCATE TICKET. THE CONTRACTOR DID CALL IN A LOCATE REQUEST AFTER THE MAIN HAD BEEN DAMAGED. THE LEAK WAS STOPPED BY INSTALLING STOPPER FITTINGS AT APPROXIMATELY 12:30 AM. GAS BLEW FOR APPROXIMATELY 12 HOURS. DENC MANAGEMENT DECIDED TO MAKE A PHMSA NOTIFICATION DUE TO THE CONCERN THAT OUR REPAIR COSTS WOULD EXCEED $129,300 AND THAT THIS EVENT WOULD BE CONSIDERED SIGNIFICANT IN NATURE. REPAIRS HAVE BEEN COMPLETED AND THE LINE IS BACK IN SERVICE.
2026-06-30 10:38 | NO | YES | NO | 20220062 | 37441 | 2022-09-30 09:59 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2022-09-01 14:12 | EASTERN | NO | 2022 | 120 DEEDS DRIVE | DOVER | TUSCARAWAS | OH | 44622 | 40.5538 | -81.4983 | YES | [8 empty] | 2022-09-01 16:05 | 1346162 |  | NATURAL GAS |  | 13.208 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-09-01 14:12 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 13.2 | NO | 2 | 2022-09-01 14:12 | NO |  |  | 2022-09-01 14:14 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1989 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | DRISCO | PLASTIC |  |  |  |  | OTHER | DRISCO 8000 |  |  | UNKNOWN |  | MECHANICAL PUNCTURE | 2 | 1.3 | [7 empty] | CLASS 3 LOCATION | 310000 | 329590.98360655725 | 800 | 850.55737704918 | 5000 | 5315.983606557375 | 0 | 0 |  | 10.5828 | 140 | 98.83551673944687045123726346433770014556 | 0 | 0 | 315940 | 136418.0850693202130800582241630276564774 | 335856.3601069032518704512372634643377001 | 6 | 0 | 0 | 1 | 0 | 0 | 8 | 58 | 58 | 80 | 192.619(A)(2) | 1989-04-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | [7 empty] | YES | [6 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | A223704353 | OH811 |  | CONTRACT LOCATOR | YES | YES | 4 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | AMY LAURIE KONCELIK | SUPERVISOR PIPELINE COMPLIANCE | amy.l.koncelik@dominionenergy.com | 13308109842 |  | AMY LAURIE KONCELIK | amy.l.koncelik@dominionenergy.com | 13308109842 | AMY LAURIE KONCELIK | SUPERVISOR PIPELINE COMPLIANCE | 13308109842 | amy.l.koncelik@dominionenergy.com | A SUBCONTRACTOR FOR A THIRD PARTY CONTRACTOR WAS BORING TO INSTALL FIBER OPTIC LINES AND BORED THROUGH OPERATOR'S 4 INCH MAINLINE, WHICH WAS PROPERLY MARKED. THIRD PARTY CONTRACTOR ACKNOWLEDGED THAT THEIR SUB-CONTRACTOR DECIDED TO DO A PORTION OF THE JOB WITHOUT BEING INSTRUCTED TO DO SO AND FAILED TO POTHOLE, WHICH CREATED THIS EXCAVATION DAMAGE.
2026-06-30 10:38 | NO | YES | NO | 20220063 | 37556 | 2022-09-30 15:37 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-09-02 10:59 | EASTERN | YES | 2022 | 1631 N. JEROME ROAD (FARM FIELD WEST OF ADDRESS) | ARCADA TOWNSHIP | GRATIOT | MI | 48847 | 43.3113 | -84.6302 | YES | [8 empty] | 2022-09-02 19:44 | 1346279 | 1346357 | NATURAL GAS |  | 309 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-09-02 10:59 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-09-02 10:59 | 2022-09-02 11:32 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1944 | UNKNOWN |  |  |  |  | 4 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 4 | 12.5 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 250000 | 265799.18032786875 | 372 | 395.5091803278687 | 0 | 0 |  | 8.95 | 2766 | 1952.707423580786026200873362445414847162 | 0 | 0 | 253138 | 109681.27754169951845886462882096069869 | 268147.3969317774047262008733624454148472 | 220 | 18 | 1294 | 0 | 0 | 1294 | 238 | 259 | 259 | 375 | 192.619(C) | 1968-11-08 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | TRENCHER | DRAINAGE | NO | [5 empty] | YES | 30 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON FRIDAY, SEPTEMBER 2, 2022 AT APPROXIMATELY 10:59 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE BY A THIRD-PARTY CONTRACTOR INSTALLING DRAIN TILES IN A FARM FIELD WEST OF 1631 N. JEROME ROAD, ARCADA TOWNSHIP (GRATIOT COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) ARRIVED ONSITE AT APPROXIMATELY 11:32 HOURS AND CONFIRMED A 4-INCH HIGH-PRESSURE PIPELINE FEEDING CONSUMERS ENERGY'S ITHACA REGULATION STATION HAD BEEN DAMAGED RESULTING IN A SEVERED PIPELINE. A DISTRIBUTION CREW ARRIVED ONSITE AT APPROXIMATELY 12:00 HOURS. TO CONTROL THE GAS FLOW, THE GAS MECHANICS CLOSED THE G-VALVE AT REGULATOR STATION #63831 AT 12:00 HOURS TO ISOLATE DOWNSTREAM OF THE DAMAGE TO MAINTAIN SERVICE TO CUSTOMERS. THE H-67 VALVE WAS CLOSED AT 12:20 HOURS TO ISOLATE AND SHUT-OFF GAS AT THE DAMAGE LOCATION. A REQUEST WAS MADE TO LARGE COMMERCIAL AND INDUSTRIAL CUSTOMERS TO REDUCE GAS USAGE IN AN EFFORT TO MAINTAIN THE PRESSURE REQUIRED TO SERVE THE CITY OF ITHACA. DESPITE EFFORTS TO MAINTAIN PRESSURE, A CONTINUED PRESSURE DROP WAS OBSERVED, AND A DECISION WAS MADE AT APPROXIMATELY 15:30 HOURS TO BEGIN SHUTTING OFF METERS FOR THE 1400+ CUSTOMERS SERVED BY THIS FEED. THE DAMAGED SEGMENT OF THE PIPELINE WAS CUT OUT AND REPLACED WITH APPROXIMATELY 62-FEET OF 4-INCH HIGH-PRESSURE PIPELINE. REPAIRS WERE COMPLETED AND GAS SERVICE RESTORED TO THE HIGH PRESSURE PIPELINE ON SEPTEMBER 3, 2022, AT APPROXIMATELY 06:30 HOURS. RESTORATION TO THE MEDIUM PRESSURE PIPELINE WAS COMPLETED AT 15:30 AND SERVICE RESTORATION BEGAN AT 18:00 HOURS.
2026-06-30 10:38 | NO | YES | NO | 20220064 | 37991 | 2022-10-07 13:07 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-09-08 17:52 | EASTERN | YES | 2022 | 1102 LAKE STREET | KALAMAZOO | KALAMAZOO | MI | 49001 | 42.2809 | -85.5665 | [5 empty] | YES |  |  |  | 2022-09-08 21:02 | 1346805 | 1346828 | NATURAL GAS |  | 315 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-09-08 17:52 | ALLOWED TO BURN OUT |  | 315 | NO | 25 | 2022-09-08 17:52 |  |  |  | 2022-09-08 17:58 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 42 | NO | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1991 | UNKNOWN |  |  |  |  | 4 | D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 6.2 | [7 empty] | CLASS 3 LOCATION | 112929 | 120065.742540983560275 | 26190 | 27845.12213114753025 | 165 | 175.427459016393375 | 0 | 0 |  | 8.95 | 2819 | 1990.12372634643377001455604075691411936 | 0 | 0 | 142103 | 61752.6935638437720877438136826783114993 | 150076.4158574939176700145560407569141194 | 11 | 0 | 86 | 2 | 0 | 86 | 11 | 54 | 54 | 60 | 192.619(A)(2) | 1991-05-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 6 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | NATURAL GAS | YES | 2022082304088 |  |  | CONTRACT LOCATOR | NO | YES | 11 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON SEPTEMBER 8, 2022, AT APPROXIMATELY 17:52 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE NEAR 1102 LAKE STREET, KALAMAZOO (KALAMAZOO COUNTY), MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 17:58 HOURS. THE GSW CONFIRMED A 4-INCH MEDIUM-PRESSURE PLASTIC PIPELINE WAS DAMAGED BY A CONSUMERS ENERGY (2ND-PARTY) CONTRACTOR. DURING THE BORE SHOT PULL BACK, THE BORE REAMER DAMAGED THE PIPELINE CAUSING GAS TO BE RELEASED AND A SUBSEQUENT IGNITION. THE PREVIOUS NIGHT A CANDLELIGHT VIGIL WAS HELD NEAR THE DAMAGE LOCATION, CANDLES REMAINING AT THE SIGHT ARE THOUGHT TO BE THE IGNITION SOURCE. THE POLICE AND FIRE DEPARTMENT WERE ONSITE AND RESIDENTIAL AND COMMERCIAL STRUCTURES WITHIN ONE BLOCK IN ALL DIRECTIONS WERE EVACUATED AND ELECTRIC SERVICE DISCONTINUED. SEVERAL CONTRACT EMPLOYEES WORKING ON BEHALF OF THE OPERATOR SUSTAINED MINOR BURNS AND RECEIVED MEDICAL TREATMENT BUT OVERNIGHT HOSPITALIZATION WAS NOT REQUIRED. POST-ACCIDENT DRUG AND ALCOHOL TESTING WAS PERFORMED FOR ALL CONTRACT EMPLOYEES WORKING ON THIS PROJECT. A DISTRIBUTION CREW ARRIVED ONSITE AT APPROXIMATELY 18:40 HOURS AND SQUEEZED THE PIPELINE AT A REMOTE LOCATION WEST OF MILL STREET STOPPING GAS FROM BLOWING. ONCE THE GAS WAS CONTAINED, THE FIRE WAS ALLOWED TO EXTINGUISH BEFORE ASSESSING DAMAGE AND MAKING REPAIRS. IN ADDITION TO OPERATOR EMERGENCY RESPONSE AND REPAIRS COSTS, SIGNAGE, TRAFFIC CONTROL AND LIGHTING AND A NEARBY AUTOMOBILE WAS DAMAGED AND WILL REQUIRE REPLACEMENT AND/OR REPAIR. THE DAMAGED SEGMENT OF THE PIPELINE WAS CUT OUT AND REPLACED WITH APPROXIMATELY 4-FEET OF 4-INCH MEDIUM-PRESSURE PLASTIC PIPE. REPAIRS WERE COMPLETED AND GAS SERVICE WAS RESTORED ON SEPTEMBER 9, 2022, AT APPROXIMATELY 04:30 HOURS. SERVICE RESTORATION TO IMPACTED CUSTOMERS BEGAN ON SEPTEMBER 9, 2022, AT APPROXIMATELY 15:30 HOURS. FURTHER INCIDENT INVESTIGATION DETERMINE THE THE CONTRACTOR PERFORMING WORK ON BEHALF OF CONSUMERS ENERGY AND RESPONSIBLE FOR LOCATING AND STAKING THE NATURAL GAS PIPELINE FAILED TO PROPERLY IDENTIFY AND MARK THE PIPELINE DOCUMENTED ON THE CONSTRUCTION PRINT. THE FAILURE RESULTED IN THE CREW UNKNOWINGLY BORING NEAR AN UNMARKED GAS FACILITY CAUSING A RELEASE OF GAS AND SUBSEQUENT IGNITION.
2026-06-30 10:38 | NO | YES | NO | 20220065 | 37666 | 2022-10-07 15:12 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-09-09 11:23 | EASTERN | YES | 2022 | HALL ROAD W/AVON LANE | CLINTON TOWNSHIP | MACOMB | MI | 48036 | 42.6299 | -82.8645 | [6 empty] | YES |  |  | 2022-09-09 20:03 | 1346895 |  | NATURAL GAS |  | 6068 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 12 | 2022-09-09 11:23 | YES | OPERATOR | 2022-09-09 13:15 | 2022-09-09 11:51 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 42 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1953 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 1.2 | 18.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 68869 | 73221.294999999971775 | 183 | 194.564999999999925 | 0 | 0 |  | 8.95 | 54309 | 38340.4148471615720524017467248908296943 | 0 | 0 | 123361 | 61036.9186899563431977292576419213973799 | 111756.2748471615437524017467248908296943 | 13 | 0 | 7 | 0 | 0 | 7 | 13 | 329 | 329 | 400 | 192.619(A)(2) | 1994-10-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 2022080903891 |  |  | CONTRACT LOCATOR | YES | YES | 24 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON SEPTEMBER 9, 2022, AT APPROXIMATELY 11:23 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE ON HALL ROAD (WEST OF AVON LANE), CLINTON TOWNSHIP (MACOMB COUNTY), MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 11:51 HOURS. THE GSW CONFIRMED THE DAMAGE WHICH WAS LATER DETERMINED TO BE A 2-INCH STUB (OFF A 6-INCH HIGH-PRESSURE PIPELINE) STRUCK BY A THIRD-PARTY CONTRACTOR INSTALLING DRAIN TILES. A DISTRIBUTION CREW ARRIVED ONSITE AT APPROXIMATELY 12:09 HOURS AND PROCEEDED TO EXCAVATE TWO REMOTE HOLES TO THE EAST AND WEST OF THE DAMAGE LOCATION. WHILE ATTEMPTING TO SQUEEZE THE PIPELINE ON THE WEST SIDE OF THE DAMAGE, THE PIPELINE CRACKED AND REQUIRED EXCAVATION AT A THIRD LOCATION. A MUELLER CONTROL FITTING WAS INSTALLED WEST OF THE DAMAGE TO CONTAIN THE BLOWING GAS. THE PIPELINE WAS A ONE-WAY FEED AND RESULTED IN A LOSS OF SERVICE TO 20 CUSTOMERS. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE INCIDENT. THE DAMAGED SEGMENT OF THE PIPELINE WAS CUT OUT AND REPLACED WITH APPROXIMATELY 6-FEET OF 6-INCH HIGH-PRESSURE PIPELINE. REPAIRS WERE COMPLETED AND GAS SERVICE WAS RESTORED ON SEPTEMBER 10, 2022, AT APPROXIMATELY 11:35 HOURS. SERVICE RESTORATION TO IMPACTED CUSTOMERS BEGAN AFTER REPAIRS TO THE PIPELINE WERE COMPLETED. AN INCIDENT INVESTIGATION DETERMINED THE A 2" NATURAL GAS STUB WAS DOCUMENTED ON THE RECORD BUT WAS NOT MARKED BY THE STAKING EMPLOYEE RESULTING IN A NATURAL GAS PIPELINE DAMAGE.
2026-06-30 10:38 | YES | NO | NO | 20220066 | 37623 | 2022-10-19 11:56 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2022-09-28 14:05 | EASTERN | YES | 2022 | 5409 INNISBROOKE PLACE | GREENWOOD | JOHNSON | IN | 46142 | 39.6189 | -86.2052 | [5 empty] | YES |  |  |  | 2022-09-28 15:22 | 1348530 | 1348695 | NATURAL GAS |  | 22.08 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-09-28 14:05 | OTHER | FIRE EXTINGUISHED BY OPERATOR SQUEEZING OFF THE GAS SERVICE LINE. | 22.08 | NO | 1 | 2022-09-28 14:24 | YES | OPERATOR | 2022-09-28 14:31 | 2022-09-28 14:23 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 28 | YES | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1992 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 1 |  | CLASS 3 LOCATION | 400000 | 425278.68852459 | 1381 | 1468.274672131146975 | 2500 | 2657.9918032786875 | 0 | 0 |  | 6.4311 | 142 | 100.247452692867540029112081513828238719 | 0 | 0 | 404023 | 174445.6798326055975054876273653566229985 | 429505.2024526927020150291120815138282387 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 54 | 54 | 60 | 192.619(A)(2) | 1992-11-04 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 5.2 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [150 empty] | YES | [16 empty] | YES | RANDA POWERS | LEAD OPERATIONS SPECIALIST - GAS COMPLIANCE | randa.powers@centerpointenergy.com | 317-997-3939 |  | RANDA POWERS | lead operations specialist - gas compliance | 317-997-3939 | SHERRI BELL | MANAGER PIPELINE SAFETY AND COMPLIANCE | 812-4914806 | sherri.bell@centerpointenergy.com | A CREW FROM JOHNSON COUNTY REMC WAS REPAIRING A BURIED 3 PHASE ELECTRIC SERVICE 4' FROM THE HOME LOCATED AT 5409 INNISBROOKE PL, GREENWOOD IN WHEN THE GAS SERVICE CAUGHT ON FIRE, CATCHING THE HOME ON FIRE. THE REMC CREW HAD BEEN USING A BLOW TORCH TO HEAT SHRINK THE REPAIR. THE 3-PHASE ELECTRIC REPAIR WAS APPROXIMATELY 7 INCHES BELOW THE GAS SERVICE LINE. REMC CREW STATED THEY HAD SPOTTED THE GAS SERVICE, WHICH WAS CORRECTLY LOCATED, USED A SHOVEL TO PROTECT THE PLASTIC GAS LINE BEFORE INTRODUCING FLAME NEAR IT. WHILE USING THE FLAME TO SHRINK WRAP THE REPAIR, THERE WAS AN IGNITION OF THE GAS LINE.
2026-06-30 10:38 | NO | YES | YES | 20220068 | 38008 | 2022-10-26 16:13 | SUPPLEMENTAL | 40247 | TEXAS REPUBLIC UTILITY, LLC | 19926 KEENAN CUT OFF RD. | MONTGOMERY | TX | 77316 | 2022-10-03 12:30 | CENTRAL | YES | 2022 | 14020 GROVER CREEK DR | CONROE | MONTGOMERY | TX | 77303 | 30.3531 | -95.3622 |  | YES |  |  |  | YES |  |  |  | 2022-10-04 17:27 | 1349031 | 1349815 (48 Hour Update) | NATURAL GAS |  | 2 | 0 | NO | [5 empty] | 0 | YES | 2 | 0 | 0 | 0 | 0 | 2 | YES | 2022-10-03 12:30 | OPERATOR/CONTRACTOR |  | 2 | NO | 0 | 2022-10-03 12:30 | YES | OPERATOR | 2022-10-03 12:33 | 2022-10-03 12:33 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE VALVE |  | 2022 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 4" |  |  | 2406 | LEAK |  |  | OTHER | ELECTROFUSION JOINT | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 5000 | 5315.983606557375 | 0 | 0 | 0 | 0 |  | 11 | 22 | 15.53129548762736535662299854439592430859 | 0 | 0 | 5022 | 2171.255756794808369723435225618631732169 | 5331.514902045002365356622998544395924309 | 0 | 0 | 100 | 0 | 0 | 50 | 0 | 40 | 40 | 70 | 192.619(A)(2) | 2022-01-03 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | SADDLE, ELECTROFUSION |  | 2022 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [8 empty] | YES |  |  |  | OTHER | SADDLE ELECTROFUSION JOINT DID NOT SEAL COMPLETELY | YES | 2022 | 105 | [69 empty] | YES | [14 empty] | MICHAEL SWAIM | OPERATIONS ADMINISTRATOR | mswaim@ldcgas.com | 936-539-3500 | 936-539-3501 | MICHAEL SWAIM | mswaim@ldcgas.com | 936-539-3500 | BOBBY BROWN JR | CHIEF OPERATING OFFICER | 936-539-3500 | bbrown@ldcgas.com | DURING A HOT TAP PROCEDURE TO CONNECT NEW SERVICE TO A RESIDENCE, THE ELECTROFUSION JOINT DID NOT SEAL COMPLETELY, RESULTING IN A LEAK. DURING AN ATTEMPT TO SQUEEZE OFF THE GAS SUPPLY SO REPAIRS COULD BE MADE, ONE OF TWO PROPERLY GROUNDED SQUEEZERS FAILED. AN ADDITIONAL SQUEEZER (ALSO GROUNDED) WAS BROUGHT INTO THE LOCATION TO SQUEEZE OFF THE SUPPLY ON THAT SIDE OF THE FUSION THE PROCEDURES WERE ADEQUATE AND FOLLOWED FOR ELECTROFUSION AND SQUEEZE OFF. EITHER A SPARK FROM INADVERTENT CONTACT OF METAL ON METAL OR STATIC ELECTRICITY CAUSED THE LEAK TO IGNITE, BURNING TWO OF OUR EMPLOYEES. ALL EMPLOYEES INVOLVED WHERE BOTH QUALIFIED TO PERFORM EACH TASK SUCH AS ELECTROFUSION AND SQUEEZE-OFF. ANOTHER NOTE TO ADD IS THAT THE NEW SERVICE LINE WAS PRESSURE TESTED PRIOR TO TAP.
2026-06-30 10:38 | NO | YES | NO | 20220069 | 38282 | 2022-11-02 15:29 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-10-03 13:23 | EASTERN | YES | 2022 | INTERSTATE 94 & PORTAGE ROAD | PORTAGE | KALAMAZOO | MI | 49002 | 42.2463 | -85.5587 | YES | [5 empty] | YES |  |  | 2022-10-03 16:47 | 1348944 | 1349071 | NATURAL GAS |  | 7578 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-10-03 13:23 | YES | OPERATOR | 2022-10-03 13:45 | 2022-10-03 13:42 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 120 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1973 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 2 | 18.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 31896 | 33911.7226229508066 | 62 | 65.91819672131145 | 0 | 0 |  | 8.95 | 67823 | 47880.8660844250363901018922852983988355 | 0 | 0 | 99781 | 52792.7065862505123142066957787481804949 | 81858.5069040971544401018922852983988355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 352 | 400 | 192.619(A)(2) | 1973-08-16 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | INTERSTATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 2022092302752 |  |  | CONTRACT LOCATOR | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON OCTOBER 3, 2022, AT APPROXIMATELY 13:23 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE NEAR INTERSTATE HIGHWAY 94 (I-94) AND PORTAGE STREET, KALAMAZOO (KALAMAZOO COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 13:42 HOURS. THE GSW CONFIRMED A THIRD-PARTY CONTRACTOR CUTTING IN A NEW ENTRANCE RAMP TO I-94 DAMAGED A NATURAL GAS PIPELINE, WHICH WAS LATER DETERMINED TO BE A 6-INCH STEEL HIGH PRESSURE PIPELINE. THE ROADWAY WAS ALREADY CLOSED TO TRAFFIC WHEN THE DAMAGED OCCURRED DUE TO THE ON-GOING CONSTRUCTION. POLICE AND FIRE DEPARTMENTS WERE ONSITE AND ENSURED NO CONSTRUCTION VEHICLES USED THE CONSTRUCTION ENTRANCES INTO THE AREA. AIR TRAFFIC INTO THE LOCAL AIRPORT WAS ALSO DIVERTED TO PREVENT THE POTENTIAL FOR INJURY. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE PIPELINE DAMAGE AND SUBSEQUENT GAS RELEASE. A DISTRIBUTION CREW ARRIVED ONSITE AT APPROXIMATELY 14:02 HOURS AND AN ISOLATION PLAN TO STOP GAS FROM BLOWING WAS DEVELOPED. TO ISOLATE, THE CREW UTILIZED AN EXISTING PRESSURE CONTROL FITTING TO THE NORTH OF THE DAMAGE LOCATION AND MULTIPLE VALVES WERE UTILIZED SOUTH OF THE DAMAGE LOCATION. GAS WAS CONTROLLED AT APPROXIMATELY 18:30 HOURS, THE DAMAGED SEGMENT WAS REMOVED AND REPLACED WITH 28-INCHES OF 6-INCH STEEL PIPELINE. REPAIRS WERE COMPLETED AND NORMAL OPERATIONS RESUMED ON OCTOBER 4, 2022, AT APPROXIMATELY 03:00 HOURS. NO LOSS OF SERVICE TO CUSTOMERS OCCURRED BECAUSE OF THE PIPELINE DAMAGE. FURTHER INVESTIGATION DETERMINED THE STAKING CONTRACTOR FAILED TO STAKE THE REQUESTED LOCATION AND PROVIDED AN INACCURATE POSITIVE RESPONSE CODE, CAUSING THE CONTRACTOR TO DAMAGE THE UNDERGROUND NATURAL GAS PIPELINE.
2026-06-30 10:38 | NO | NO | NO | 20220070 | 37834 | 2022-11-03 21:56 | SUPPLEMENTAL FINAL | 30839 | WALDEN, TOWN OF | PO BOX 489 513 HARRISON ST | WALDEN | CO | 80480 | 2022-08-31 13:00 | MOUNTAIN | YES | 2022 | 0.5 MILES EAST OF FAIR GROUNDS | WALDEN | JACKSON | CO | 80480 | 40.747 | -106.2604 | YES | [8 empty] | 2022-10-25 13:38 | 1350815 |  | NATURAL GAS |  | 6100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-09-02 05:30 | NO |  |  | 2022-09-02 09:00 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1970 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | 0 | 0 | 2000 | 2126.39344262295 | 0 | 0 | 0 | 0 |  | 5.3514 | 32644 | 23045.6186317321688500727802037845705968 | 0 | 0 | 34644 | 19632.5547044646482387190684133915574964 | 25172.0120743551188500727802037845705968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 15 | 275 | 192.619(A)(2) | 1995-04-15 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SCADA SYSTEM IS OPERATED BY THE GAS SUPPLIER (COLORADO INTERSTATE GAS). THEY DID NOT HAVE REASONABLE ALARMS SET FOR OUR SYSTEM AND NOTIFIED BY TELEPHONE US A WEEK AFTER THE LEAK LIKELY STARTED. SINCE THE EVENT, WE NOW RECEIVE REALISTIC VOLUME BASED ALARMS AS WELL AS DAILY VOLUME REPORTS FROM CIG. THE ALARM VALUES WILL LIKELY BE SET SEASONALLY GOING FORWARD. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1975 | YES | YES | YES |  |  | 2022 |  |  |  |  | YES | COLD APPLIED TAPE |  | YES | [19 empty] | 2022-05-11 | NO | [182 empty] | YES | [44 empty] | JOEL SHUTE | OPERATIONS AND COMPLIANCE MANAGER | joel@pipeline.group | 7202272026 |  | GRAHAM CREWS | graham@waldengas.com | 9703818557 | JOEL SHUTE | OPERATIONS AND COMPLIANCE MANAGER | 7202272026 | joel@pipeline.group | ON AUGUST 31, 2022 THE WALDEN PIPELINE OPERATORS RECEIVED PHONE CALLS FROM THE CIG CONTROL CENTER, ABOUT CONCERNS FOR INCREASED GAS USAGE. ONLINE FLOW RECORDS SHOWED AN APPARENT 10X FLOW INCREASE AROUND AUGUST 23. CIG HAD CHECKED ITS DELIVERY METER AND FOUND NOTHING ABNORMAL. THE 50-MILE TRANSMISSION SYSTEM WAS SYSTEMATICALLY ISOLATED AND CHECKED BY SECTION, AND CIG NOTED AN ABRUPT DROP IN FLOW. THE LAST SECTION ISOLATED WAS THE HIGH-PRESSURE DISTRIBUTION SYSTEM IN COLORADO THAT FEEDS THE TOWN SYSTEMS IN COWDREY AND WALDEN.NEXT DAY WE PINPOINTED LOW PRESSURE ON THE 2-INCH SECTION THAT HELPS FEED WALDEN. THIS WAS THE ORIGINAL SUPPLY LINE TO WALDEN, BUILT CA 1958 OF COATED STEEL 2" PIPE. WE HAD FOUND AND FIXED A CORROSION PINHOLE LEAK ON THIS SEGMENT EARLIER IN JULY, THE ONLY LEAK FOUND IN 20+ YEARS ON ANY PIPELINE IN COLORADO. THIS 17,000 FT SEGMENT WAS LOOPED CA 1979 WITH A 3" COATED STEEL LINE, PARALLEL AND ABOUT 10 FT SOUTHEAST. THE 2" SECTION WAS ISOLATED AND QUICKLY PRESSURED DOWN. LATER, GAS WAS REINTRODUCED AND A LEAK SURVEY DONE IN THE AREA AROUND THE PREVIOUS LEAK. THE NEWER LEAK WAS DETECTED ABOUT 180 FT SW OF THE PREVIOUS REPAIR, RUNNING ALONG A SHALLOW SAGEBRUSH WASH. WITH THIS SEGMENT SHUT DOWN AND THE 3" LOOP CARRYING THE LOAD, WE EXCAVATED THE NEW LEAK AREA ON NOVEMBER 2, INTENDING A REPAIR. THE PIPE AND COATING LOOKED IDENTICAL TO THAT WITH THE NEARBY LEAK REPAIR, BUT WAS VERY SHALLOW. THE EXCAVATED MATERIAL WAS MOSTLY BLACK, SMELLY LEAK DIRT INDICATIVE OF A LONG-TERM GAS LEAK. THE EXCAVATOR STRIPPED OUT THE PIPE FOR 60 FT, AND WE INTRODUCED A SMALL AMOUNT OF GAS FROM THE NEARBY BLOCK VALVE. THE EXPOSED & CLEANED-OFF PIPELINE DIDN'T LEAK. BUT THE GAS DETECTOR PICKED UP GAS NEAR THE FRONT AND NORTH SIDE OF THE BACKHOE, WELL AWAY FROM THE EXPOSED 2" AND THE SIDE AWAY FROM THE 3" LOOP. AFTER FURTHER INVESTIGATION, DIGGING OUT MORE LEAK DIRT, WE EVENTUALLY FOUND A SECOND STRING OF 2" PIPE RUNNING PARALLEL TO THE EXPOSED LINE, ABOUT 7 FT NW AND 3.5 FT DEEPER. WE STRIPPED OUT A 10-FT SECTION OF THIS NEWLY-DISCOVERED PIPE. THE COATING WAS A COLD-APPLIED YELLOW TAPE WITH THICK BLACK MASTIC, LIKELY HAND-APPLIED WITH GOOD OVERLAPS AND NO WRINKLES. WE COULD FIND NO OBVIOUS DEFECTS OR HOLES, UNTIL GAS WAS INTRODUCED. IN LESS THAN 5 SECONDS, THE SHORT SECTION APPEARED TO LEAK IN AT LEAST 4 PLACES, INCLUDING A PINKIE-SIZE HOLE IN THE TAPE AND THE PIPE ON THE BOTTOM. ALTHOUGH THE TAPE LOOKED GOOD ON FIRST INSPECTION, THERE WERE SEVERAL DEEP MARKS AND DENTS, ALTHOUGH THE SOIL WAS ROCK-FREE, MOIST CLAY. THE DEEP DENTS MAY HAVE BEEN MADE DURING INSTALLATION, WHEN THE PIPE WAS LOWERED IN WITH LOG CHAINS INSTEAD OF SOFTER PIPE SLINGS. THIS 3RD LINE IS NOT SHOWN ON ANY MAPS OR DESCRIBED IN ANY DOCUMENTS CONVEYED FROM THE ORIGINAL OWNER ROCKY MOUNTAIN NATURAL GAS TO THE TOWN IN 1995. WITH 5 CORROSION LEAKS (DESPITE GOOD CP READINGS) IN 200 FT IN A FEW MONTHS; AND WITH LITTLE HYDRAULIC VALUE, WE DECIDED TO PERMANENTLY ABANDON THE 2-INCH SEGMENT. WE CUT OUT AN 8-FT SECTION OF THE LEAKING PIPE, AND WELD-CAPPED BOTH ENDS OF THE 17,000 FT SEGMENT, WITH DOCUMENTATION THAT THIS SECTION CAN'T BE USED AGAIN. THIS LEAK WAS ABOUT 1.2 MILES FROM THE EDGE OF WALDEN. THE NEAREST PUBLIC ROAD IS THE COUNTY RODEO & FAIRGROUNDS ABOUT 1/2 MILE AWAY, AND 0.9 MILE TO THE NEAREST RESIDENCE. WE BELIEVE THIS LEAK HAS PERSISTED FOR DECADES. IT WAS NOT REPORTED BY THE PUBLIC, SINCE IT IS VERY REMOTE AND THE PREVAILING WIND GENERALLY BLOWS FROM THE SOUTHWEST, AWAY FROM ANY RESIDENCES OR ROADS. THE UTILITY HAD LEAK-SURVEYED THE 2 KNOWN PARALLEL LINES AS REQUIRED BY DOT PART 192. THE VEHICLE-MOUNTED RIG WAS ALWAYS DRIVEN BETWEEN THE 2 PIPELINES THAT ARE ONLY 8 FT APART. THE UNKNOWN LINE WAS ABOUT 12 FT OUTSIDE THE LEAK SURVEY PATH. WE BELIEVE OLD UNDETECTED PINHOLE LEAKS BLEW OUT WITH THE RE-PRESSURIZATION AFTER THE PREVIOUS REPAIR. NO INJURIES OR DEATHS RESULTED FROM THIS LEAK. THE ONLY DAMAGE WAS THE VALUE OF LOST GAS.
2026-06-30 10:38 | NO | YES | NO | 20220071 | 41505 | 2022-11-07 12:22 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2022-10-08 21:15 | PACIFIC | YES | 2022 | 2793 RIVER PLAZA DRIVE | SACRAMENTO | SACRAMENTO | CA | 95833 | 38.6091 | -121.5247 | [5 empty] | YES |  |  |  | 2022-10-09 00:36 | 1349399 | 1349521 | NATURAL GAS |  | 39.9 | 0.01 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-10-08 16:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 39.9 | YES | 24 | 2022-10-08 15:48 |  |  |  | 2022-10-08 16:00 | 2022-10-08 21:15 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 40 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | SERVICE TEE CAP | 1987 | UNKNOWN | [7 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 837176 | 890082.7783606553946 | 233444 | 248196.8954098359699 | 0 | 0 | 0 | 0 |  | 7.3 | 291 | 205.436681222707423580786026200873362445 | 0 | 0 | 1070911 | 462376.784902283803544978165938864628821 | 1138485.11045171407192358078602620087336 | 10 | 0 | 8 | 0 | 0 | 8 | 0 | 54 | 54 | 60 | 192.619(A)(2) | 1987-08-17 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA NOT IN PLACE THEREFORE GAS CONTROL INVOLVEMENT IS NOT A FACTOR. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | OTHER COMPRESSION TYPE FITTING | SERVICE TEE | TAPPING TEE |  | PLEXCO | UNKNOWN | PLASTIC |  | OTHER | LEAKED THROUGH A CRACK IN THE PLASTIC TEE CAP. | [13 empty] | YES | [9 empty] | YES |  |  |  | OTHER | CRACK ON PLASTIC TEE CAP | NO | [86 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | r1dj@pge.com | 510-298-7063 |  | SUSIE RICHMOND | gsr8@pge.com | 925-786-0267 | SUSIE RICHMOND | GAS OPS COMPLIANCE AND RISK MANAGER | 925-786-0267 | gsr8@pge.com | ON SATURDAY, OCTOBER 8, 2022, AT APPROXIMATELY 15:48 HOURS, PG&E WAS NOTIFIED OF AN EXPLOSION AT 2793 RIVER PLAZA DR., IN SACRAMENTO, CA. UPON ARRIVAL A PG&E GSR MEASURED GAS IN THE SOIL ABOVE THE 2-INCH SERVICE LINE. A LEAK INVESTIGATION FOUND THAT A PLEXCO POLYACETAL SERVICE TEE CAP (“INCIDENT TEE CAP”) WAS CRACKED AND LEAKING. THE CRACK WAS DISCOVERED WHEN THE TEE WAS EXPOSED BY EXCAVATION DURING THE LEAK INVESTIGATION FOLLOWING THE INCIDENT. PG&E MAINTENANCE AND CONSTRUCTION (“M&C”) CREWS SHUT IN THE GAS USING A SQUEEZE TOOL UPSTREAM OF THE LEAK. THE FIRE DEPARTMENT, POLICE, AND MEDIA WERE REPORTED ON SITE. NO FATALITIES OR INJURIES WERE REPORTED. THIS INCIDENT WAS REPORTED ONCE ESTIMATED DAMAGE WAS CONFIRMED TO BE AT LEAST $129,300K. THIS INCIDENT HAS BEEN REPORTED TO CPUC AND DOT (1349399/1349521).
2026-06-30 10:38 | NO | YES | NO | 20220072 | 37520 | 2022-11-08 08:36 | SUPPLEMENTAL FINAL | 2188 | CENTRAL FLORIDA GAS CORP | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2022-10-11 15:35 | EASTERN | NO | 2022 | ADAMS ST AT BRIDGERS AVE | AUBURNDALE | POLK | FL | 33823 | 28.0627 | -81.7804 | [5 empty] | YES |  |  |  | 2022-11-01 16:25 | 1351443 | 1351654 | NATURAL GAS |  | 2187.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-10-11 15:35 |  |  |  | 2022-10-11 16:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 96 | NO | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2015 | 2015 |  |  |  |  | 6 | D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 200000 | 212639.344262295 | 47000 | 49970.245901639325 | 1500 | 1594.7950819672125 | 0 | 0 |  | 5 | 10938 | 7721.877729257641921397379912663755458515 | 0 | 0 | 259438 | 113571.6978667048871834061135371179039301 | 271926.2629751591794213973799126637554585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 50 | 60 | 192.619(A)(2) | 2015-10-13 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | 263201452 |  |  | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [169 empty] | YES | MICHAEL MCCARTY |  | mmccarty@fpuc.com | 863 224-0417 |  | GEORGE FREEMAN | gfreeman@fpuc.com | 863 209-5030 | MICHAEL MCCARTY |  | 863 224-0417 | mmccarty@fpuc.com | ON 10/11/22 DRILLING SMART, DIRECTIONAL BORE CONTRACTOR, HIT A 6" PE GAS MAIN OPERATED BY CENTRAL FLORIDA GAS UNDER THE PAVING AT ADAMS ST AND BRIDGERS AVE IN AUBURNDALE, FLORIDA. THE 6" PE IS IN THE AREA WHERE THERE IS AN OLD ABANDONED 4" BARE STEEL GAS MAIN. THE CONTRACT LOCATOR FOR CENTRAL FLORIDA GAS WAS OFF ON HIS MARKINGS. DRILLING SMART EXPOSED THE 4" BARE STEEL AND ASSUMED IT WAS THE ACTIVE GAS MAIN AND BORED DEEPER THAN THAT LINE AND HIT THE ACTIVE 6" PE GAS MAIN. CENTRAL FLORIDA GAS RESPONDED AND USED PIPE SQUEEZERS ON BOTH SIDES OF THE INTERSECTION TO STOP THE FLOW OF GAS IN THIS DUAL FED GAS MAIN AND DID NOT LOSE SERVICE TO ANY CUSTOMERS. THE POINT OF DAMAGE WAS UNDER THE ROADWAY PAVING AND THE ACTUAL DAMAGE COULD NOT BE SEEN. ON 10/12/22, A NEW PIECE OF 6" PE WAS INSTALLED UNDER THE INTERSECTION VIA DIRECTIONAL BORE, TESTED AND TIED IN. GAS WAS RESTORED TO THAT MAIN ON 10/14/22. ON 11/1/22, THE CITY OF AUBURNDALE PRESENTED CENTRAL FLORIDA GAS WITH COSTS TO RESTORE THE ROAD BASE AND PAVING AT THAT INTERSECTION, PUSHING THE DAMAGE COST ABOVE THE PHMSA REPORTING THRESHOLD OF $122,000. A NOTICE WAS MADE TO THE NATIONAL REPORTING CENTER VIA TELEPHONE ON 11/1/22 AND A 48 HOUR FOLLOW UP ON 11/3/22. 12/28/2022 SUPPLEMENT CORRECTION MADE TO PART A (19) - INCORRECT NRC REPORT NUMBER ENTERED INITIALLY WITH A NUMBER LEFT OUT. CORRECT NRC REPORT NUMBER OF 1351443 ENTERED. PART J - EXCAVATION DAMAGE (EXCAVATION DAMAGE BY THIRD PARTY) REMOVED AS NOT NECESSARY SINCE LISTED IN G3. CHANGED CONTRIBUTING FACTOR TO INCORRECT OPERATION (FAILURE TO FOLLOW PROCEDURES) DUE TO CONTRACT LOCATOR BEING OFF ON MARKS AND NOT LISTING THE TYPE AND SIZE OF GAS MAIN IN THE POSITIVE RESPONSE FOR THE LOCATE TICKET. THE LOCATOR WAS OFF ON THE LOCATE MARKS BY A FEW FEET. THE EXCAVATOR SPOTTED A PIPE SEVERAL FEET AWAY IN A GRASSY AREA AND ASSUMED IT WAS THE GAS MAIN AND AT A CERTAIN DEPTH. THEY BORED THE ROAD AT A DEEPER DEPTH AND HIT THE LIVE PE GAS MAIN. THE PIPE THEY DUG UP AND SPOTTED FOR DEPTH WAS AN OLD RETIRED 4" BARE STEEL GAS MAIN AND NOT THE LIVE 6" PE GAS MAIN. THE CONTRACTOR LOCATOR TECHNICIANS WERE BROUGHT IN AND INSTRUCTED AGAIN TO LIST THE SIZE AND TYPE OF PIPE ON THE POSITIVE RESPONSE TO MARKED LOCATE TICKETS, PER PROCEDURES, TO ENSURE EXCAVATORS ARE SURE WHICH PIPES THEY ARE SPOTTING. NO OTHER DAMAGE INFORMATION OR COSTS REQUIRE UPDATING.
2026-06-30 10:38 | NO | YES | NO | 20220073 | 38489 | 2022-11-16 17:36 | SUPPLEMENTAL FINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2022-10-17 11:06 | EASTERN | YES | 2022 | 1372 BARRON LAKE ROAD | NILES | CASS COUNTY | MI | 49120 | 41.8533 | -86.177 | [5 empty] | YES |  | YES | RETIRED SERVICE LINE. | 2022-10-17 11:06 | 1350127 | 1350718 | NATURAL GAS |  | 7.04 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-10-17 07:57 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 7.04 | NO | 1 | 2022-10-17 07:57 |  |  |  | 2022-10-17 08:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1997 | 1997 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | GAS METER | [9 empty] | OTHER | [8 empty] | CAR IMPACT DISLODGED METER FROM METER BAR AND PIPING. | CLASS 3 LOCATION | 200000 | 212639.344262295 | 990 | 1052.56475409836025 | 2240 | 2381.560655737704 | 0 | 0 |  | 8.94 | 63 | 44.4759825327510917030567685589519650655 | 0 | 0 | 203293 | 87774.9448385711550860262008733624454148 | 216117.9456546638153417030567685589519651 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1962-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  |  | YES |  |  | NO | UNKNOWN | SMALL TRUCK | ROADWAY | 47 | NO | [142 empty] | JENNIFER POND | SUPERVISOR OF CODES AND STANDARDS | jennifer.pond@semcoenergy.com | 8102422381 |  | JOHN O'BRYANT | john.obryant@semcoenergy.com | 269-506-3222 | PHIL LENN | DIRECTOR OF OPERATIONS SUPPORT | 8106503774 | phil.lenn@semcoenergy.com | ON 17 OCT 2022 AT APPROXIMATELY 07:57, SEMCO WAS NOTIFIED BY THE CASS CO CENTRAL DISPATCH THAT THERE WAS A STRUCTURE FIRE AT THE REFERENCED ADDRESS. UPON ARRIVING AT 8:15 AM, THE SEMCO TECHNICIAN CHECKED WITH THE HOWARD TWP. FIRE CHIEF WHOM INFORMED HIM THAT THE VEHICLE HAD STRUCK ANOTHER VEHICLE IN THE ROAD, VEERED OFF THE ROAD, TRAVELED THRU THE YARD, STRIKING THE GAS METER SET WHICH THEN IGNITED, CAUSING THE STRUCTURE FIRE. THE GAS WAS SECURED AT 8:33 AM AND THE FIRE DEPARTMENT DISTINGUISHED THE FIRE.
2026-06-30 10:38 | NO | NO | NO | 20220075 | 37413 | 2022-12-02 15:08 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-11-04 15:29 | EASTERN | YES | 2022 | N. ELM AVENUE & ROSEHILL ROAD | JACKSON | JACKSON | MI | 49201 | 42.2766 | -84.3842 | [5 empty] | YES | YES |  |  | 2022-11-04 22:02 | 1351782 | 1351886 | NATURAL GAS |  | 3444 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-11-04 15:29 | YES | OPERATOR | 2022-11-04 15:55 | 2022-11-04 15:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2022 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 2 | 9.4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 36708 | 39027.8252459016243 | 73 | 77.613360655737675 | 0 | 0 |  | 5.77 | 19872 | 14028.9956331877729257641921397379912664 | 0 | 0 | 56653 | 27304.8184132722517165502183406113537118 | 53134.4342397451349007641921397379912664 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 53 | 53 | 60 | 192.619(A)(2) | 2022-05-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 2022083000497 |  |  | CONTRACT LOCATOR | NO | YES | 7 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON NOVEMBER 4, 2022, AT APPROXIMATELY 15:29 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE AT THE INTERSECTION OF N. ELM AVENUE AND ROSEHILL ROAD, JACKSON (JACKSON COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 15:55 HOURS. THE GSW CONFIRMED A THIRD-PARTY CONTRACTOR PERFORMING ROADWAY EXCAVATION WORK DAMAGED A NATURAL GAS PIPELINE, WHICH WAS LATER DETERMINED TO BE A 6-INCH STEEL MEDIUM PRESSURE PIPELINE. POLICE AND FIRE DEPARTMENTS WERE ONSITE AND ASSISTED THE CONTRACTOR WITH ROAD CLOSURE TO ENSURE THE SAFETY OF PEDESTRIANS AND VEHICLE TRAFFIC. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE DAMAGE AND SUBSEQUENT NATURAL GAS RELEASE. A DISTRIBUTION CREW ARRIVE ONSITE AT APPROXIMATELY 16:15 HOURS AND DEVELOPED A PLAN TO ISOLATE AND ARREST THE BLOWING GAS. THE DAMAGED SEGMENT WAS ISOLATED BY INSTALLING A PRESSURE CONTROL FITTING AT A REMOTE LOCATION EAST OF THE DAMAGE AND SQUEEZING THE PIPELINE AT A LOCATION WEST OF THE DAMAGE. THE BLOWING GAS WAS CONTAINED AT APPROXIMATELY 04:30 HOURS (NOVEMBER 5, 2022) AND A PERMANENT REPAIR WAS COMPLETED BY WELDING AN ENCAPSULATED FITTING AROUND THE DAMAGED SEGMENT. REPAIRS WERE COMPLETED AND NORMAL OPERATIONS RESUMED ON NOVEMBER 5, 2022, AT APPROXIMATELY 10:30 HOURS. SERVICE RESTORATION FOR ALL IMPACTED CUSTOMERS BEGAN AFTER THE PIPELINE REPAIR.
2026-06-30 10:38 | NO | YES | NO | 20220077 | 38088 | 2022-12-15 12:18 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2022-11-16 11:45 | PACIFIC | NO | 2022 | EAST SIDE OF GRANT ST, ACROSS THE STREET FROM RESIDENCE 2707 GRANT ST | CONCORD | CONTRA COSTA | CA | 94520 | 37.9878 | -122.0379 | [5 empty] | YES |  |  |  | 2022-11-16 12:23 | 1352705 | 1352897 | NATURAL GAS |  | 2076 | 2.37 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-11-16 10:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 2076 | NO | 1 | 2022-11-16 10:30 |  |  |  | 2022-11-16 10:53 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 22 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1961 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 6 | [7 empty] | CLASS 3 LOCATION | 350750 | 372916.24999999985625 | 48695 | 51772.364344262275125 | 2533 | 2693.077295081966175 | 0 | 0 |  | 6.3 | 13079 | 9233.355167394468704512372634643377001456 | 15 | 10.58951965065502183406113537117903930131 | 415072 | 181071.0428522681833963027656477438136827 | 436625.6363263892212763464337700145560408 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 54 | 54 | 60 | 192.619(A)(2) | 1975-06-10 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | MILLING EQUIPMENT | ROAD WORK | YES | X229201521 | 811 |  | FACILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | r1dj@pge.com |  |  | SUSIE RICHMOND | gas ops compliance and risk manager |  | SUSIE RICHMOND | GAS OPS COMPLIANCE AND RISK MANAGER | 925-786-0267 | gsr8@pge.com | ON NOVEMBER 16, 2022, AT APPROXIMATE 11:45 HOURS PG&E INCIDENT ON-CALL PERSONNEL CONFIRMED THAT A DIG-IN LOCATED AT THE EAST SIDE OF GRANT STREET, ACROSS THE STREET FROM THE RESIDENCE OF 2707 GRANT STREET IN CONCORD, CA REACHED DOT REPORTABLE INCIDENT CRITERIA. THIRD-PARTY CONSTRUCTION EQUIPMENT STRUCK A 4" STEEL DISTRIBUTION MAIN RESULTING IN MULTIPLE PUNCTURES RESULTING IN A RELEASE OF GAS WITH SUBSEQUENT IGNITION. PG&E PERSONNEL RESPONDED AND STOPPED GAS FLOW APPROXIMATELY AT 12:27 HOURS. THERE WERE NO FATALITIES OR INJURIES. MEDIA, FIRE AND POLICE WERE REPORTED ON SITE. THIS INCIDENT WAS REPORTED TO THE DOT #1352705/1352897 AND CPUC 221116-15335 DUE TO MEDIA COVERAGE AND ONCE IT WAS CONFIRMED THAT THE INCIDENT RESULTED IN ESTIMATED PROPERTY DAMAGE OF AT LEAST $129,300.
2026-06-30 10:38 | NO | YES | YES | 20220078 | 38138 | 2022-12-20 17:10 | SUPPLEMENTAL FINAL | 18704 | SULLIVAN GAS DEPT, CITY OF | 304 S HAMILTON ST | SULLIVAN | IL | 61951 | 2022-11-10 13:00 | CENTRAL | YES | 2022 | 1209 S HAMILTON ST. | SULLIVAN | MOULTRIE | IL | 61951 | 39.5875 | -88.6094 |  |  | YES | [6 empty] | 2022-11-14 08:19 | 1352505 | 1352759 | NATURAL GAS |  | 1.04 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2022-11-10 13:00 | YES | OPERATOR | 2022-11-10 13:00 | 2022-11-10 13:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2022 | UNKNOWN |  |  |  |  | 2 | GRADE B | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 200 | 212.639344262295 | 35000 | 37211.885245901625 | 5000 | 5315.983606557375 | CITY EMPLOYEE AND CONSULTANTS TIME AND LABOR. | 3.32 | 3 | 2.11790393013100436681222707423580786026 | 0 | 0 | 40203 | 17356.9216121411763231441048034934497817 | 42742.6261006514260043668122270742358079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 37 | 40 | 192.619(A)(3) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 60 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | INCORRECT OPERATION | INCORRECT EQUIPMENT | [222 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED |  |  |  | YES |  |  | CONSTRUCTION | YES | NO, THEY WERE NOT QUALIFIED FOR THE TASK(S) NOR WERE THEY PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | ANDREW J WOODWORTH | CITY OF SULLIVAN GAS DEPARTMENT FOREMAN | gasdept@sullivanil.us | 2174339303 |  |  |  |  | ANDREW J WOODWORTH |  | 2174339303 | gasdept@sullivanil.us | ON NOVEMBER 10TH 2022, I (FOREMAN) AND THE REST OF MY CREW WERE INSTALLING A SECTION OF NEW GAS MAIN INSIDE THE CITY LIMITS OF SULLIVAN IL. AFTER I COMPLETED THE WELDING AND SUCCESSFUL PRESSURE TESTING OF TWO BOLT ON VALVE FLANGE WELDS AND ONE WELD SECURING THE 2 INCH TEE TO THE PREEXISTING 37 PSI, 2 INCH GAS MAIN, ALL FOUR OF US PROCEEDED TO COMMENCE DRILLING THE MAIN TO INTRODUCE GAS TO THE NEW MAIN BY UTILIZING ONE OF OUR MUELLER E-4 MODEL DRILLING MACHINES. UPON SUCCESSFUL COMPLETION OF THE DRILLING PROCESS TECHNICIAN 1 RAISED THE SHELL CUTTER INTO THE DRILLING MACHINE CHAMBER AND THE GATE VALVE WAS CLOSED TO STOP OFF GAS FLOW FROM THE TOP OF THE TEE. THE DRILLING MACHINE WAS DISASSEMBLED FROM THE GATE VALVE AND THE SHELL CUTTER DISASSEMBLED AND THE COMPLETION PLUG INSTALLED. ONCE TECHNICIAN 1 REASSEMBLED THE MACHINE IT WAS REATTACHED TO THE TOP OF THE GATE VALVE AND THE VALVE WAS OPENED ALLOWING THE COMPLETION PLUG TO BE LOWERED INTO THE TOP OF THE TEE AND THREADED INTO IT. ONCE THE PLUG WAS THREADED INTO THE TEE AND TIGHT THE SHAFT WAS REMOVED FROM THE COMPLETION PLUG AND THE MACHINE WAS REMOVED AGAIN FROM THE GATE VALVE. THE GATE VALVE WAS THEN REMOVED AND THE COMPLETION PLUG WRENCH WAS PUT INTO THE TOP OF THE COMPLETION PLUG BY TECHNICIAN 1. TECHNICIAN 1 PERFORMED ALL THE ASSEMBLY AND DISASSEMBLY OF THE MACHINE. TECHNICIAN 1 THEN TURNED THE PLUG TIGHTENING IT INTO THE TEE A 1/4 - 1/2 TURN AND THEN HANDED THE WRENCH TO TECHNICIAN 3 AND TOLD HIM TO FINISH TIGHTENING THE PLUG. TECHNICIAN 3 THEN FITTED THE WRENCH INTO THE TOP OF THE COMPLETION PLUG. HE IS RIGHT HANDED SO HE PUT HIS LEFT HAND ON TOP OF THE WRENCH TO SECURE IT AND HIS RIGHT HAND ON THE HANDLE TO TURN IT. AS SOON AS HE STARTED TO TURN THE PLUG IT BLEW OUT THE TOP. AT THE TIME THAT IT BLEW OUT I (FOREMAN) WAS SEATED ON THE EAST EDGE OF THE BELL HOLE, TECHNICIAN 2 WAS SEATED ON THE SOUTH EDGE, TECHNICIAN 3 WAS STANDING IN THE SOUTH WEST CORNER OF THE PREEXISTING AND NEW MAINS AND TECHNICIAN 1 WAS STANDING IN THE NORTH WEST CORNER OF THE PREEXISTING AND NEW MAINS. I ROLLED AWAY FROM THE EXCAVATION. I LOOKED TO MY LEFT AND SAW THAT TECHNICIAN 2 WAS CLEAR OF THE HOLE. I LOOKED RIGHT AND SAW TECHNICIAN 3 MOVING WEST IN THE DITCH AWAY FROM IT. I LOOKED RIGHT AND SAW TECHNICIAN 1 LOOKING AROUND ALL AROUND HIM I YELLED ARE YOU OK AND HE GAVE ME A THUMBS UP AND CONTINUED LOOKING AROUND HIM. I LOOKED AT TECHNICIAN 3 AND SAW HIS FACE WAS OBVIOUS SHOCK. I SAW HIM HOLDING HIS LEFT ARM AND THEN SAW HIS ARM STARTING TO BLEED. I THEN RAN AROUND THE NORTH SIDE OF THE HOLE AND GRABBED TECHNICIAN 3 AND PULLED HIM OUT OF THE DITCH AND TOOK HIM TO GET A FIRST AID KIT. AT THIS TIME I SAW HOW BAD HIS ARM WAS BLEEDING SO I KEYED UP ON THE CITY RADIO AND STATED SULLIVAN EMS SULLIVAN EMS YOU ARE NEEDED NOW AT THE H&R BLOCK BUILDING ON SOUTH HAMILTON STREET INJURED CITY EMPLOYEE WITH SHRAPNEL WOUNDS TO HIS LEFT FOREARM AND BICEP WITH SEVERE BLEEDING. I REPEATED THIS MESSAGE TWICE ON THE RADIO. I THEN TURNED TO TECHNICIAN 3 AND BEGAN MEDICAL TRIAGE. HE SAID IT FEELS LIKE SOMETHING IS MOVING UP MY ARM! I THEN TOOK OFF MY LEATHER BELT AND TOLD HIM IM GONNA TIE OFF YOUR ARM! I USED MY BELT JUST BELOW HIS LEFT ARMPIT TO APPLY A TOURNIQUET. I WRAPPED IT TIGHT AND GAVE HIM THE LOOSE END AND TOLD HIM TO HOLD IT AND NOT LET GO UNTIL THE EMTS TOLD HIM TO. MOMENTS LATER EMTS ARRIVED AND TOOK TECHNICIAN 3 TO ST MARYS HOSPITAL BY AMBULANCE IN DECATUR IL. I TURNED BACK TO TECHNICIANS 1 AND 2 AND THEY HAD ALREADY PUT THE GATE VALVE BACK ON AND SHUT DOWN THE GAS. TECHNICIAN 1 AND I PUT A NEW COMPLETION PLUG IN THE TEE AND THEN SECURED THE AREA AND WENT TO DO DRUG SCREENINGS PER HUMAN RESOURCES.
2026-06-30 10:38 | NO | YES | NO | 20220079 | 37670 | 2022-12-21 13:21 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2022-11-30 17:00 | PACIFIC | NO | 2022 | LA CIENEGA STREET AND PYLE AVE | LAS VEGAS | CLARK | NV | 89183 | 36.0055 | -115.1614 | [5 empty] | YES |  |  |  | 2022-11-30 17:44 | 1353841 | 1354008 | NATURAL GAS |  | 500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 6 | 2022-10-31 19:52 | YES | OPERATOR | 2022-10-31 23:01 | 2022-10-31 18:23 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1999 | 1998 |  |  |  |  | 2 | ASTM D-2513 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 180432 | 191834.7108196720572 | 12285 | 13061.371721311470375 | 0 | 0 |  | 5.4087 | 2704 | 1908.937409024745269286754002911208151383 | 0 | 0 | 195421 | 84754.7375847710722305531295487627365357 | 206805.0199500082728442867540029112081514 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 48 | 55 | 60 | 192.619(A)(2) | 1999-01-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 8 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [9 empty] | YES |  |  |  | OTHER | MATERIAL DEGRADATION | NO | [73 empty] | YES | [12 empty] | MICHAEL ROSS | SUPERVISOR OF ENGINEERING | michael.ross@swgas.com | 7023652361 |  |  |  |  | ANTHONY HILLS | DIRECTOR OF GAS OPERATIONS | 7023652049 | anthony.hills@swgas.com | AT 17:35 ON OCTOBER 31, 2022, SOUTHWEST GAS RECEIVED A CALL ABOUT AN ODOR/HISSING ON A DIRT LOT NEAR THE INTERSECTION OF LA CIENEGA STREET AND PYLE AVENUE IN LAS VEGAS, NEVADA. CREWS ARRIVED ONSITE AT 18:23 AND BEGAN INVESTIGATION. AT 19:52, SOUTHWEST GAS IDENTIFIED A LEAK ON ITS FACILITIES AND MADE THE AREA SECURE. THE LEAK WAS ISOLATED AND GAS SUPPLY WAS SHUT OFF TO THE AFFECTED PIPE SEGMENT BY 21:24 ON OCTOBER 31, 2022. THIS SEGMENT OF THE MAIN WILL NOT BE RETURNED TO SERVICE. SOUTHWEST GAS EVACUATED A TOTAL OF SIX PERSONS FROM THREE NEARBY HOMES. AFTER GAS WAS SHUT OFF, CREWS BEGAN AERATING THE SURROUNDING SOIL TO REMOVE RESIDUAL GAS IN THE GROUND. ALTHOUGH RESIDUAL GAS READS WERE DROPPING, SOUTHWEST GAS REMAINED ONSITE CONTINUOUSLY MONITORING THE RESIDUAL READS AND AERATING THE SOILS. ON NOVEMBER 30, 2022 SOUTHWEST GAS DETERMINED THAT THE ACCUMULATED EMERGENCY RESPONSE COSTS EXCEEDED $129,300. THE INCIDENT COSTS WERE MOSTLY ATTRIBUTED TO EMPLOYEE LABOR UTILIZED TO CONTINUOUSLY AERATE AND REMEDIATE THE RESIDUAL GAS IN THE SOIL. SOUTHWEST DISCONTINUED ITS EMERGENCY RESPONSE AND DECOMMISSIONED THE INCIDENT COMMAND STRUCTURE ON DECEMBER 8, 2022 AFTER THE RESIDUAL GAS READS WERE REMEDIATED TO SAFE NON-HAZARDOUS CONDITIONS. LABORATORY ANALYSIS COMPLETED IN JANUARY 2023 CONCLUDED: FRACTOGRAPHIC AND ANALYTICAL EXAMINATION INDICATED THAT THE THROUGHWALL AXIAL FRACTURE RESPONSIBLE FOR THE LEAK PATH OCCURRED DUE TO INTERNAL THERMAL-OXIDATIVE DEGRADATION. THE FRACTURE PROGRESSED THROUGH THE WALL OF THE PIPE FROM THE INSIDE DIAMETER TO THE OUTSIDE DIAMETER BY WAY OF HOOP STRESS AND BRITTLE FRACTURE DUE TO DEGRADATION AND LOW SLOW CRACK GROWTH RESISTANCE OF THE PIPE MATERIAL. THIS SUPPLEMENTAL REPORT UPDATES THE CAUSE OF THE LEAK IN PART G BASED ON THE LABORATORY ANALYSIS TO BE A CRACK CAUSED BY DEGRADATION. IT ALSO UPDATES PART J AND THE COSTS ASSOCIATED WITH THE INCIDENT IN PART D.
2026-06-30 10:38 | NO | NO | NO | 20220080 | 37509 | 2022-12-22 13:57 | ORIGINAL | 6720 | ATMOS ENERGY CORPORATION - COLORADO/KANSAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-11-24 18:02 | MOUNTAIN | NO | 2022 | 1621 SAN JUAN CIRCLE | EVANS | WELD | CO | 80620 | 40.3772 | -104.7056 |  |  |  | YES | [5 empty] | 2022-11-24 18:45 | 1353337 |  | NATURAL GAS |  | 5.61 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-11-24 18:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 4.98 | NO | 4 | 2022-11-24 18:02 |  |  |  | 2022-11-24 18:23 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1995 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | STEEL NIPPLE | [9 empty] | OTHER | [8 empty] | VEHICLE HIT | CLASS 3 LOCATION | 90000 | 95687.70491803275 | 2100 | 2232.7131147540975 | 1400 | 1488.475409836065 | 0 | 0 |  | 10.97 | 62 | 43.77001455604075691411935953420669577875 | 0 | 0 | 93562 | 40401.5903667645176783114992721979621543 | 99452.6634571789532569141193595342066958 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 18 | 18 | 20 | 192.619(A)(2) | 1995-05-25 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 75 | NO | [142 empty] | VONNA M SEEBER | COMPLIANCE | vonna.seeber@atmosenergy.com | 8163944940 |  | KURTIS RUTZ | kurtis.rutz@atmosenergy.com | 9705390057 | DOUGLAS L SHATAS | MANAGER COMPLIANCE | 8168630951 | doug.shatas@atmosenergy.com | DRIVER LOST CONTROL OF VEHICLE ON ROADWAY BEHIND 1621 SAN JUAN CIRCLE IN EVANS, COLORADO. VEHICLE WENT OFF THE ROAD THROUGH A PRIVATE FENCE AND HIT AN ATMOS GAS METER AND A HOUSE. THE HOUSE, THE METER, AND THE VEHICLE CAUGHT FIRE. THE DRIVER FLED THE SCENE. THE EVANS FIRE DEPARTMENT RESPONDED, PULLED THE VEHICLE AWAY FROM THE HOUSE, PUT OUT THE FIRE, AND SHUT OFF THE GAS RISER VALVE TO STOP THE RELEASE OF GAS. THREE HOMES AND FOUR PEOPLE WERE EVACUATED DURING THE INITIAL INVESTIGATION. ATMOS DETERMINED THAT THERE WAS NO DAMAGE TO UNDERGROUND PIPING.
2026-06-30 10:38 | NO | YES | YES | 20220081 | 38655 | 2022-12-22 16:15 | SUPPLEMENTAL FINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2022-11-22 14:29 | EASTERN | NO | 2022 | 1121 BAYARD ST | BALTIMORE | BALTIMORE CITY | MD | 21223 | 39.2799 | -76.6371 | [6 empty] | YES |  |  | 2022-11-22 16:39 | 1353220 |  | NATURAL GAS |  | 5.6 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES | 2022-11-22 14:29 | OPERATOR/CONTRACTOR |  | 5.6 | YES | 0 | 2022-11-22 14:29 |  |  |  | 2022-11-22 14:40 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1904 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 600000 | 637918.032786885 | 0 | 0 | 20000 | 21263.9344262295 | 0 | 0 |  | 0.45 | 3 | 2.11790393013100436681222707423580786026 | 0 | 0 | 620003 | 267668.9380055838943231441048034934497817 | 659184.0851170446310043668122270742358079 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0.25 | 0.25 | 0.36 | 192.623 | 1904-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | THE FRACTURE IN THE CAST IRON GAS MAIN AT THIS LOCATION LIKELY OCCURRED WHEN THE LOAD EXCEEDED THE FRACTURE STRENGTH OF THE PIPE. | NO | [218 empty] | JEFFREY WEATHERHOLTZ | MANAGER GAS ENGINEERING AND STANDARDS | jeffrey.weatherholtz@bge.com | 4105981601 |  |  |  |  | ROBERT REX | SR. MANAGER GAS ENGINEERING AND ASSET PERFORMANCE | 3025933732 | robert.rex@delmarva.com | ON NOVEMBER 22, 2022, A NATURAL GAS EXPLOSION OCCURRED AT 1121 BAYARD STREET IN BALTIMORE CITY, MARYLAND. IT WAS DETERMINED AFTER THE INCIDENT THAT A 4" CAST IRON LOW-PRESSURE GAS MAIN EXPERIENCED A FULL CIRCUMFERENTIAL BREAK WHICH ALLOWED NATURAL GAS TO MIGRATE UNDERGROUND. THE FRACTURE IN THE CAST IRON GAS MAIN AT THIS LOCATION LIKELY OCCURRED WHEN THE LOAD EXCEEDED THE FRACTURE STRENGTH OF THE PIPE. THE GAS ENTERED THE RESIDENCE LOCATED AT 1121 BAYARD STREET. THE GAS THAT ENTERED THIS PROPERTY REACHED AN EXPLOSIVE LIMIT AND WAS IGNITED BY AN UNKNOWN SOURCE.
2026-06-30 10:38 | NO | YES | NO | 20230001 | 37527 | 2023-01-03 13:43 | ORIGINAL FINAL | 12642 | SPIRE GULF INC. | 700 MARKET | SAINT LOUIS | MO | 63101 | 2022-11-16 09:06 | CENTRAL | YES | 2022 | 1363 CREOLA AXIS LOOP RD | CREOLA | MOBILE COUNTY | AL | 36505 | 30.9317 | -88.0075 | [5 empty] | YES |  |  |  | 2022-11-16 10:12 | 1352681 | 1352863 | NATURAL GAS |  | 23 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-11-16 09:06 | ALLOWED TO BURN OUT |  | 23 | NO | 0 | 2022-11-16 09:06 | YES | OPERATOR | 2022-11-16 09:26 | 2022-11-16 09:26 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO LOSS OF COVER |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2022 | UNKNOWN |  |  |  |  | 2 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | OTHER | [8 empty] | LINE DAMAGED BY TRACKHOE TRACK. | CLASS 2 LOCATION | 0 | 0 | 10000 | 10631.96721311475 | 500 | 531.5983606557375 | 125000 | 132899.590163934375 | TRACKHOE DAMAGED BY FIRE | 6 | 138 | 97.42358078602620087336244541484716157205 | 0 | 0 | 135638 | 58577.5826830839938646288209606986899563 | 144160.5793184908887008733624454148471616 | 1 | 0 | 62 | 0 | 0 | 62 | 1 | 40 | 40 | 60 | 192.619(A)(2) | 2022-04-11 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER RESPONDED TO THE SCADA AND MADE THE APPROPRIATE NOTIFICATIONS | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE TRACK RAILS OF A TRACKHOE DUG INTO SOFT GROUND AND DAMAGED PIPE WHILE MOBILIZING FROM A JOB SITE. | [154 empty] | JUSTIN MONROE | MANAGER PIPELINE SAFETY DISTRIBUTION | justin.monroe@spireenergy.com | 205-572-2928 |  | JUSTIN MONROE | justin.monroe@spireenergy.com | 205-572-2928 | CRAIG HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | ON NOVEMBER 16, 2022 AT 9:06 AM, A THIRD-PARTY CONTRACTOR DAMAGED A 2-INCH MEDIUM PRESSURE (60 PSIG MAOP) PLASTIC MAIN LOCATED AT 1363 CREOLA AXIS LOOP, CREOLA AL. THE CONTRACTOR WAS MOVING A TRACKHOE IN A SOFT AREA OF DIRT AND SUNK THE TRACKS INTO THE UNDERGROUND PIPELINE, CAUSING A RUPTURE. A FIRE IGNITED AND DAMAGED THE TRACKHOE. THIS REPORT WAS SUBMITTED BY PORTAL ON DECEMBER 16, 2022 BUT HAD TO BE RESUBMITTED DUE TO TECHNICAL ISSUES IN THE PORTAL.
2026-06-30 10:38 | NO | YES | NO | 20230002 | 41251 | 2023-01-12 16:41 | SUPPLEMENTAL FINAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2022-12-13 09:30 | EASTERN | NO | 2022 | 3204 CREST ROAD | HARRISBURG | DAUPHIN | PA | 17109 | 40.2923 | -76.848 |  | YES | [7 empty] | 2022-12-13 10:39 | 1354879 | 1355040 | NATURAL GAS |  | 42.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-12-13 09:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 42.1 | YES | 11 | 2022-12-13 09:07 |  |  |  | 2022-12-13 09:25 | 2022-12-13 09:25 | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | EXPOSED DUE TO EXCAVATION | 42 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | SERVICE W/INSIDE METER | 1958 | UNKNOWN | [7 empty] | STEEL |  | FURNACE BUTT WELDED |  | 0.105 | [6 empty] | OTHER | [8 empty] | WHEN THE SERVICE WAS STRUCK, THE EXCAVATOR DAMAGED THE SERVICE AT THE POINT OF CONTACT AND THE DAMAGE ALSO INDUCED FRACTURE WITHIN THE THREADED SERVICE LINE CONNECTION INSIDE THE BASEMENT AND PULLED THE SERVICE LINE AWAY FROM THE INSIDE METER AND REGULATOR ASSEMBLY. THE FRACTURED SERVICE LINE WAS SIMULTANEOUSLY PULLED INTO THE FOUNDATION WALL SLEEVE AND REMAINED WITHIN THE FOUNDATION WALL ALLOWING PRESSURIZED NATURAL GAS TO ESCAPE INTO THE BASEMENT. | CLASS 3 LOCATION | 1060000 | 1126988.5245901635 | 25000 | 26579.918032786875 | 11000 | 11695.163934426225 | 0 | 0 |  | 9.17 | 386 | 272.503639010189228529839883551673944687 | 0 | 0 | 1096386 | 473388.4933304700295778748180494905385735 | 1165536.11019638678922852983988355167394 | 0 | 0 | 14 | 2 | 0 | 23 | 0 | 55 | 55 | 60 | 192.619(A)(1) | 1958-07-23 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 15.8 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FACILITY WAS HIT BY EXCAVATOR. GAS CONTROL DID NOT HAVE AN IMPACT ON THIS INCIDENT. | [12 empty] | YES | 4 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [6 empty] | NO | NO | MEASURED DEPTH FROM GRADE | 42 | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 20223461851 |  | YES | FACILITY OWNER | NO | YES | 12 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CHAD REINER | ENGINEER II | creiner@ugi.com | 484 577-6666 |  | JOHN TOUMEH | joumeh@ugi.com | 717 675 4606 | PAM JOCSAK | VP EHS AND TECHNICAL SUPPORT | 484-824-5508 | pjocsak@ugi.com | ON 12/12/2022 AT 13:17, UGI RECEIVED AN EMERGENCY EXCAVATION TICKET ("TICKET") (SERIAL # 20223461851) THROUGH THE PENNSYLVANIA ONE CALL SYSTEM, ISSUED BY AN EXCAVATOR, PRONTO PLUMBING, WITH A PROPOSED DIG DATE OF 08:00 ON 12/13/22 AT 3204 CREST ROAD, HARRISBURG (THE "PROPERTY"). UGI RESPONDED THROUGH THE ONE CALL SYSTEM ON 12/12/22 AT 13:18 STATING: "CONFLICT LINES NEARBY DIRECT CONTACT TO FOLLOW BY FACILITY OWNER". THE UGI DISPATCHER MISTAKENLY ASSIGNED THE TICKET TO A CONTRACTOR THAT DOES NOT PERFORM EMERGENCY LOCATES. ON 12/13/2022 AT 09:06:20, THE FIRE DEPARTMENT WAS DISPATCHED TO THE PROPERTY DUE TO A LINE HIT. AT 09:07:09, EXCAVATOR PLACED A RE-NOTIFY TICKET THROUGH THE ONE CALL SYSTEM. AT 09:07:46, UGI DISPATCH RECEIVED A CALL FROM DAUPHIN COUNTY 911, REGARDING A HIT GAS LINE AT THE PROPERTY. UGI RESPONDED TO THE RE-NOTIFY TICKET AT 9:09 STATING: "CONFLICT LINES NEARBY DIRECT CONTACT TO FOLLOW BY FACILITY OWNER". UGI DISPATCHED THE CLOSEST AVAILABLE QUALIFIED FIRST RESPONDER BASED ON THE CALL RECEIVED BY DISPATCH, WHO ARRIVED AT 9:25. AT 9:30, AN EXPLOSION OCCURRED AT THE PROPERTY. THE LINE HIT RESULTED WHEN EXCAVATOR, WHO WAS WORKING FOR THE PROPERTY OWNER, BEGAN DIGGING WITH A BACKHOE NEAR THE FRONT WALL OF THE PROPERTY ON 12/13/22 TO REPAIR A BLOCKED SEWER SERVICE LINE. EXCAVATOR BEGAN DIGGING BEFORE UGI'S LOCATOR ARRIVED TO COMPLETE THE RE-NOTIFY TICKET AND BEFORE UGI WAS ABLE TO CONTACT EXCAVATOR TO DISCUSS THE FACILITY CONFLICTS. THE RESIDENTS AT THE PROPERTY WERE EVACUATED PRIOR TO THE EXPLOSION. THE EXPLOSION INJURED UGI'S FIRST RESPONDER AND A RESIDENT OF AN ADJACENT HOME. BOTH INDIVIDUALS WERE TREATED AT A HOSPITAL AND RELEASED THE SAME DAY. THE SITUATION WAS MADE SAFE BY CLOSING THE MAIN LINE VALVE AT THE END OF THE STREET, SHUTTING OFF GAS TO 14 CUSTOMERS. *ON AUGUST 14, 2025 UGI IS FILING THIS SUPPLEMENTAL AND FINAL REPORT TO CLOSE OUT THIS INCIDENT. AS SET FORTH IN THE TIMELINE OF EVENTS AS DESCRIBED ABOVE, THE EXCAVATOR’S RENOTIFICATION TICKET WAS SUBMITTED AFTER THE EXCAVATOR HAD ALREADY STRUCK AND DAMAGED THE GAS SERVICE LINE. UGI RECEIVED AN EMERGENCY EXCAVATION TICKET ON 12/12/2022 AT 13:17. UGI RESPONDED TO THIS REQUEST THROUGH ITS TICKET MANAGEMENT SYSTEM THE SAME DAY AT 13:18 REMARKING "CONFLICT LINES NEARBY DIRECT CONTACT TO FOLLOW BY FACILITY OWNER". WHILE UGI AVERS THE FACILITIES WERE NOT MARKED BY THE TIME THE EXCAVATOR BEGAN DIGGING, THE EXCAVATOR WAS MADE AWARE THE DAY PRIOR OF FACILITY CONFLICTS AND HAD VISUAL INDICATIONS OF UGI’S GAS METER AND SERVICE PIPING EXITING THE FOUNDATION WALL OF THE BASEMENT WHICH WAS APPROXIMATELY 6.5” LATERALLY FROM THE SEWER CLEAN OUT. THE EXCAVATOR BEGAN EXCAVATION THROUGH THE USE OF MECHANICAL EXCAVATION EQUIPMENT (BACKHOE) WITHOUT EXERCISING DUE CARE, AS REQUIRED IN PENNSYLVANIA THROUGH THE 2017 UNDERGROUND UTILITY LINE PROTECTION LAW (ACT 50). THE EXCAVATOR DID NOT HAVE SUFFICIENT INFORMATION TO SAFELY USE MECHANICAL EXCAVATION EQUIPMENT TO EXCAVATE AT THIS LOCATION AND OTHERWISE DID NOT EMPLOY PRUDENT EXCAVATION TECHNIQUES SUCH AS HAND DUG TEST HOLES, VACUUM EXCAVATIONS, OR SIMILAR DEVICES. AS A RESULT, UGI'S SERVICE LINE WAS STRUCK AND PULLED BY THE HOMEOWNER’S SUBCONTRACTOR EXCAVATOR AT A POINT APPROXIMATELY 6 FEET FROM THE STRUCTURE’S FOUNDATION WALL. WHEN THE SERVICE WAS STRUCK, IT NOT ONLY DAMAGED THE SERVICE AT THE POINT OF CONTACT BUT ALSO INDUCED FRACTURE WITHIN ITS THREADED CONNECTION INSIDE THE BASEMENT AND PULLED THE SERVICE AWAY FROM THE INSIDE METER AND REGULATOR ASSEMBLY. THE FRACTURED SERVICE LINE WAS SIMULTANEOUSLY PULLED INTO THE FOUNDATION WALL SLEEVE AND REMAINED WITHIN THE FOUNDATION WALL ALLOWING PRESSURIZED NATURAL GAS TO ESCAPE INTO THE BASEMENT.
2026-06-30 10:38 | YES | NO | NO | 20230003 | 37594 | 2023-01-19 14:28 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-12-20 08:48 | EASTERN | NO | 2022 | 1014 THIRD STREET | BANGOR | VAN BUREN | MI | 49013 | 42.319 | -86.1167 | [5 empty] | YES |  |  |  | 2022-12-20 13:35 | 1355473 | 1355602 | NATURAL GAS |  | 6.6 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2022-12-20 08:48 | ALLOWED TO BURN OUT |  | 6.6 | NO | 0 | 2022-12-20 08:48 |  |  |  | 2022-12-20 09:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE RISER |  | 1974 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 0.09 |  |  | 2708 | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 143500 | 152568.7295081966625 | 2147 | 2282.683360655736825 | 548 | 582.6318032786883 | 0 | 0 |  | 6.17 | 41 | 28.94468704512372634643377001455604075691 | 0 | 0 | 146236 | 63139.0706391533873663027656477438136827 | 155462.9893591762113513464337700145560408 | 0 | 0 | 1 | 2 | 0 | 1 | 0 | 48 | 48 | 60 | 192.619(A)(2) | 1974-07-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON TUESDAY, DECEMBER 20, 2022, AT APPROXIMATELY 08:48 HOURS, CONSUMERS ENERGY RECEIVED NOTIFICATION FROM EMERGENCY PERSONNEL OF A HOUSE FIRE AT 1014 3RD STREET, BANGOR, (VAN BUREN COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED AT THE SITE AT APPROXIMATELY 09:25 HOURS AND CONFIRMED THE STRUCTURE FIRE WITH A RELEASE AT THE NATURAL GAS EQUIPMENT (METER/RISER). THE GSW ADVISED A DISTRIBUTION CREW WOULD BE NEEDED TO CONTAIN THE BLOWING GAS. THE GSW BEGAN EXCAVATING AT A REMOTE LOCATION NEAR THE PIPELINE IN PREPARATION FOR SQUEEZING THE 5/8-INCH PLASTIC PIPELINE, THE PLASTIC PIPELINE (SERVICE) WAS INSERTED IN A STEEL PIPELINE MAKING IT NECESSARY FOR ADDITIONAL EQUIPMENT UTILIZED BY GAS DISTRIBUTION. DISTRIBUTION ARRIVED ONSITE AT APPROXIMATELY 10:45 HOURS AND SQUEEZED THE PIPELINE STOPPING GAS FROM BLOWING AT APPROXIMATELY 10:48 HOURS. EMERGENCY RESPONDERS WERE ONSITE AND CONFIRMED ONE FATALITY AND MULTIPLE PERSONS REQUIRING MEDICAL ATTENTION WERE TRANSPORTED TO THE LOCAL HOSPITAL. FURTHER INVESTIGATION PERFORMED BY THE MICHIGAN STATE POLICE CONFIRMED THE RELEASE AT THE NATURAL GAS EQUIPMENT (METER/RISER) WAS NOT THE PRIMARY CAUSE OF THE FIRE. THE NATURAL GAS EQUIPMENT WAS COMPROMISED BY THE STRUCTURE FIRE RESULTING IN A RELEASE AT THE NATURAL GAS EQUIPMENT. THIS REPORT IS BEING SUBMITTED BECAUSE IT CANNOT BE DETERMINED IF THE SECONDARY RELEASE AT THE NATURAL GAS FACILITIES CONTRIBUTED TO THE FATALITY.
2026-06-30 10:38 | NO | YES | NO | 20230004 | 37605 | 2023-01-20 15:54 | ORIGINAL FINAL | 18408 | DOMINION ENERGY SOUTH CAROLINA, INC. | 601 TAYLOR ROAD | CAYCE | SC | 29033 | 2022-12-15 16:08 | EASTERN | NO | 2022 | ROSEWOOD DRIVE / BELTLINE BLVD | COLUMBIA | RICHLAND | SC | 29205 | 33.9879 | -80.9832 |  |  |  | YES | [5 empty] | 2022-12-15 17:32 | 1355104 | 1355199 | NATURAL GAS |  | 1613 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-12-15 16:08 |  |  |  | 2022-12-15 16:57 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1980 | UNKNOWN | [7 empty] | STEEL |  | FURNACE BUTT WELDED |  | 0.25 | [6 empty] | OTHER | [8 empty] | BROKEN RELIEF VALVE FROM VEHICLE IMPACT | CLASS 3 LOCATION | 0 | 0 | 135265 | 143813.304508196665875 | 0 | 0 | 0 | 0 |  | 8.36 | 13485 | 9519.978165938864628820960698689956331878 | 0 | 0 | 148750 | 66150.167476197316182751091703056768559 | 153333.2826741355305038209606986899563319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 145 | 175 | 192.621 M | 1980-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE INCIDENT WAS IMPACT BY A MOTOR VEHICLE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  | YES |  |  |  | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 35 | YES |  | YES | [140 empty] | JOHNNIE WALLER | ENGINEER III - COMPLIANCE | johnnie.waller@dominionenergy.com | 803-491-4644 |  | ASHLEY MCJUNKIN | ashley.mcjunkin@dominionenergy.com | 803-457-0541 | CYNTHIA OSTRANDER | DIRECTOR - GAS OPERATIONS | 803-530-4135 | cynthia.ostrander@dominionenergy.com | AN INCIDENT WAS REPORTED AT THE INTERSECTION OF ROSEWOOD DRIVE & BELTLINE BLVD. WHERE A VEHICLE CRASHED INTO ONE OF DOMINION ENERGY REGULATING STATIONS. OPERATOR RESOURCES WERE DISPATCHED TO THE SCENE AND REPAIR PLAN WAS INITIATED. THE LEAK WAS STOPPED AND FINAL REPAIRS WERE COMPLETED APPROXIMATELY 50 MINUTES FROM INITIAL REPORT. AT THIS TIME, THERE WAS NO LOSS OF CUSTOMERS AND NO ONE WAS INJURED RELATED TO RELEASE OF GAS. THE OFFICE OF REGULATORY STAFF FOR SOUTH CAROLINA WAS NOTIFIED AROUND 4:30 P.M. THE PRELIMINARY COST ESTIMATE WAS STATED TO EXCEED THE $129K THRESHOLD, THEREFORE TRIGGERING AN INITIAL 1-HR NOTIFICATION AND 48-HR TO THE NRC. THIS CALL WAS MADE AT APPROXIMATELY 5:32 P.M. (NRC REPORT # 1355104 AND 1355199). THE COST ESTIMATE WAS APPROXIMATELY $35,000 ON 12/22/2022, BUT SUBSEQUENTLY, ADDITIONAL COST WERE COLLECTED AFTER THE INITIAL ESTIMATE WHICH PUT THE FINAL COST OVER THE FEDERAL THRESHOLD. THE DATE OF DETERMINING COST THRESHOLD BEING EXCEEDED WAS 12/22/2022, WHICH WAS THE DATE USED FOR DETERMINING THE SUBMITTAL TIMEFRAME FOR THIS REPORT. RECORDED ON OUR LDF REPORT # 548785
2026-06-30 10:38 | NO | YES | NO | 20230005 | 37961 | 2023-01-27 12:12 | SUPPLEMENTAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2022-12-29 15:09 | EASTERN | NO | 2022 | 1210 ROBBINS AVENUE | NILES | TRUMBULL | OH | 44446 | 41.1828 | -80.7425 |  |  |  | YES |  |  |  | YES | CUT AT MAIN | 2022-12-29 16:07 | 1356293 | 1356377, 1356388 (corrected 48 hour update) | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-12-29 15:09 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 0 | 2022-12-29 15:49 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-12-29 15:53 | 2022-12-29 16:23 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNDER INVESTIGATION | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNDER INVESTIGATION | CLASS 3 LOCATION | 176100 | 187228.9426229507475 | 200 | 212.639344262295 | 5000 | 5315.983606557375 | 5000 | 5315.983606557375 | UPDATE ESTIMATED COST DUE TO JOINT SITE EXAMINATION WITH HOMEOWNER'S INSURANCE. | 6.89 | 0 | 0 | 0 | 0 | 186300 | 80429.680327868883 | 198073.5491803277925 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.48 | 0.47 | 1 | 192.623 | 1926-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 10.8 |  | NO |  |  |  |  | OTHER | PUBLIC UTILITIES COMMISSION STAFF MEMBER |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | ALLISON WALTERS-THOMPSON | MANAGER GAS OPERATIONS | a.walters-thompson@dominionenergy.com | 2167899152 |  | ALLISON S WALTERS-THOMPSON | a.walters-thompson@dominionenergy.com | 12167899152 | ALLISON S WALTERS-THOMPSON | MANAGER GAS OPERATIONS | 12167899152 | a.walters-thompson@dominionenergy.com | THE FIRE/EXPLOSION THAT OCCURRED ON DECEMBER 29, 2022 IS STILL CURRENTLY UNDER INVESTIGATION AS TO ITS CAUSE, SO RESPONSES TO CERTAIN SECTIONS OF THIS FORM ARE UNKNOWN OR LEFT BLANK. ALTHOUGH SECTION A21 IS CHECKED, YES, THE SOURCE OF IGNITION IS NOT YET DETERMINED. A JOINT SITE EXAMINATION TOOK PLACE ON FEBRUARY 8, 2022, AND PHYSICAL EVIDENCE FROM INSIDE THE SUBJECT PROPERTY IS BEING PRESERVED BY THE HOMEOWNER'S INSURANCE COMPANY FOR POTENTIAL LABORATORY EXAMINATION. AS OF THIS SUPPLEMENTAL REPORT, NO LABORATORY TESTING HAS BEEN CONDUCTED OR SCHEDULED FOR THE NON-JURISDICTIONAL PIPING. THE INVESTIGATION REMAINS ONGOING, AND THE APPARENT CAUSE AND CONTRIBUTING CAUSES (IF ANY) OF THIS INCIDENT ARE YET TO BE DETERMINED.
2026-06-30 10:38 | NO | NO | NO | 20230006 | 37843 | 2023-02-01 18:30 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2023-01-05 06:22 | PACIFIC | NO | 2023 | 2761 ROLLINGWOOD DRIVE | SAN PABLO | CONTRA COSTA | CA | 94806 | 37.9655 | -122.3345 | [5 empty] | YES |  |  |  | 2023-01-06 10:32 | 1356987 | 1357066 | NATURAL GAS |  | 5358 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 3 | 2023-01-05 06:22 |  |  |  | 2023-01-05 06:44 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1943 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 4 | 4 |  | CLASS 3 LOCATION | 0 | 0 | 13571 | 14120.763757420186183 | 596 | 620.144071875501508 | 0 | 0 |  | 6 | 32148 | 28042.7697841726618705035971223021582734 | 0 | 0 | 46315 | 28824.6450264142940177194244604316546763 | 42783.6776134683495615035971223021582734 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 54 | 54 | 60 | 192.619(A)(3) | 1966-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPE RUPTURED AS A RESULT OF NATURAL FORCE DAMAGE, EARTH MOVEMENT DUE TO HEAVY RAIN. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  |  |  | YES | HEAVY RAIN (BOMB CYCLONE + ATMOSPHERIC RIVER) | [213 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | r1dj@pge.com | 510/298-7063 |  |  |  |  | SUSIE RICHMOND | GAS REGULATORY COMPLIANCE MANAGER | 925/786-0267 | gsr8 | ON JANUARY 6, 2023, AT 09:50, PG&E INCIDENT ON-CALL PERSONNEL CONFIRMED EXTENT OF CONDITION OF AN UNINTENTIONAL RELEASE OF GAS DUE TO A COMPLETELY SEVERED PIPE. ON JANUARY 5, AT APPROXIMATELY 06:22, A 4" STEEL MAIN NEAR OUR FACILITIES IN SAN PABLO BROKE AS A RESULT OF NATURAL FORCE DAMAGE, EARTH MOVEMENT DUE TO HEAVY RAIN, RESULTING IN A GAS LEAK. PG&E CREWS CONDUCTED REPAIRS. THIS SECTION OF MAIN CROSSES THE HAYWARD FAULT LINE, AND GEOSCIENCES EXAMINED THE AREA. AFTER THEIR INSPECTION IT WAS DETERMINED THAT CREEP HAS LOADED THE PIPE SINCE IT WAS INSTALLED. BASED ON A NEARBY USGS MONITORING STATION, THE AREA WHERE THE FAILURE OCCURRED CREEPS AT A RATE OF ABOUT 5 MM/YEAR. THE PIPE RUPTURED AT A PARTIAL PENETRATION GIRTH WELD. THE ORIENTATION OF THE PIPE RELATIVE TO THE FAULT AND THE SENSE OF MOVEMENT ON THE FAULT CAUSES THE PIPE TO BE LOADED IN EXTENSION, WHICH IS CONSISTENT WITH THE SEPARATION OF THE PIPE THAT WAS OBSERVED AT THE BREAK. GIVEN THAT NO OTHER BREAKS OCCURRED WHERE DISTRIBUTION MAINS IN THE AREA INTERSECT THE HAYWARD FAULT, PG&E CONCLUDES THAT THE BREAK WAS DUE TO A COMBINATION OF HEAVY RAIN FALL AND LONG-TERM CREEP LOADING. A DETAILED ASSESSMENT OF HISTORICAL LEAKS IN THE AREA DID NOT SHOW A CORRELATION BETWEEN LEAKS IN THE AREA AND THE HAYWARD FAULT. NO MEDIA WAS REPORTED ONSITE. THE FIRE DEPARTMENT AND POLICE WERE ONSITE. NO FATALITIES OR INJURIES WERE REPORTED. THREE HOMES WERE EVACUATED, AND GAS SERVICE WAS INTERRUPTED FOR EIGHT CUSTOMERS AS PART OF THE ISOLATION STRATEGY. THIS INCIDENT WAS REPORTED TO DOT (NRC #1356987/ 1357066) AND CPUC ONCE IT WAS CONFIRMED THAT THE UNINTENDED GAS LOSS WAS OVER 3 MILLION CUBIC FEET.
2026-06-30 10:38 | NO | YES | YES | 20230007 | 38650 | 2023-02-10 11:11 | SUPPLEMENTAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2023-01-18 11:57 | CENTRAL | NO | 2023 | 4616 CORTEZ CIRCLE | MANDAN | MORTON | ND | 58554 | 46.8667 | -100.9446 | [5 empty] | YES |  |  |  | 2023-01-18 13:04 | 1357989 | 1358143 | NATURAL GAS |  | 8.21 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2023-01-18 11:57 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 8.21 | YES | 2 | 2023-01-18 11:57 |  |  |  | 2023-01-18 12:26 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2017 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | 0.113 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 105000 | 109253.569709610165 | 270 | 280.93775068185471 | 1100 | 1144.5612064816303 | 0 | 0 |  | 6.74 | 55 | 47.97661870503597122302158273381294964029 | 0 | 0 | 106425 | 44981.3800140699331146043165467625899281 | 110727.0452854786859812230215827338129496 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 30 | 30 | 60 | 192.619(A)(2) | 1983-09-30 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 15 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THERE WAS A CRACKED NIPPLE BETWEEN THE RISER VALVE AND THE REGULATOR. THE ANALYSIS CONCLUDES THAT THE NIPPLE DAMAGE WAS DUE TO AN UNKNOWN OUTSIDE FORCE. IT IS UNKNOWN WHEN THE NIPPLE DAMAGE OCCURRED. | [154 empty] | SAMANTHA CALDWELL | MANAGER POLICY AND PROCEDURE | samantha.caldwell@mdu.com | 208-509-2140 |  | SAMANTHA CALDWELL | samantha.caldwell@mdu.com | 208-509-2140 | JOSH SANDERS | DIRECTOR POLICY AND PROCEDURE | 701-222-7773 | josh.sanders@mdu.com | ON JANUARY 18, 2023, MDU RESPONDED TO A STRUCTURE FIRE/EXPLOSION AT 4616 CORTEZ CIRCLE IN MANDAN, ND. AN UNINTENTIONAL RELEASE AND IGNITION OF NATURAL GAS OCCURRED. MDU PERSONNEL SECURED THE RELEASE BY SQUEEZING OFF THE SERVICE LINE. ON JANUARY 19, 2023, THE MANDAN FIRE DEPARTMENT AND ATF CONDUCTED AN INVESTIGATION AT 4616 CORTEZ CIRCLE IN MANDAN, ND, WITH REPRESENTATIVES FROM MDU AND THE ND PSC PRESENT. DURING EXAMINATION OF THE STRUCTURE'S INTERIOR, APPROXIMATELY TEN (10) FEET DOWNSTREAM OF THE GAS METER, THE NON-JURISDICTIONAL GAS PIPING WAS FOUND TO BE SEPARATED AT A CONNECTION POINT. A NATURAL GAS RANGE AND NATURAL GAS FURNACE WERE THE ONLY TWO FUEL FIRED APPLIANCES LOCATED IN THE STRUCTURE. THE CONNECTIONS AND PIPING TO THE RANGE AND FURNACE APPEARED TO BE INTACT. THE HEAT SOURCE OR CAUSE OF IGNITION WAS INCONCLUSIVE. FOLLOWING THE INVESTIGATION ON JANUARY 19, 2023, MDU MADE ATTEMPTS TO COORDINATE THE INVESTIGATION OF JURISDICTIONAL FACILITIES WITH ALL PARTIES. AFTER FAILED ATTEMPTS TO COORDINATE, THE COMPANY PROVIDED NOTIFICATION TO ALL PARTIES THAT AN INVESTIGATION WOULD COMMENCE ON AUGUST 15, 2023. MDU AND THE NORTH DAKOTA GAS PIPELINE SAFETY PROGRAM MANAGER/INSPECTOR CONDUCTED AN INVESTIGATION OF JURISDICTIONAL FACILITIES AT 4616 CORTEZ CIRCLE IN MANDAN, ND. A PRESSURE TEST WAS PERFORMED ON THE SERVICE LINE. THE PRESSURE TEST PASSED, HOLDING AT SYSTEM PRESSURE. ABOVE GROUND PIPING WAS INTACT UP TO THE RISER VALVE. THERE WAS A CRACKED NIPPLE BETWEEN THE RISER VALVE AND THE REGULATOR. THE ANALYSIS CONCLUDES THAT THE NIPPLE DAMAGE WAS DUE TO AN UNKNOWN OUTSIDE FORCE. IT IS UNKNOWN WHEN THE NIPPLE DAMAGE OCCURRED. MDU WAS ALLOWED TO INVESTIGATE JURISDICTIONAL FACILITIES ONLY. OCTOBER 11, 2023 - CORRECTED TIME IN FIELD A4. UPDATED FROM 12:26 TO 11:57.
2026-06-30 10:38 | NO | YES | NO | 20230008 | 37951 | 2023-02-10 19:46 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2023-01-10 15:49 | CENTRAL | NO | 2023 | 1520 BIG TIMBER RD | ELGIN | KANE | IL | 60123 | 42.0585 | -88.3153 | YES | [5 empty] | YES |  |  | 2023-01-11 11:45 | 1357409 | 1357625 1357628 | NATURAL GAS |  | 1830 | 21 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 50 | 2023-01-10 15:49 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-01-10 16:03 | 2023-01-10 16:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 114 | NO | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1958 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 1 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 353550 | 367872.37686507308415 | 284225 | 295739.008102037610925 | 0 | 0 |  | 6.59 | 12060 | 10519.9640287769784172661870503597122302 | 138 | 120.377697841726618705035971223021582734 | 649973 | 278131.66635695138871924460431654676259 | 674251.7266937294001109712230215827338129 | 12 | 0 | 0 | 0 | 0 | 0 | 6 | 160 | 160.6 | 165 | 192.621 M | 1979-06-30 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS MAIN AT INCIDENT LOCATION IS NOT MONITORED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | YES |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | A22299449 | JULIE OTHER JULIE DIG #S - A223211418 A223402053 |  | CONTRACT LOCATOR | YES | YES | 41 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JOSE L DELREAL | MANAGER OPS QA | jdelrea@southernco.com | 630-918-4934 |  |  |  |  | LETICIA QUEZADA | MANAGER COMPLIANCE AND QA | 630-514-2036 | lquezad@southernco.com | THIRD PARTY CONTRACTOR, VERITA TELECOMMUNICATIONS CORP, WAS DIRECTIONAL DRILLING ALONG THE EAST SIDE OF MCLEAN BLVD, AT/NEAR THE INTERSECTION OF BIG TIMBER RD. THE VERITA HDD CREW WAS DRILLING ACROSS BIG TIMBER RD. A VERITA CREW-PERSON CALLED A NICOR GAS EMPLOYEE AT 15:49 ON JANUARY 10, 2023, INDICATING THEY SMELLED GAS. COMPANY EMERGENCY RESPONDERS WERE DISPATCHED IN RESPONSE TO THE NOTIFICATION. UPON EVALUATION, IT WAS DETERMINED THAT A 12-INCH MAIN HAD BEEN DAMAGED AND THE SYSTEM COULD BE ISOLATED USING TWO EXISTING VALVES (EAST & WEST OF THE DAMAGE) AND A LINE STOP FITTING (NORTH OF THE DAMAGE). THE RELEASE WAS SECURED AT APPROXIMATELY 22:42 ON JANUARY 11, 2023. NICOR INSTALLED A 250-FOOT LONG, 4-INCH BYPASS TO MINIMIZE THE RISK OF ADDITIONAL GAS SERVICE INTERRUPTION TO CUSTOMERS THAT WERE NOT ALREADY IMPACTED BY THE INCIDENT. THE BYPASS WAS IN SERVICE AT APPROXIMATELY 03:00 (24-HOUR TIME) ON JANUARY 12, 2023. THE DAMAGED SECTION OF MAIN WAS EXPOSED AND EXAMINED, AND A CLAMP WAS INSTALLED TO REPAIR THE DAMAGED SECTION. THE SYSTEM WAS RETURNED TO SERVICE IN SECTIONS, WITH THE LAST SECTION RETURNING TO NORMAL OPERATION BY 21:46 ON JANUARY 12, 2023. AT THE TIME OF THE INCIDENT, THERE WAS A VALID ONE-CALL TICKET AND MARKINGS WERE ACCURATE. THE CONTRACTOR INDICATED THEY POTHOLED DOWN TO 4.5 FEET AND OBSERVED THE TOP OF WHAT THEY THOUGHT WAS A GAS MAIN. THERE WAS NO EVIDENCE THAT THE CONTRACTOR HAD EXPOSED THE 12-INCH GAS MAIN TO OBSERVE THE DRILLING EQUIPMENT PASS THE GAS MAIN DURING THEIR OPERATION. THE DAMAGE TO THE 12-INCH MAIN OCCURRED AT A DEPTH OF 9.5 FEET.
2026-06-30 10:38 | NO | YES | NO | 20230009 | 37866 | 2023-02-14 09:13 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | 3600 MIDTOWN DR. | TAMPA | FL | 33607 | 2023-01-14 13:02 | EASTERN | NO | 2023 | 1906 PROMENADE WAY | JACKSONVILLE | DUVAL | FL | 32207 | 30.3014 | -81.6437 | [6 empty] | YES |  |  | 2023-01-14 13:02 | 1357662 | 1357780 | NATURAL GAS |  | 9.25 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-01-12 08:44 | YES | OPERATOR | 2023-01-13 08:16 | 2023-01-12 09:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 96 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | UNKNOWN |  |  |  |  | 8 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 72103 | 75023.906064495445019 | 165852 | 172570.695652173953196 | 65078 | 67714.321995828669694 | 0 | 0 |  | 10 | 93 | 81.1241007194244604316546762589928057554 | 0 | 0 | 303126 | 128100.3081512649893693309352517985611511 | 315390.0478132174923694316546762589928058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 220 | 250 | 192.619(A)(4) | 1999-10-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR HAIR-LINE CRACK WAS IDENTIFIED WITH NO IMPACT TO ALARMS WITHIN THE SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2022-09-27 | YES | 1999 | 250 | [10 empty] | YES | YES | CITY STREET | [12 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  |  | UNKNOWN/OTHER |  | NO |  | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [144 empty] | YES | [25 empty] | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | rharris@tecoenergy.com | 407-420-6667 |  |  |  |  | KRISTOPHER KELLEY | DIRECTOR OF SAFETY | 813-228-1784 | kjkelley@tecoenergy.com | PEOPLES GAS RECEIVED A LEAK REPORT ON 1/12/23, RESPONDED TO THE SCENE AND BEGAN AN INVESTIGATION. A DETERMINATION OF THE SOURCE AND LOCATION WAS IDENTIFIED, AND THE SCENE WAS MADE SAFE WITH FIRST RESPONDER SUPPORT. BASED ON THE LOCATION OF THE IDENTIFIED LEAK, DEPTH OF PIPELINE AND POTENTIAL CUSTOMER LOSS, THE CORRECTIVE ACTION PLAN TO MAKE THE SCENE SAFE WAS TO INSTALL A TEMPORARY BY-PASS TO REMEDIATE THE IDENTIFIED LEAK. THE DAMAGED PIPE WAS ISOLATED, AND THE LEAKAGE STOPPED. A NEW PRETESTED SECTION OF PIPE WAS INSTALLED FOR PERMANENT REPAIR, AND THE TEMPORARY BYPASS WAS CAPPED AND TAKEN OUT OF SERVICE. DURING THE ASSESSMENT, A PREVIOUS UNREPORTED LONGITUDINAL GOUGE (EXCAVATION DAMAGE) WAS IDENTIFIED ON THE 8" PIPELINE, THAT OVER TIME RESULTED IN A LEAK. LEAK SURVEY PERFORMED ON 9/27/2022 DID NOT IDENTIFY A LEAK AT THIS LOCATION. PART G, #9 IS "NO" DUE TO LIMITATIONS OF THE FORM, IN FACT IS UNKNOWN WHETHER A LOCATE TICKET WAS CALLED OR NOT AT THE TIME OF THE EXCAVATION/DAMAGE.
2026-06-30 10:38 | NO | YES | NO | 20230010 | 37778 | 2023-03-03 13:29 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2023-02-03 17:05 | CENTRAL | NO | 2023 | 136 E. LAKE ST | BLOOMINGDALE | DUPAGE | IL | 60108 | 41.9572 | -88.0754 | [5 empty] | YES |  |  |  | 2023-02-03 19:03 | 1359221 | 1359323 | NATURAL GAS |  | 201.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-02-03 17:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 201.4 | NO | 0 | 2023-02-03 17:17 |  |  |  | 2023-02-03 17:48 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1993 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | OTHER | PE RISER- STEEL-ALUMINUM REGULATOR/METER | [9 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 1 |  | CLASS 3 LOCATION | 1255000 | 1305840.285576769115 | 200 | 208.1020375421146 | 2207 | 2296.405984277234611 | 0 | 0 |  | 6.12 | 1233 | 1075.548561151079136690647482014388489209 | 0 | 0 | 1258640 | 532142.0194257878804951294964028776978417 | 1309420.34215973954334769064748201438849 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 54.8 | 58 | 60 | 192.619(A)(2) | 1993-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | YES | UNKNOWN | PASSENGER CAR | DRIVEWAY | 25 | YES | YES | [141 empty] | LETICIA QUEZADA | MANAGER COMPLIANCE AND QA | lquezad@southernco.com | 6305142036 |  |  |  |  | LETICIA QUEZADA | MANAGER COMPLIANCE AND QA | 6305142036 | lquezad@southernco.com | A BANK DRIVE-THRU CUSTOMER LOST CONTROL OF HER VEHICLE, CRASHING THROUGH THE BUILDING BRICK WALL. THE COLLISION DAMAGED THE METER SET LOCATED IN FRONT OF THE WALL, CAUSING A RELEASE OF NATURAL GAS INTO THE ATMOSPHERE. THE NATURAL GAS IGNITED, AND THE FIRE SPREAD INTO THE BANK BUILDING. THE DRIVER OF THE VEHICLE WAS NOT INJURED AND EXITED THE VEHICLE PRIOR TO THE GAS IGNITION.
2026-06-30 10:38 | NO | YES | YES | 20230011 | 37940 | 2023-03-10 14:23 | SUPPLEMENTAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2023-02-10 04:58 | MOUNTAIN | NO | 2023 | 1414 DEGEEST DRIVE | RAPID CITY | PENNINGTON | SD | 57703 | 44.0725 | -103.1423 | [5 empty] | YES |  |  |  | 2023-02-10 06:00 | 1359693 | 1359810 | NATURAL GAS |  | 22 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 4 | 4 | YES | 2023-02-10 04:24 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 22 | NO | 8 | 2023-02-10 04:58 |  |  |  | 2023-02-10 04:58 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2000 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ANODELESS SERVICE RISER | [9 empty] | OTHER | [8 empty] | VEHICLE STRUCK METER SET, SHEARING OFF RISER AT GROUND LEVEL. | CLASS 3 LOCATION | 750000 | 780382.64078292975 | 500 | 520.2550938552865 | 2000 | 2081.020375421146 | 0 | 0 |  | 6.284 | 138 | 120.377697841726618705035971223021582734 | 0 | 0 | 752638 | 318036.2314502642012410071942446043165468 | 783104.2939500479091187050359712230215827 | 0 | 0 | 2 | 0 | 0 | 3 | 0 | 50 | 50 | 55 | 192.619(A)(2) | 2000-11-06 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 9 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | NO | [5 empty] | YES | 80 | SMALL TRUCK | ROADWAY | 62 | NO | [118 empty] | YES | [23 empty] | DANNY L. HOOD | MANAGER POLICY AND PROCEDURE | danny.hood@mdu.com | 7015162749 |  | TOBY BORDEWYK | toby.bordewyk@mdu.com | 6053554054 | DANNY L. HOOD | MANAGER POLICY AND PROCEDURE | 7015162749 | danny.hood@mdu.com | ON FEBRUARY 10, 2023, AT 04:24 AM, MONTANA DAKOTA UTILITIES (MDU) RECEIVED A CALL REPORTING A HOUSE FIRE AT 1414 DEGEEST DRIVE IN RAPID CITY SOUTH DAKOTA. UPON ARRIVAL THE MDU SERVICE TECHNICIAN DETERMINED A VEHICLE TRAVELING IN A RESIDENTIAL SUBDIVISION LEFT THE ROADWAY AND STRUCK AN OUTSIDE METER SET ON THE HOUSE, SHEARING OFF THE RISER AT GROUND LEVEL, CAUSING A RELEASE OF NATURAL GAS THAT IGNITED. THE DRIVER OF THE VEHICLE DID NOT SURVIVE, AND 4 RESIDENTS OF THE HOUSE WERE TRANSPORTED TO THE HOSPITAL. THE FOUR RESIDENTS OF 1414 DEGEEST DR WERE EVACUATED, OCCUPANTS AT 1426 DEGEEST DR AND 1392 DEGEEST DR WERE ALSO EVACUATED. NUMBER OF PEOPLE EVACUATED IN PART A IS AN ESTIMATE AS NUMBER OF OCCUPANTS FROM 1426 DEGEEST AND 1392 DEGEEST IS UNKNOWN AT THE TIME OF THIS REPORT. GAS SERVICE TO 1414 DEGEEST DR AND 1426 DEGEEST DR WAS LOST DURING THE INCIDENT. GAS SERVICE TO 1426 DEGEEST DR WAS RESTORED AT APPROXIMATELY 10:00 AM. GAS SERVICE TO 1414 DEGEEST DR HAS BEEN RETIRED. THE HOME AT 1414 DEGEEST WAS A TOTAL LOSS. THE HOUSE AT 1426 DEGEEST SUSTAINED DAMAGE, A CAMPER AT THIS LOCATION WAS A TOTAL LOSS. THREE 3 VEHICLES SUSTAINED DAMAGE. UPDATE: APRIL 12, 2023- THE POLICE REPORT INDICATED THE SPEED OF THE VEHICLE WAS ESTIMATED AT 80 MPH USING INFORMATION FROM A WITNESS. POLICE REPORT INDICATES THE INJURIES TO THE DRIVER OF THE VEHICLE AND THE RESULTING FIRE PROVED TO BE FATAL. NO INDICATION OF THE CAUSE OF THE FATALITY IN THE POLICE OR FIRE REPORT. THE FIRE REPORT INDICATES ACCESS TO THE VEHICLE AFTER THE GAS LINE WAS CLAMPED AND THE FIRE WAS CONTROLLED ALLOWING RECOVERY OF THE VICTIM. THE NUMBER OF REPORTED INJURIES VARIES FROM 2 TO 5 INDIVIDUALS ON THE POLICE, FIRE, AND COMPANY FIRST RESPONDER REPORTS. NO INFORMATION IN THE REPORTS COULD CONFIRM IF THE INJURIES REQUIRED HOSPITALIZATION. THE HOUSES AT 1414 DEGEEST DR, 1426 DEGEEST AND 1392 DEGEEST DR. WERE EVACUATED BY UNKNOWN PERSONS. THE NUMBER OF RESIDENTS EVACUATED IS AN ESTIMATE AS NO SPECIFIC INFORMATION ON THE NUMBER OF EVACUATIONS IS INCLUDED IN THE POLICE OR FIRE REPORTS. THE POLICE REPORT INDICATES TOTAL LOSS OR DAMAGE TO 1 CAMPER TRAILER, 1 UTILITY TRAILER, AND 6 VEHICLES. ESTIMATED VALUE OF TRAILERS AND VEHICLES - $100,000. UPDATED THE ESTIMATED PROPERTY DAMAGE INFORMATION, USING INFORMATION FROM POLICE AND FIRE REPORTS. 1414 DEGEEST DR. - $500,000 INCLUDING POSSESSIONS, 1426 DEGEEST DR. - $100,000 AND 1392 DEGEEST DR. - $50,000 TOTAL ESTIMATED LOSS TO NON-OPERATOR - $750,000
2026-06-30 10:38 | NO | YES | NO | 20230012 | 37877 | 2023-03-22 16:09 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2023-02-20 16:00 | CENTRAL | NO | 2023 | 2101 TEXAS AVE | COLLEGE STATION | BRAZOS | TX | 77840 | 30.612 | -96.3147 | [5 empty] | YES |  |  |  | 2023-02-21 18:07 | 1360544 | 1360697 | NATURAL GAS |  | 1058.34 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 8 | 2023-02-20 16:00 | YES | OPERATOR | 2023-02-20 16:00 | 2023-02-20 16:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 180 | YES | YES |  |  |  |  | YES | CASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2004 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 113589 | 118190.511711856276497 | 14330 | 14910.51098989251109 | 0 | 0 |  | 7.7224 | 8173 | 7129.325539568345323741007194244604316547 | 0 | 0 | 136092 | 59853.3154782447204172014388489208633094 | 140230.3482413171329107410071942446043165 | 1 | 0 | 10 | 0 | 0 | 17 | 1 | 34 | 34 | 50 | 192.619(A)(2) | 2004-10-14 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2354567778 | TEXAS 811 |  | CONTRACT LOCATOR | YES | YES | 24 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | LUIS CISNEROS | COMPLIANCE SUPERVISOR | luis.cisneros@atmosenergy.com | 979-324-8823 |  |  |  |  | JEFF KNIGHTS | SR VP TECHNICAL AND OPERATING SERVICES | 214-206-2701 | jeffrey.knights@atmosenergy.com | ON FEBRUARY 20, 2023, AT 4PM, A THIRD-PARTY CONTRACTOR WAS DIRECTIONAL DRILLING AT 2101 TEXAS AVENUE / RICHARDS ST, COLLEGE STATION AND BORED INTO ATMOS ENERGY'S 2-INCH POLY MAIN AT A DEPTH OF 15 FEET. THE TECHNICIAN ARRIVED ON THE SCENE AND CONFIRMED THE LEAK AT 4:30PM. COLLEGE STATION FIRE DEPARTMENT EVACUATED 8 STRUCTURES AND GAS WAS SUBSEQUENTLY TURNED OFF TO 10 HOUSES AND 1 COMMERCIAL ENTITY ON RICHARDS ST. UPON ARRIVAL ON THE SCENE, ATMOS ENERGY'S CREW WORKED CONTINUOUSLY TO CONDUCT THE NECESSARY EXCAVATION TO LOCATE AND REPAIR THE DAMAGED LINE. ON FEBRUARY 21, 2023 AT 2:30PM, A SQUEEZE TOOL WAS INSTALLED ON THE 2-INCH POLY PIPE TO STOP GAS FLOW WHERE THE PIPE WAS DAMAGED. AT 5PM, THE 2-INCH MAIN WAS REPLACED AND GAS SERVICE WAS RESTORED TO THE 11 CUSTOMERS. REGARDING PART A QUESTION 22 - THIS NUMBER REFERS TO THE 8 STRUCTURES THAT WERE EVACUATED AND NOT PEOPLE. THE TOTAL OF PEOPLE THAT WERE EVACUATED IS NOT KNOWN.
2026-06-30 10:38 | NO | YES | NO | 20230013 | 37860 | 2023-03-23 10:39 | ORIGINAL | 32013 | AMERIGAS PROPANE LP | 500 N. GULPH RD. | KING OF PRUSSIA | PA | 19406 | 2023-03-01 22:30 | PACIFIC | NO | 2023 | 65 HAYS STREET | BRIDGEPORT | MONO | CA | 93517 | 38.254 | -119.2268 |  |  |  | YES | [5 empty] | 2023-03-02 13:33 | 1361287 |  | PROPANE GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-03-01 22:30 |  |  |  | 2023-03-03 08:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | COOPERATIVE |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN LOCATION - UNDER INVESTIGATION | CLASS 3 LOCATION | 130000 | 135266.32440237449 | 300 | 312.1530563131719 | 0 | 0 | 0 | 0 | ESTIMATE NOT AWARE OF AN ACTUAL DOLLAR AMOUNT | 3 | 0 | 0 | 0 | 0 | 130300 | 55052.9520295203053 | 135578.4774586876619 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 10 | 192.619(A)(3) | 1965-07-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | ON 3/1/2023 AROUND 22:30 LOCAL TIME SYSTEM MANAGEMENT WAS NOTIFIED BY EMERGENCY RESPONDERS THAT AN AUTO PARTS BUILDING THAT HAD L.P GAS SERVICE WAS ON FIRE. EMERGENCY RESPONDERS THEN CLOSED THE RISER SERVICE VALVE AND SECURED/LOCKED IT AT THAT TIME. CAUSE OF FIRE IS UNCLEAR, ESTIMATED COST OF DAMAGES IS UNKNOWN. THE INCIDENT IS UNDER INVESTIGATION, THIS FORM IS SUBMITTED AS A PRECAUTIONARY MEASURE. | [47 empty] | BILL L RUNYANS | FIELD SAFETY COMPLIANCE MANAGER | bill.runyans@amerigas.com | 2564591078 |  | KYLE MUIR | kyle.muir@amerigas.com | 7067090195 | BILL L RUNYANS | FIELD SAFETY COMPLIANCE MANAGER | 2564591078 | bill.runyans@amerigas.com | ON 3/1/2023 AROUND 22:30 LOCAL TIME SYSTEM MANAGEMENT WAS NOTIFIED BY EMERGENCY RESPONDERS THAT AN AUTO PARTS BUILDING THAT HAD L.P GAS SERVICE WAS ON FIRE. EMERGENCY RESPONDERS THEN CLOSED THE RISER SERVICE VALVE AND SECURED/LOCKED IT AT THAT TIME. CAUSE OF FIRE IS UNCLEAR, ESTIMATED COST OF DAMAGES IS UNKNOWN. THE INCIDENT IS UNDER INVESTIGATION, THIS FORM IS SUBMITTED AS A PRECAUTIONARY MEASURE.
2026-06-30 10:38 | NO | YES | NO | 20230014 | 37863 | 2023-03-23 15:41 | ORIGINAL FINAL | 13420 | NEW YORK STATE ELECTRIC & GAS CORP | 180 SOUTH CLINTON AVENUE | ROCHESTER | NY | 14604 | 2022-02-02 08:59 | EASTERN | NO | 2022 | 2592 CARMEL AVE | BREWSTER | PUTMAN | NY | 10509 | 41.3993 | -73.625 |  |  |  | YES | [5 empty] | 2022-02-03 17:45 | 1328021 | 1328415 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-02-02 08:20 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 3 | 2022-02-02 08:20 | YES | OPERATOR | 2022-02-02 08:30 | 2022-02-02 07:07 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | 2X1 MECHANICAL TAPPING TEE | 1997 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | 425000 | 451858.606557376875 | 100 | 106.3196721311475 | 5000 | 5315.983606557375 | 0 | 0 |  | 37.09 | 37 | 26.1208151382823871906841339155749636099 | 0 | 0 | 430137 | 185704.6097191400709854439592430858806405 | 457307.0306512036798871906841339155749636 | 1 | 0 | 2 | 0 | 0 | 1 | 1 | 52 | 52 | 56 | 192.619(A)(2) | 1997-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | BOLTED |  | TAPPING TEE |  | PERFECTION | UNKNOWN | PLASTIC |  | PULLED OUT | [21 empty] | YES | TEE NOT INSTALLED IN ACCORDANCE WITH MANUFACTURER INSTRUCTIONS | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | DAN BLANCE | ENGINEER | dcblance@nyseg.com | 607-240-3821 |  |  |  |  | BARRY KACHMARYK | MANAGER GAS ENGINEERING | 585-315-1227 | barry_kachmaryk@rge.com | ON THE MORNING OF FEBRUARY 2, 2022, NYSEG COMPANY PERSONNEL INVESTIGATING A GAS ODOR COMPLAINT AT 2586 CARMEL AVE, BREWSTER NOTICED SMOKE COMING FROM THE RESIDENCE NEXT DOOR AT 2592 CARMEL AVE ("THE RESIDENCE"). NYSEG PERSONNEL IMMEDIATELY SHUT OFF THE SERVICE LINE TO THE RESIDENCE AND CALLED THE FIRE DEPARTMENT. THE FIRE CONTINUED FOR SEVERAL HOURS BEFORE IT WAS EXTINGUISHED. ALL OCCUPANTS OF THE RESIDENCE ESCAPED AND, TO NYSEG'S KNOWLEDGE, NO INJURIES WERE REPORTED AT THAT TIME. AFTER THE FIRE WAS EXTINGUISHED, NYSEG CONDUCTED A LEAK SURVEY OF THE SURROUNDING AREA AND IDENTIFIED A LEAK IN THE GAS MAIN AT A PERMALOCK TAPPING TEE APPROXIMATELY 20 FT - 30 FT FROM THE FOUNDATION OF THE RESIDENCE. THE PERMALOCK TAPPING TEE WAS MANUFACTURED BY PERFECTION CORPORATION (NOW KNOWN AS EAMCO, LLC), WHICH IS TODAY A SUBSIDIARY OF HONEYWELL INTERNATIONAL, INC. AFTER THE FIRE THE COMPANY CONDUCTED PRESSURE TESTS AND CONFIRMED THAT THERE WERE NO LEAKS IN THE SERVICE LINE TO THE RESIDENCE. FACTS LEARNED THROUGH THE INCIDENT INVESTIGATION RAISE QUESTIONS AS TO THE ACTUAL CAUSE OF THE FIRE. SPECIFICALLY, NYSEG LEARNED THAT A NEW FURNACE WAS INSTALLED IN THE RESIDENCE'S BASEMENT BY A CONTRACTOR UNAFFILIATED WITH NYSEG THE DAY BEFORE THE FIRE. ACCORDING TO INVESTIGATIVE FINDINGS SHARED WITH THE COMPANY BY A REPRESENTATIVE OF THE HOMEOWNER'S INSURER, THE TENANTS OF 2592 CARMEL AVE STARTED SMELLING GAS IMMEDIATELY AFTER THE NEW FURNACE WAS INSTALLED AND THROUGHOUT THE NIGHT BEFORE THE FIRE, HOWEVER, THEY DID NOT NOTIFY NYSEG BECAUSE THE INSTALLER HAD TOLD THEM THAT THIS WAS "NORMAL." THIS MATTER IS NOW THE SUBJECT OF MULTIPLE CIVIL LAWSUITS FOR PROPERTY DAMAGE IN WHICH THE CAUSE OF THE FIRE WILL BE THE SUBJECT OF DISCOVERY AND EXPERT TESTIMONY. THE COMPANY DID NOT HAVE ADEQUATE CAUSE TO REPORT WITHIN THE REQUIRED 30 DAYS. ALTHOUGH THE CAUSE OF THE FIRE IS STILL UNDER INVESTIGATION AND CURRENTLY THE SUBJECT OF LITIGATION, THE COMPANY IS MAKING THIS FILING NOW IN AN ABUNDANCE OF CAUTION AND TO THE EXTENT IT MEETS THE CRITERIA SET FORTH UNDER 49 CFR PART 191.3(3).
2026-06-30 10:38 | NO | YES | NO | 20230016 | 38043 | 2023-03-27 09:57 | SUPPLEMENTAL FINAL | 7685 | HUNTSVILLE GAS SYSTEM | P.O. BOX 2048 | HUNTSVILLE | AL | 35804 | 2023-03-11 13:43 | CENTRAL | NO | 2023 | 278 BREVARD BLV | HUNTSVILLE | MADISON | AL | 35811 | 34.8088 | -86.4832 |  | YES |  | YES |  | YES |  |  |  | 2023-03-11 13:43 | 1362057 | 1362183 | NATURAL GAS |  | 64.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-03-11 13:38 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 50 | YES | 7 | 2023-03-11 13:00 | YES | OPERATOR | 2023-03-11 13:43 | 2023-03-11 12:58 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 2005 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 3 | [7 empty] | CLASS 3 LOCATION | 390000 | 405798.97320712347 | 5000 | 5202.550938552865 | 500 | 520.2550938552865 | 0 | 0 |  | 5 | 324 | 282.625899280575539568345323741007194245 | 0 | 0 | 395824 | 167332.5783801003784136690647482014388489 | 411804.4051388121970395683453237410071942 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 47 | 49 | 50 | 192.619(A)(2) | 2005-01-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT DID NOT INDICATE ANY PRESSURE ISSUES ON THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | 230581806 |  |  | CONTRACT LOCATOR | NO | YES | 24 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | TODD GENTLE | GAS OPERATIONS DIRECTOR | todd.gentle@hsvutil.org | 2563484852 |  | TODD GENTLE | todd.gentle@hsvutil.org | 2563484852 | TODD GENTLE | GAS OPERATIONS DIRECTOR | 2563484852 | todd.gentle@hsvutil.org | AT APPROXIMATELY 1245 (12:45PM CST) ON MARCH 11, 2023, HUNTSVILLE UTILITIES (HU) DISPATCH CENTER RECEIVED A TELEPHONE CALL FROM A CONTRACTOR NOTIFYING HU THAT HE HAD CUT A GAS SERVICE LINE AT 278 BREVARD BLVD. ON-CALL CREWS FROM HU GAS DEPARTMENT RECEIVED NOTIFICATION AT 1245 (12:45PM CST) OF AN OUTSIDE LEAK DUE TO A DIG IN. HU GAS DEPARTMENT HELPER ARRIVED ON SCENE AT 1258 (12:58PM CST) AND NOTICED A STRONG SMELL OF GAS. THE FIRST RESPONDER KNOCKED ON THE FRONT DOOR, BUT NO ONE ANSWERED. THE METER WAS THEN TURNED OFF AND CONTACT WAS MADE WITH ONE OF THE HOMEOWNERS THAT ARRIVED AT THE HOUSE. DUE TO THE RESIDENT NOT BEING ABLE TO SPEAK ENGLISH, HU EMPLOYEE HAD TO REQUEST HELP FROM THE CONTRACTOR FOR TRANSLATION. AFTER THE CONTRACTOR TRANSLATED THE INFORMATION, THE RESIDENT WENT INSIDE AND RETRIEVED A RESIDENT THAT COULD SPEAK ENGLISH. THE HU EMPLOYEE WENT INTO THE HOUSE AND COULD SMELL GAS IN THE LAUNDRY ROOM. HE INSTRUCTED THE RESIDENT TO GET EVERYONE IN THE HOUSE OUT AND TO NOT TURN ON ANY SWITCHES. THE RESIDENT PROCEEDED TO TURN ON SOME LIGHT SWITCHES AND THE HU EMPLOYEE REITERATED NOT TO TURN ON/OFF ANYTHING AND TO GET EVERYONE OUT OF THE HOUSE. AT APPROXIMATELY 1315 (01:15PM CST) HU LEADMAN ON-CALL ARRIVED AND NOTICED GAS WAS BLOWING OUT OF THE GROUND NEAR THE SERVICE RISER. ONE CREW MEMBER BEGAN TO ATTEMPT TO TEST THE ATMOSPHERE IN THE HOUSE WITH A GAS DETECTION UNIT. IN HIS ATTEMPT TO GET INTO THE HOUSE, THE RESIDENCE LOCKED THE DOOR THUS HE HAD TO FIND THE RESIDENT TO UNLOCK THE DOOR. ALSO, HU PERSONNEL WERE BEGINNING TO IDENTIFY THE MAINLINE VALVES THAT WOULD ISOLATE THIS SECTION OF MAIN SERVING THE RESIDENCE. AT 1333 (01:33PM CST) THE SUPERVISOR ON-CALL ARRIVED AT THE SCENE AND BEGAN ACCESS THE SCENE. DURING THIS TIME OTHER CREW MEMBERS BEGAN DIGGING A HOLE NEAR THE AREA THAT THE SERVICE LINE WAS DAMAGED TO VENT THE GAS AWAY FROM THE HOUSE. UPON GAINING ACCESS TO THE RESIDENCE TO TEST THE ATMOSPHERE WITH THE GAS DETECTION UNIT, THE CREW MEMBER IN THE HOUSE HEARD WHAT SOUNDED LIKE THE GARAGE DOOR OPENING AND HEARD A LOUD ROARING SOUND. AS HE SAW THE FLAMES, HE RAN OUT THE FRONT DOOR. THE CREW MEMBERS DIGGING IN THE YARD HEARD WHAT THEY ASSUMED WHAT THE GARAGE DOOR OPENING IMMEDIATELY FOLLOWED BY AN EXPLOSION AT 1343 (01:43PM CST). CREW MEMBERS RE-ASSEMBLED NEAR THE STREET, THE SUPERVISOR ON SCENE CALL 911 AT 1343 (01:43PM CST) WHILE THE OTHER CREW MEMBERS CHECKED ON THE HEALTH STATUS OF ALL INDIVIDUALS AT THE SCENE. UPON FINDING NO ONE WAS INJURED, THE CREWS BEGAN TO LOCATE THE NEAREST MAIN LINE VALVES TO BEGIN TO SHUT OFF GAS TO THE WHOLE AREA. AFTER THE SUPERVISOR ENDED HIS CALL WITH 911, HE BEGAN TO CALL ADDITIONAL CREWS TO BRING SOME EQUIPMENT TO DIG THE SERVICE UP AND CAP IT OFF. ADDITIONAL CREWS ARRIVED ON SCENE AT 14:00 (02:00 PM CST) TO BEGIN DIGGING THE SERVICE UP ACROSS THE STREET SQUEEZE IT OFF AND CAP BOTH ENDS OF THE CUT. DURING THIS TIME ADDITIONAL CREW MEMBERS BEGAN LEAK SURVEYING THE SURROUND AREA AND PERFORMING BAR HOLE TEST AROUND THE MAIN. ONCE THE FIRE WAS EXTINGUISHED, CREWS MOVED ONTO THE PROPERTY AND CONTINUED LEAK SURVEY THE SURROUNDING AREA AND BAR HOLING THE SCENE. THE FIRE MARSHAL INSTRUCTED US TO REMAIN AWAY FROM THE STRUCTURE TILL THEIR INVESTIGATION WAS COMPLETE. AN INVESTIGATION INTO THE CAUSE OF THE INCIDENT IS ONGOING. CONTRIBUTING FACTORS MAY HAVE BEEN THE CUT GAS SERVICE LEAKING INTO THE HOUSE WITH AN UNKNOW IGNITION SOURCE. THE LOCAL WEATHER CONDITIONS AT THE TIME OF THE INCIDENT WERE A TEMPERATURE OF 60 DEGREES FAHRENHEIT, THE WIND SPEED WAS 4 MPH, NO WIND GUST, EAST WIND AND PARTLY CLOUDY. A SUPPLEMENTAL OR SUPPLEMENTAL PLUS FINAL REPORT WILL BE FILLED AS SOON AS NEW, UPDATED AND/OR CORRECTED INFORMATION IS KNOWN. IT HAS BEEN DETERMINED THAT THE ROOT CAUSE OF THE INCIDENT WAS LOCATES NOT BEING PERFORMED WITHIN THE ALLOTTED TIME FRAME. THE CONTRACTOR CORRECTLY LOCATED THE SERVICE LINE THEMSELVES, BUT DID NOT POT-HOLE THE UTILITIES.
2026-06-30 10:38 | NO | YES | YES | 20230019 | 38071 | 2023-04-14 16:55 | SUPPLEMENTAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2023-03-17 20:40 | MOUNTAIN | YES | 2023 | 8913 PADILLA DRIVE | EL PASO | EL PASO | TX | 79907 | 31.6878 | -106.334 | [5 empty] | YES |  |  |  | 2023-03-17 21:12 | 1362513 | 1362610 | NATURAL GAS |  | 5.772 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2023-03-17 16:49 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.54 | NO | 4 | 2023-03-17 17:49 |  |  |  | 2023-03-17 17:31 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2017 | 2017 |  |  |  |  | 2 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | DR11 |  |  | 2708 | MECHANICAL PUNCTURE | 0.2 | 0.2 | [7 empty] | CLASS 3 LOCATION | 129383 | 134624.329616557066459 | 5000 | 5202.550938552865 | 7895 | 8214.827931974973835 | 0 | 0 |  | 5.82 | 34 | 29.65827338129496402877697841726618705036 | 0 | 0 | 142312 | 60137.9222039342805837553956834532374101 | 148071.3667604662002580287769784172661871 | 0 | 0 | 1 | 2 | 0 | 1 | 0 | 49 | 50 | 60 | 192.619(A)(2) | 2017-11-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.1 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | DAMAGED DURING SEWER CLEAN OUT AT A CROSS BORE. | [149 empty] | YES |  |  |  |  | BRYAN WEEKS | DIRECTOR OF ENGINEERING | bryan.weeks@onegas.com | 5124071529 | 5124651133 | BRYAN WEEKS | bryan.weeks@onegas.com | 5124071529 | BRYAN WEEKS | DIRECTOR OF ENGINEERING | 5124071529 | bryan.weeks@onegas.com | POST-INCIDENT INVESTIGATION REVEALED A 2-INCH PE PIPE WAS MOST LIKELY PUNCTURED WHEN A RESIDENT'S PLUMBER USED A MECHANICAL TOOL TO CLEAR A CLOGGED SEWER LATERAL. THE GAS PIPE HAD BEEN INADVERTENTLY CROSS-BORED THROUGH THE SEWER LATERAL BY THE ORIGINAL GAS LINE INSTALLATION CONTRACTOR IN 2017. CAMERA INSPECTIONS WERE PERFORMED ON THE REMAINDER OF THE ORIGINAL INSTALLATION PROJECT AND NO ADDITIONAL AREAS WERE DISCOVERED TO HAVE CROSS-BORES. TEXAS GAS SERVICE COMPANY'S PUBLIC AWARENESS TO THE AFFECTED PUBLIC INCLUDES OUTREACH ON THE POSSIBILITY OF CROSS-BORES. SUPPLEMENTAL INFORMATION 5/19/23 TGS SELECTED 20:40 AS THE EARLIEST LOCAL TIME THAT THE INCIDENT REPORTING CRITERIA WERE MET BASED ON ITS PRELIMINARY EVALUATION THAT NATURAL GAS FROM ITS SYSTEM WAS LIKELY TO HAVE CAUSED THE FIRE AND THE PRESUMPTION THAT ONE OF THE HOME'S OCCUPANTS COULD BE ADMITTED TO THE HOSPITAL FOR CARE OR THAT THE TOTAL COST OF DAMAGES COULD EXCEED $129,300. WHILE THE ORIGINAL TELEPHONIC REPORT TO THE NATIONAL RESPONSE CENTER NOTED THE POTENTIAL THAT AN EXPLOSION HAD OCCURRED, THE INVESTIGATION MADE NO OBSERVATIONS OR FORMAL REPORTS OF AN EXPLOSION.
2026-06-30 10:38 | NO | YES | YES | 20230022 | 42308 | 2023-04-23 13:24 | SUPPLEMENTAL FINAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2023-03-24 16:55 | EASTERN | YES | 2023 | 17 S 2ND AVENUE | WEST READING | BERKS | PA | 19611 | 40.3344 | -75.9422 |  | YES | [7 empty] | 2023-03-24 19:09 | 1363061 | 1363191 | NATURAL GAS |  | 83 | 0.09 | YES | 0 | 0 | 0 | 0 | 7 | 7 | YES | 0 | 0 | 0 | 0 | 4 | 4 | YES | 2023-03-24 16:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 83 | YES | 0 | 2023-03-24 17:00 |  |  |  | 2023-03-24 17:19 | 2023-03-24 17:19 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 35 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | SERVICE TAPPING TEE | 1982 | UNKNOWN | [7 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 1881114 | 1957318.281244986818322 | 101142 | 105239.281405422774366 | 425531 | 442769.340686667839263 | 0 | 0 | PUBLIC & NON-OPERATOR PROPERTY DAMAGE COSTS BASED UPON PHMSA PERSONNEL FEEDBACK | 2.11 | 175 | 152.652877697841726618705035971223021583 | 0 | 0 | 2407962 | 1017436.54509676410386074100719424460432 | 2505479.55621477527367761870503597122302 | 14 | 4 | 11 | 7 | 0 | 18 | 7 | 53 | 53 | 60 | 192.619(A)(2) | 1982-04-29 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 9 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL DID NOT HAVE AN IMPACT ON THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | STEAM ESCAPING THROUGH A CRACK IN A CORRODED STEAM PIPE HAD SIGNIFICANTLY ELEVATED THE GROUND TEMPERATURES NEAR AN ALDYL A SERVICE TAPPING TEE. THIS CAUSED A UNIQUE FAILURE OF THE NATURAL GAS SERVICE TEE DUE TO SEVERE DEGRADATION OF ITS DELRIN INSERT AND ALDYL A COMPONENTS CAUSED BY EXPOSURE TO HEAT. | [154 empty] | CHAD REINER | STANDARDS ENGINEER | creiner@ugi.com | 484-577-6666 |  | JOHN TOUMEH | jtoumeh@ugi.com | 717-675-4606 | PAM JOCSAK | VP EHS AND TECHNICAL SUPPORT | 484-824-5508 | pjocsak@ugi.com | THIS IS A SUPPLEMENTAL AND FINAL REPORT BEING FILED TO PROVIDE UPDATED INCIDENT INFORMATION REGARDING THE ROOT CAUSE OF THIS EVENT. ON FRIDAY, MARCH 24, 2023, AT 4:55 P.M. EASTERN DAYLIGHT TIME, A NATURAL GAS-FUELED EXPLOSION AND FIRE OCCURRED AT R. M. PALMER COMPANY (PALMER) CANDY FACTORY BUILDING 2 AT 17 SOUTH 2ND AVENUE IN WEST READING, PENNSYLVANIA. SEVEN EMPLOYEES WERE KILLED AND FOUR PEOPLE WERE INJURED REQUIRING HOSPITALIZATION. UGI FIRST RESPONDERS BEGAN ARRIVING ONSITE AT 5:19 P.M AND ISOLATED THE DISTRIBUTION SYSTEM SUPPLYING NATURAL GAS TO THE AREA BY 6:15 P.M. MECHANICAL AND VISUAL EXAMINATION INDICATED THAT NATURAL GAS WAS LEAKING FROM A DUPONT ALDYL A SERVICE TEE THAT WAS INSTALLED IN 1982. UGI EXPOSED AND RETIRED THE SERVICE LINE THAT WAS CONNECTED TO THIS SERVICE TEE IN 2021 WHEN THE NATURAL GAS METER WAS RELOCATED FROM THE BASEMENT TO THE EXTERIOR OF BUILDING 2. PALMER OWNED SUBSURFACE INFRASTRUCTURE RAN UNDERNEATH THE PUBLIC RIGHT OF WAY ALONG CHERRY STREET, BETWEEN PALMER BUILDINGS 1 AND 2 AND INCLUDED A STEAM, CONDENSATE, AND SEVERAL HEATED CHOCOLATE PIPELINES. THE PALMER STEAM PIPE WAS LOCATED APPROXIMATELY 21 INCHES TO THE WEST AND 21 INCHES ABOVE THE 1982 RETIRED TEE (CENTER OF PIPE TO TOP OF TEE). THE STEAM PIPE LAID PERPENDICULAR TO THE GAS MAIN, WITH STEAM FLOWING FROM 77 S. 2ND AVE TO 17 S. 2ND AVE (FROM SOUTH TO NORTH). THE STEAM LINE WAS FOUND TO BE DEFORMED, CORRODED, AND CRACKED ALONG ITS EAST SIDE. THE STEAM LINE CRACK WAS MEASURED TO BE APPROXIMATELY 5-INCHES BY 2-INCHES AT THE 3 O'CLOCK POSITION ON THE STEAM PIPE. A PALMER MECHANIC INDICATED THAT ON THE DAY BEFORE THE ACCIDENT, A CHOCOLATE UNLOADER ENTERED THE MAINTENANCE SHOP AROUND 6:00 PM AND TOLD THE MECHANIC THAT HE SMELLED GAS AROUND THE MECHANIC'S CAR. SEVERAL EMPLOYEES WORKING THE SECOND SHIFT IN BUILDING 1 REPORTED THAT THEY SMELLED GAS ON THE DAY OF ACCIDENT. ONE EMPLOYEE REPORTED THAT SHE SMELLED GAS AS EARLY AS 2:58 P.M., AND AT 4 P.M. THREE EMPLOYEES REPORTED THE ODOR TO THE SECOND SHIFT SUPERVISOR BETWEEN 4:20-4:46 P.M. SOME OF THE EMPLOYEES REPORTED THAT THEY DID NOT FEEL THEY COULD EVACUATE FOR FEAR OF LOSING THEIR JOB. NO EVACUATION ORDER WAS GIVEN BY PALMER MANAGEMENT FOR BUILDINGS 1 AND 2 PRIOR TO THE EXPLOSION. UGI STATES THAT NO CALL WAS MADE TO THEM REGARDING THE SMELL OF GAS ODORANT ON THE DAY BEFORE OR DAY OF THE ACCIDENT. THE PROBABLE CAUSE OF THIS ACCIDENT WAS A UNIQUE FAILURE OF A NATURAL GAS SERVICE TEE DUE TO SEVERE DEGRADATION OF ITS DELRIN INSERT AND ALDYL A COMPONENTS CAUSED BY EXPOSURE TO HEAT FROM A PRIVATE, UNDOCUMENTED, RUPTURED STEAM LINE IN A PUBLIC RIGHT-OF-WAY. PLEASE NOTE THROUGH FURTHER INVESTIGATION A10 HAS BEEN INCREASED FROM 3 TO 4 INDIVIDUALS REQUIRING HOSPITALIZATION AS RESULT OF THE EVENT. COSTS IN PART D WERE ALSO UPDATED BASED UPON FEEDBACK FROM PHMSA PERSONNEL REGARDING PART D2(A).
2026-06-30 10:38 | NO | NO | NO | 20230023 | 40401 | 2023-04-26 10:26 | SUPPLEMENTAL FINAL | 32013 | AMERIGAS PROPANE LP | 500 N. GULPH RD. | KING OF PRUSSIA | PA | 19406 | 2023-04-01 01:30 | PACIFIC | YES | 2023 | 205 JUNIPER DRIVE | MAMMOTH LAKES | MONO | CA | 93546 | 37.6355 | -118.9959 |  | YES |  | YES | [5 empty] | 2023-04-01 13:15 | 1363726 | 1364037 | PROPANE GAS |  | 2.67 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-04-01 01:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 2.67 | NO | 0 | 2023-04-01 01:30 |  |  |  | 2023-04-01 02:05 | 2023-04-01 02:06 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | COOPERATIVE |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN | CLASS 2 LOCATION | 100000 | 104051.0187710573 | 300 | 312.1530563131719 | 2350 | 2445.19894111984655 | 0 | 0 | ESTIMATED AMOUNT - COST UNKNOWN | 3 | 8 | 6.9784172661870503597122302158273381295 | 0 | 0 | 102658 | 43376.2554089569752219424460431654676259 | 106815.3491857565055003597122302158273381 | 0 | 0 | 27 | 0 | 0 | 1 | 0 | 0.51 | 0.51 | 10 | 192.619(A)(1) | 1980-07-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | AN INVESTIGATION BY OUR 3RD PARTY INVESTIGATION/LEGAL TEAM WAS UNABLE TO COMPLETE A/THE INVESTIGATION OF THE RESIDENCE, THE HOMEOWNER HAD THE RESIDENCE DEMOLISHED. WE WERE NOT GIVEN NOTICE THAT THE STRUCURE HAS/WAS DEMOLISHED, WHEN NOTIFIED THE INSURANCE COMPANY WAS NOTIFED OF THIS - THEY STATED THE FILE WAS CLOSED, AND NO FURTHER ACTION WOULD BE NECESSARY. | [45 empty] | BILL L RUNYANS | SAFETY COMPLIANCE MANAGER | bill.runyans@amerigas.com | 2566979938 |  | KYLE MUIR | kyle.muir @amerigas.com | 7607090195 | BILL L RUNYANS | SAFETY COMPLIANCE MANAGER | 2566979938 | bill.runyans@amerigas.com | ON 4/1/2023 AT APPROXIMATELY 01:30 AM LOCAL TIME MANAGEMENT WAS NOTIFIED BY EMERGENCY RESPONDERS, THAT A SINGLE FAMILY RESIDENCE THAT HAD GAS SERVICE WAS ON FIRE. AT THAT TIME EMERGENCY RESPONDERS, SHUT OFF GAS SERVICE TO THE RESIDENCES AND SECURED THE SCENE. THE CAUSE OF THE FIRE IS UNCLEAR, ESTIMATED COSTS AND DAMAGES IS UNKNOWN. THIS INCIDENT WAS UNDER INVESTIGATION, THIS FORM IS BEING SUBMITTED AS A PRECAUTIONARY MEASURE. THE CAL FIRE REPORT WAS UNABLE TO DETEMINE THE ROOT CAUSE OF THE FIRE WAS SPECIFICALLY GAS RELATED OR THAT THE SYSTEM HAD A LEAK AT ANY POINT IN THE COMPANY PIPING. THE RESIDENCE WAS DEMOLISHED WITH OUT OUR CONSENT AND WE WERE NOT ALLOWED/ABLE TO PERFORM A FULL INVESTIGATION.
2026-06-30 10:38 | NO | YES | NO | 20230024 | 39284 | 2023-05-03 16:47 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2023-04-04 15:21 | EASTERN | YES | 2023 | 7307 THORNAPPLE LAKE ROAD | NASHVILLE | BARRY | MI | 49073 | 42.6245 | -85.1473 | [6 empty] | YES |  |  | 2023-04-05 10:02 | 1364022 | 1364164 | NATURAL GAS |  | 4971 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-04-04 15:21 | YES | OPERATOR | 2023-04-05 10:00 | 2023-04-04 15:24 | 2023-04-05 09:30 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO LOSS OF COVER |  | 66 | NO | YES | [6 empty] | YES | UNCASED | THORNAPPLE RIVER | UNKNOWN | BELOW WATER, PIPE ON OR ABOVE BOTTOM | INVESTOR OWNED |  | MAIN |  | 1950 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - LOW FREQUENCY |  | 0.219 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 6 | 18.8 |  | CLASS 1 LOCATION | 3800 | 3953.9387133001774 | 3995456 | 4157312.672549335156288 | 422 | 439.095299213861806 | 0 | 0 |  | 2.16 | 10737 | 9365.90827338129496402877697841726618705 | 0 | 0 | 4010415 | 1697528.75707478328798375539568345323741 | 4171071.61483523049045802877697841726619 | 414 | 22 | 4002 | 0 | 0 | 4002 | 436 | 385 | 385 | 400 | 192.619(C) | 1969-11-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | RCA RESULTS INDICATE THAT LINE 1022F CROSSING THE THORNAPPLE RIVER FAILED DUE TO OVERSTRESS FROM EXTERNAL FORCES EXHIBITED DURING A FLOOD EVENT. ACCELERATED WATER FLOW AND DEBRIS APPLIED STRESS ONTO THE UNSECURED PIPE CREATING AN INITIAL FRACTURE AND LEAK THAT PROGRESSED INTO A FULL SEPARATION OVER APPROXIMATELY A 13-HOUR PERIOD. | YES |  |  |  | YES | FLOODING EVENT | [178 empty] | YES | [34 empty] | CARMELLA Q. KING | PRINCIPAL ENGINEER TECHNICAL ANALYST | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | SENIOR MANAGER ENGINEERING | 989-598-5031 | jason.pionk@cmsenergy.com | ON APRIL 4, 2023, AT APPROXIMATELY 15:21 HOURS, CONSUMERS ENERGY RECEIVED NOTIFICATION OF A POSSIBLE NATURAL GAS LEAK ON THE PIPELINE THAT CROSSES THE THORNAPPLE RIVER NEAR 7307 THORNAPPLE LAKE ROAD NASHVILLE, (BARRY COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 15:24 HOURS. THE GSW CONFIRMED A LEAK INDICATION AT THE THORNAPPLE RIVER CROSSING ON A 6-INCH HIGH-PRESSURE, STEEL, SINGLE-FEED PIPELINE SERVING OVER FOUR THOUSAND DOWNSTREAM CUSTOMERS. A GAS DISTRIBUTION SUPERVISOR WAS NOTIFIED AND ARRIVED ONSITE TO ASSIST WITH THE RESPONSE. DUE TO EXTREME FLOODING CONDITIONS AND MINIMAL REMAINING DAYLIGHT, AN INITIAL RESPONSE PLAN WAS IMPLEMENTED TO CONTINUOUSLY MONITOR THE LEAK LOCATION. A CONTINGENCY PLAN ALSO WAS PREPARED FOR IMMEDIATE CONTAINMENT USING EMERGENCY VALVES TO ISOLATE THE AFFECTED SEGMENT SHOULD THE CONDITION WORSEN DURING THE NIGHT. GAS OPERATIONS AND GAS ENGINEERING ALSO EVALUATED AND ASSESSED THE SITUATION IN DEVELOPING A LONG-TERM REMEDIATION PLAN. THE FOLLOWING DAY, AN INCIDENT COMMAND STRUCTURE (ICS) WAS ACTIVATED BECAUSE OF THE POTENTIAL IMPACT TO CUSTOMERS IN HASTINGS, MI. THE REMEDIATION PLAN WAS FINALIZED, AND IMPLEMENTATION WAS ALREADY UNDERWAY WHEN OPERATIONS PERSONNEL DISCOVERED THE LEAK WAS WORSENING AND DUE TO AN ANTICIPATED TEMPERATURE DECREASE SERVICE LOSS FOR CUSTOMERS WAS LIKELY TO OCCUR. CONSEQUENTLY, ADDITIONAL COMMUNICATION WAS UNDERTAKEN WITH KEY STAKEHOLDERS AND CUSTOMERS NOTIFYING THEM OF THE POTENTIAL INTERRUPTION IN NATURAL GAS SERVICE. A HIGH-PRESSURE BYPASS WAS INSTALLED TO ALLOW FOR FASTER RESTORATION OF NATURAL GAS SERVICE TO IMPACTED CUSTOMERS ONCE THE RELEASE WAS CONTAINED. ON APRIL 6, 2023, GAS WAS SHUT-OFF AT THE LEAK LOCATION BY INSTALLING PRESSURE CONTROL FITTINGS AT THE EAST AND WEST SIDES OF THE LOCATION. CONCURRENT TO THE PRESSURE CONTROL WORK, MULTIPLE GSW'S WERE TURNING OFF AFFECTED CUSTOMERS' SERVICE-LINE VALVE PRIOR TO ADMITTING GAS BACK INTO THE SYSTEM. THE BYPASS WAS ACTIVATED AT APPROXIMATELY 07:21 HOURS. PURGING FROM AIR TO GAS OF THE PIPELINE WAS PERFORMED IN STAGES PRIOR TO TURNING SERVICE-LINE VALVES AND RELIGHTING CUSTOMERS. CONSTRUCTION FOR PERMANENT PIPELINE REPLACEMENT WAS ALSO UNDER WAY DURING THIS TIME. CUSTOMER RESTORATION STARTED ON APRIL 7, 2023, AND AS OF THIS REPORT'S DATE, SERVICE HAS BEEN RESTORED TO ALL IMPACTED CUSTOMERS OR THEY RECEIVED NOTIFICATION REQUESTING ACCESS TO THEIR PROPERTIES FOR SERVICE RESTORATION. WEEKLY RESTORATION STATUSES ARE PROVIDED TO THE MICHIGAN PUBLIC SERVICE COMMISSION STAFF. THE PERMANENT PIPELINE REPLACEMENT REQUIRED INSTALLATION OF APPROXIMATELY ONE THOUSAND FEET OF 6-INCH HIGH-PRESSURE STEEL PIPELINE. THE PIPELINE REPLACEMENT WAS COMPLETED, AND NORMAL OPERATIONS RESUMED ON APRIL 11, 2023, AT APPROXIMATELY 19:50 HOURS. THE ROOT CAUSE INVESTIGATION IDENTIFIED THE FAILURE OF THE PIPELINE CROSSING THE THORNAPPLE RIVER WAS A RESULT OF OVERSTRESS INDUCED BY EXTERNAL FORCES DURING THE FLOODING EVENT. THE COMBINATION OF ACCELERATED WATER FLOW AND DEBRIS IN THE WATERWAY EXERTED SIGNIFICANT PRESSURE ON THE UNSECURED PIPELINE, LEADING TO AN INITIAL FRACTURE THAT ULTIMATELY RESULTED IN COMPLETE SEPARATION.
2026-06-30 10:38 | NO | YES | NO | 20230025 | 38039 | 2023-05-04 15:40 | SUPPLEMENTAL FINAL | 31044 | LOWER VALLEY ENERGY, INC. | 236 N. WASHINGTON BLVD/P.O. BOX 188 | AFTON | WY | 83110 | 2023-03-25 02:56 | MOUNTAIN | YES | 2023 | 900 SNOW KING DR | JACKSON | TETON | WY | 83001 | 43.4698 | -110.7489 |  |  |  | YES | [5 empty] | 2023-03-25 07:10 | 1363085 | 1363250 | NATURAL GAS |  | 27 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-03-25 03:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 27 | NO | 0 | 2023-03-25 05:30 |  |  |  | 2023-03-25 03:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | COOPERATIVE |  | SERVICE RISER |  | 2006 | 2006 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | OTHER | THREADS | 0.113 | [6 empty] | OTHER | [8 empty] | METER CAIN SHEARED OFF RIGHT AT THE METER | CLASS 2 LOCATION | 3000000 | 3121530.563131719 | 100 | 104.0510187710573 | 540 | 561.87550136370942 | 0 | 0 |  | 27 | 729 | 635.90827338129496402877697841726618705 | 0 | 0 | 3001369 | 1268315.98585707103344575539568345323741 | 3122832.39792523506168402877697841726619 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 50 | 50 | 60 | 192.619(A)(3) | 2006-05-05 | PRESSURE DID NOT EXCEED MAOP | DRIP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS ON A RESIDENTIAL METER | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | DAMAGE FROM SNOW/ICE | [56 empty] | SNOW/ICE IMPACT OR ACCUMULATION | [5 empty] | NO | [218 empty] | CRAIG COLES | DIRECTOR OF GAS OPERATIONS | ccoles@lvenergy.com | 307 885 6151 | 307 885 5787 |  |  |  | CRAIG COLES | DIRECTOR OF GAS OPERATIONS | 307 885 6151 | ccoles@lvenergy.com | ON MARCH 25TH 2023 LOWER VALLEY ENERGY WAS CALLED TO A HOUSE FIRE WHERE THE METER CAIN HAD BEEN BROKEN BY SNOW AND ICE FALLING OFF THE ROOF AND BREAKING IT. THE GAS IGNITED BY AN UNKNOW SOURCE. LOWER VALLEY WAS CALLED BY THE FIRE DEPARTMENT TO THE SCENE WHERE IT WAS DECIDED TO PUT THE FLAME OUT AND TURN THE VALVE OFF WHICH DID STOP THE FLOW OF GAS. THE SITUATION WAS CONTROLLED BY 6:30 AM THAT DAY. THE HOUSE WAS A TOTAL LOSS FROM THE FIRE. THERE WERE NO INJURIES AS NO ONE WAS HOME AT THE TIME OF THE FIRE.
2026-06-30 10:38 | NO | YES | YES | 20230026 | 38016 | 2023-05-05 13:02 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2023-04-06 14:59 | EASTERN | YES | 2023 | 2027 HENDRIX DR. | GROVE CITY | FRANKLIN | OH | 43123 | 39.9156 | -83.0429 |  |  | YES | [6 empty] | 2023-04-06 15:18 | 1364142 | 1364239 | NATURAL GAS |  | 66.4 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2023-04-06 12:53 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 66.3 | NO | 0 | 2023-04-06 12:53 |  |  |  | 2023-04-06 13:10 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1986 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | YES | 1 | PE 2306 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 70000 | 72835.71313974011 | 800 | 832.4081501684584 | 4800 | 4994.4489010107504 | 0 | 0 |  | 5.04 | 335 | 292.221223021582733812949640287769784173 | 0 | 0 | 75935 | 32179.6920212907223625899280575539568345 | 78954.7914139409015338129496402877697842 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 48 | 48 | 60 | 192.619(A)(2) | 1996-08-24 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | AUGER | FENCING | NO | [5 empty] | YES | 48 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | rrsmith@nisource.com | 1-614-460-5491 |  | ROB R. SMITH | rrsmith@nisource.com | 1-614-460-5491 | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | 1-614-460-5491 | rrsmith@nisource.com | A THIRD-PARTY FENCING EXCAVATOR DAMAGED A ONE-INCH PLASTIC SERVICE LINE WITH AN AUGER ATTACHED TO A SKID STEER. AFTER STRIKING THE SERVICE LINE THE SKID STEER OPERATOR BACKED UP SLIGHTLY AND A COWORKER BEGAN TO REMOVE SOIL FROM THE HOLE WHEN GAS IGNITED BURNING THE CONTRACTORS FACE AND HANDS. IN ADDITION, THE FIRE DAMAGED THE SKID-STEER. THE THIRD-PARTY FENCING EXCAVATOR CALLED IN A ONE CALL TICKET TO A BUILDING ONE STREET OVER. THE DAMAGE OCCURED AT A LOCATION WITHOUT A ONE CALL TICKET. THE ODORANT READING AT THE TIME OF THE INCIDENT WAS .42 AND DUE TO A SYSTEM ISSUE, I WAS UNABLE TO DOCUMENT THE READING IN SECTION E6. PLEASE CONSIDER THIS REPORT BOTH AND INITIAL AND FINAL REPORT. NO FURTHER REPORTS WILL BE FILED.
2026-06-30 10:38 | NO | YES | NO | 20230027 | 38242 | 2023-05-18 17:22 | SUPPLEMENTAL FINAL | 20050 | AMERENUE | 1901 CHOUTEAU | SAINT LOUIS | MO | 63103 | 2023-04-19 09:05 | CENTRAL | YES | 2023 | 106 STATE HWY 114 | ESSEX | STODDARD | MO | 63846 | 36.811 | -89.8615 | YES | [8 empty] | 2023-04-19 09:55 | 1365146 | 1365278 | NATURAL GAS |  | 33.28 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-04-19 08:27 | ALLOWED TO BURN OUT |  | 33.28 | NO | 3 | 2023-04-19 09:05 |  |  |  | 2023-04-19 09:05 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | OTHER | FITTING | [9 empty] | OTHER | [8 empty] | VEHICLE DROVE OVER A METER SET. THE UNION BROKE OFF ABOVE THE RISER VALVE. | CLASS 3 LOCATION | 450000 | 468229.58446975785 | 1100 | 1144.5612064816303 | 65724 | 68386.491577089699852 | 0 | 0 | . | 0.94 | 31 | 27.0413669064748201438848920863309352518 | 0 | 0 | 516855 | 218384.9311303724948527769784172661870504 | 537787.6786202356549721438848920863309353 | 21 | 0 | 161 | 0 | 0 | 161 | 21 | 14.98 | 15 | 18 | 192.619(A)(4) | 1998-05-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | NO | UNKNOWN | SMALL TRUCK | ROADWAY | 15 | NO | [142 empty] | MARK BRANDT | MANAGER GAS COMPLIANCE AND PROGRAM MANAGEMENT | mbrandt2@ameren.com | 573-694-1794 |  | MARK BRANDT | mbrandt2@ameren.com | 573-694-1794 | PAM HARRISON | DIRECTOR MISSOURI GAS OPERATIONS | 573-619-3124 | pharrison@ameren.com | ON 4/19/2023, PRIOR TO 8:27AM A VEHICLE (VEHICLE 1) WAS PULLING OUT OF A PARKING LOT NEAR THE ESSEX ONE STOP CONVENIENCE STORE AND STRUCK AN ONCOMING VEHICLE (VEHICLE 2). VEHICLE 2 LOST CONTROL AND SLAMMED INTO THE GAS STATION WALL DRIVING OVER THE GAS METER, BREAKING THE GAS METER PIPING AT THE UNION ABOVE THE METER VALVE, CAUSING A LEAK. VEHICLE 2 CAME TO REST ON TOP OF THE BROKEN GAS PIPING. SHORTLY AFTER, THE GAS IGNITED LEADING TO A VEHICLE AND STRUCTURE FIRE. THE EXACT TIME OF IGNITION IS UNKNOWN. THE EXACT NUMBER OF INDIVIDUALS EVACUATED IS UNKNOWN, BUT IS ESTIMATED TO BE BETWEEN 3-5. AT 8:27 EMERGENCY RESPONSE PERSONNEL NOTIFIED THE AMEREN CALL CENTER OF THE FIRE. AT 8:30, AN AMEREN GAS FIRST RESPONDER WAS DISPATCHED. AT 9:05, THE FIRST AMEREN GAS PERSONNEL ARRIVED AT THE LOCATION. EMERGENCY RESPONSE PERSONNEL EXTINGUISHED THE STRUCTURE FIRE WHILE ALLOWING THE GAS FED FIRE TO BURN IN A CONTROLLED MANNER. AT 12:32, AMEREN PERSONNEL CLOSED AN EMERGENCY VALVE TO ISOLATE FLOW OF GAS TO SERVICE RISER. AT 12:48 THE FIRE BURNED OUT. AFTER VEHICLE 2 WAS REMOVED FROM THE SCENE, THE SERVICE WAS EXCAVATED AND PHYSICALLY ISOLATED FROM THE MAIN. AFTER WHICH, GAS SERVICE WAS RESTORED FOLLOWING ALL APPLICABLE STANDARD OPERATING PRACTICES. THE STRUCTURE AND VEHICLE 2 WERE TOTAL LOSSES. THE EXACT VALUE IS UNKNOWN, BUT IS ESTIMATED TO BE APPROXIMATELY $450,000.
2026-06-30 10:38 | NO | YES | YES | 20230028 | 39546 | 2023-06-13 13:39 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2023-05-02 10:00 | EASTERN | YES | 2023 | 26010 PENN STREET | INKSTER | WAYNE | MI | 48141 | 42.2854 | -83.2925 | [5 empty] | YES |  |  |  | 2023-05-02 10:40 | 1366173 | 1366323 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2023-05-02 10:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 3 | 2023-05-02 10:00 | YES | OPERATOR | 2023-05-02 10:01 | 2023-05-02 10:00 | 2023-05-02 10:01 | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | EXPLOSION ORIGINATED IN HOME CRAWL SPACE |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1952 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | CORROSION | [5 empty] | CLASS 3 LOCATION | 49000 | 50984.999197818077 | 300 | 312.1530563131719 | 10000 | 10405.10187710573 | 0 | 0 |  | 3.85 | 0 | 0 | 0 | 0 | 59300 | 25054.7970479704843 | 61702.2541312369789 | 0 | 0 | 1 | 1 | 0 | 2 | 0 | 9.1 | 10 | 10 | 192.619(A)(1) | 1952-08-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 7 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | YES |  |  |  | YES | CORROSION APPEARS TO HAVE OCCURRED AT THE GROUND-TO-ATMOSPHERE TRANSITION AREA |  |  | YES |  |  |  | NO | [11 empty] | YES | YES | UNKNOWN |  | UNKNOWN | [19 empty] | 2022-07-22 | NO | [182 empty] | YES | YES | [43 empty] | MARINA DARLING | SUPERVISOR - CODES AND STANDARDS | marina.darling@dteenergy.com | 15868724760 |  |  |  |  | MARINA I. DARLING | SUPERVISOR - CODES AND STANDARDS | 15868724760 | marina.darling@dteenergy.com | A DTE CREW WAS IN THE PROCESS OF REPLACING THE SERVICE LINE TO 26010 PENN STREET, INKSTER, MI, 48141, SINCE 8:30 AM, WHEN THE HOUSE EXPLODED INJURING ONE (1) HOMEOWNER AND ONE (1) DTE GAS EMPLOYEE. THE INVESTIGATION DETERMINED THAT A LEAK OCCURRED AT A CORRODED SECTION OF THE 3/4-INCH SERVICE RISER IN THE CRAWL SPACE OF THE HOUSE DURING REMOVAL OF THE METER MANIFOLD ASSEMBLY. THE CORROSION APPEARS TO HAVE OCCURRED AT THE GROUND-TO-ATMOSPHERE TRANSITION AREA AND THE DISTURBANCE OF THE PIPING DURING REMOVAL CAUSED THE LEAK. EMPLOYEES WERE UNAWARE OF THE LEAKING GAS AS IT ACCUMULATED IN THE CRAWL SPACE AND IGNITED. A SOURCE OF IGNITION HAS NOT BEEN DETERMINED. ESTIMATED VOLUME OF GAS RELEASED UNINTENTIONALLY (PART A.7) AND ESTIMATED VOLUME OF GAS CONSUMED BY FIRE (PART A.21C) COULD NOT BE DETERMINED DUE TO UNKNOWN SIZE AND DURATION OF THE LEAK AND IS ASSUMED TO BE MINIMAL. NOTE: DTE MADE THE INITIAL REPORT TO THE NRC AT 10:40 AM, HOWEVER, WAS ON HOLD FOR 18 MINUTES, WHICH MATCHES THE NRC'S REPORT FOR INITIAL OPERATOR REPORT TIME TO NRC OF 10:58 AM.
2026-06-30 10:38 | NO | NO | NO | 20230029 | 38184 | 2023-06-16 16:06 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2023-05-20 10:29 | EASTERN | YES | 2023 | HARPER AVENUE & FIERZ STREET | CLINTON TOWN | MACOMB | MI | 48035 | 42.5674 | -82.8717 | [5 empty] | YES |  |  |  | 2023-05-20 19:29 | 1367814 | 1367873 | NATURAL GAS |  | 3360 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-05-20 10:29 | YES | OPERATOR | 2023-05-20 10:55 | 2023-05-20 10:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 72 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | UNKNOWN |  |  |  |  | 4 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 4 | 9.6 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 100491 | 104561.909273223191343 | 2435 | 2533.642307075245255 | 0 | 0 |  | 2.19 | 7358 | 6418.399280575539568345323741007194244604 | 0 | 0 | 110284 | 48714.5406169529400950647482014388489209 | 113513.9508608739761663453237410071942446 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 55 | 54 | 60 | 192.619(A)(2) | 1969-10-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2023031501225 |  |  | CONTRACT LOCATOR | YES | YES | 24 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CARMELLA Q. KING | PRINCIPAL ENGINEER TECHNICAL ANALYST | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | SENIOR MANAGER ENGINEERING | 989-598-5031 | jason.pionk@cmsenergy.com | ON MAY 20, 2023, AT APPROXIMATELY 10:29 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE NEAR THE INTERSECTION OF HARPER AVENUE AND FIERZ STREET, CLINTON TOWNSHIP (MACOMB COUNTY) MICHIGAN. THE GAS DISTRIBUTION SUPERVISOR WAS ONSITE AT APPROXIMATELY 10:55 HOURS AND A GAS SERVICE WORKER (GSW) ARRIVED ONSITE AT APPROXIMATELY 11:02 HOURS. THE GSW CONFIRMED A THIRD-PARTY CONTRACTOR DAMAGED A 4-INCH STEEL (MEDIUM PRESSURE) PIPELINE WHILE BORING TELECOMMUNICATION CONDUIT. THE GSW BEGAN MONITORING THE AREA FOR GAS MIGRATION AND SERVICE PERSONNEL MONITORED THE AREA UNTIL THE GAS WAS CONTAINED. POLICE AND FIRE PERSONNEL WERE ONSITE AND CLOSED THE ROAD TO ENSURE THE SAFETY OF PEDESTRIANS AND VEHICLE TRAFFIC. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE DAMAGE AND SUBSEQUENT NATURAL GAS RELEASE. A DISTRIBUTION CREW ARRIVE ONSITE AT APPROXIMATELY 12:12 HOURS AND DEVELOPED A PLAN TO ISOLATE AND ARREST THE BLOWING GAS. BECAUSE THE PIPELINE DEPTH WAS GREATER THAN 6-FEET, SHORING EQUIPMENT WAS REQUIRED TO SAFELY ACCESS THE PIPELINE. THE DAMAGED SEGMENT WAS ISOLATED AT APPROXIMATELY 18:04 HOURS BY SQUEEZING THE 6-INCH S-MP PIPELINE TO THE NORTH AND SOUTH OF THE 4-INCH S-MP PIPELINE WHERE THE DAMAGE OCCURRED. ONCE GAS WAS CONTAINED, CONTROL FITTINGS WERE INSTALLED ON THE 6-INCH S-MP PIPELINE AND THE TWO SECTIONS USED DURING THE SQUEEZING OPERATION WERE REPLACED. THE SECTION OF THE 4-INCH S-MP PIPELINE WHERE THE INITIAL DAMAGE OCCURRED WAS REPLACED AND NORMAL OPERATIONS RESUMED ON MAY 21, 2023, AT APPROXIMATELY 10:45 HOURS. SERVICE RESTORATION FOR ALL IMPACTED CUSTOMERS BEGAN AFTER THE PIPELINE REPAIR.
2026-06-30 10:38 | NO | YES | NO | 20230030 | 38490 | 2023-06-26 21:38 | SUPPLEMENTAL FINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2023-05-26 12:10 | EASTERN | YES | 2023 | 29920 JAMESTOWN DRIVE | CHESTERFIELD TOWNSHIP | MACOMB | MI | 48051 | 42.6832 | -82.8084 |  | YES |  |  |  | YES |  |  |  | 2023-05-26 13:19 | 1368330 | 1368665 | NATURAL GAS |  | 15.09 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-05-26 10:53 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 15.09 | NO | 2 | 2023-05-26 10:53 |  |  |  | 2023-05-26 11:05 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1981 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 1.2 | 0.2 | [7 empty] | CLASS 3 LOCATION | 140000 | 145671.42627948022 | 3278 | 3410.792395315258294 | 14025 | 14593.155382640786325 | 0 | 0 |  | 4.5 | 68 | 59.31654676258992805755395683453237410072 | 0 | 0 | 157371 | 66510.2779872043446645107913669064748201 | 163734.6906041988545470575539568345323741 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1981-07-10 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY THIRD PARTY DAMAGE. | [12 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2023052503098 |  |  | FACILITY OWNER | YES | YES | 21 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JENNIFER POND | SUPERVISOR OF CODES AND STANDARDS | jennifer.pond@semcoenergy.com | 8102422381 |  | ADAM DZIEDZIC | adam.dziedzic@semcoenergy.com | (810) 887-5027 | PHIL LENN | DIRECTOR OF OPERATIONS SUPPORT | (810) 887-5027 | phil.lenn@semcoenergy.com | ON 05/26/23, A GAS MAIN LOCATED AT 29920 JAMESTOWN DRIVE, CHESTERFIELD TWP, MI, WAS STRUCK BY A THIRD-PARTY EXCAVATOR WHILE ATTEMPTING TO FIX A LEAKING WATER LINE. THE CONTRACTOR THEN CALLED 911 AND BEGAN EVACUATING NEARBY RESIDENTS. ACCORDING TO THE CONTRACTOR, THE GAS LEAK IGNITED WITHIN APPROXIMATELY 5 MINUTES OF THE GAS MAIN HIT. THE FIRE THEN SPREAD TO THE HOME. SEMCO DISPATCH WAS NOTIFIED OF THE INCIDENT BY THE LOCAL POLICE DEPARTMENT AT 10:53 AM. SEMCO CREWS ARRIVED, AND ONCE LOCAL FIRE PERSONNEL SECURED THE SCENE, SEMCO CREWS SECURED THE 2" PLASTIC MAIN BY 12:09 PM. REPAIRS, PURGING, AND RE-ACTIVATION OF GAS MAINS WERE COMPLETED BY 05/26/23 22:38 PM. THE FOLLOWING MORNING 05/27/23 SEMCO CREWS BEGAN RELIGHTING 26 CUSTOMERS AT 08:00 AM AND COMPLETED THE RELIGHTS BY APPROXIMATELY 11:45 AM. UPON INVESTIGATION, THE EXCAVATOR DUG USING A MINI-EXCAVATOR WITHIN THE 4' CAUTION ZONE OF THE MARKED GAS LINES WITHOUT HAND EXPOSING, RESULTING IN DAMAGE TO THE GAS LINE AND A RELEASE OF GAS. IT WAS ALSO DETERMINED THAT ALTHOUGH THE MAIN AND SERVICE LINES FEEDING THE ADDRESSED HOUSE WERE MARKED ACCURATELY, A PORTION OF MAIN LOCATED TO THE WEST OF THE SERVICE LINE WAS NOT MARKED, DUE TO A MAP ERROR. ADDITIONALLY, THE CONTRACTOR HIT AN UNDERGROUND ELECTRICAL SERVICE LINE IN THE SAME EXCAVATION WHICH WAS LIKELY THE SOURCE OF IGNITION.
2026-06-30 10:38 | NO | YES | YES | 20230032 | 38962 | 2023-07-03 13:59 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2023-06-08 15:30 | PACIFIC | YES | 2023 | 15630 ALUM ROCK AVENUE | SAN JOSE | SANTA CLARA | CA | 95127 | 37.3859 | -121.8146 | YES | YES | [7 empty] | 2023-06-08 15:55 | 1369527 | 1369698 | NATURAL GAS |  | 716 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2023-06-08 03:00 | YES | OPERATOR | 2023-06-08 03:05 | 2023-06-08 03:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1925 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | DISLODGMENT OF PLUG | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 4538 | 4721.835231830580274 | 4050 | 4214.06626022782065 | 0 | 0 | NO FACILITIES WERE DAMAGED DUE TO THIS INCIDENT, NOR WAS RESTORATION REQUIRED. | 9.2 | 6587 | 5745.854316546762589928057553956834532374 | 0 | 0 | 15175 | 8308.12253444476957361151079136690647482 | 14681.7558086051635139280575539568345324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 54 | 60 | 192.619(A)(3) | 1966-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ROSA DUENAS | PROGRAM MANAGER | r1dj@pge.com | [5 empty] | SUSIE RICHMOND | GAS REGULATORY COMPLIANCE MANAGER | 925-786-0267 | gsr8@pge.com | ON THURSDAY, JUNE 8, 2023, PG&E INCIDENT ON-DUTY PERSONNEL CONFIRMED THAT A RELEASE OF GAS FROM A PIPELINE RESULTED IN AN INJURY NECESSITATING IN-PATIENT HOSPITALIZATION. THE PG&E EMPLOYEE WAS ADMITTED TO THE HOSPITAL, WAS UNDER OBSERVATION AFTER SUFFERING FACIAL INJURIES, AND IS IN STABLE POSITION. THE INJURIES OCCURRED WHILE WORKING ON A 4-INCH STEEL DISTRIBUTION MAIN AND INVOLVED THE DISLODGMENT OF A PLUG DURING A SCHEDULED LEAK REPAIR. LOCAL FIRE AND POLICE DEPARTMENT PERSONNEL RESPONDED, AND THE EMPLOYEE WAS TRANSPORTED FOR TREATMENT IN AN AMBULANCE. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO A RELEASE OF GAS RESULTING IN AN INJURY REQUIRING HOSPITAL ADMISSION AND AT LEAST ONE OVERNIGHT STAY. PER THE INVESTIGATION REPORT THE DIRECT CAUSE FOR THIS INCIDENT IS INADEQUATE THREAD ENGAGEMENT DUE TO DEBRIS. A LACK OF PROFICIENCY COMBINED WITH THE FAILURE TO IDENTIFY AN AOC LED TO THE DISLODGEMENT OF THE PLUG. THE CE TEAM COMPLETED A HAZARD BARRIER ANALYSIS OF THE EXPECTED CONTROLS AROUND THE WORK TASK, AS WELL AS UTILIZED THE HUMAN FACTORS ANALYSIS AND CLASSIFICATION SYSTEM TO DETERMINE HUMAN PERFORMANCE PRECURSORS THAT MAY HAVE CONTRIBUTED TO THE EVENT. ON JUNE 7, 2023, PG&E CREWS RESPONDED TO A GRADE 3 LEAK AT 15630 ALUM ROCK AVE. IN SAN JOSE. AS PART OF THE LEAK REPAIR PROCESS, TWO 4" MUELLER LINE STOPPER FITTINGS WERE SUCCESSFULLY INSTALLED, AND LEAK REPAIRS WERE PERFORMED. UPON COMPLETION OF THE LEAK REPAIRS, WORKERS WERE IN THE PROCESS OF INSTALLING AND TIGHTENING TWO COMPLETION PLUGS WITH A WRENCH WHEN A FAILURE OF THE PRESSURE BOUNDARY WAS EXPERIENCED. AT APPROXIMATELY 0300AM ON JUNE 8TH, THE FINAL COMPLETION PLUG HAD BEEN INSTALLED AND WAS BEING TIGHTENED WITH A WRENCH WHEN IT INADVERTENTLY BLEW OUT OF THE FITTING AND EXPOSED TWO COWORKERS TO A DIRECT STREAM OF GAS AT DISTRIBUTION PRESSURE. THIS RESULTED IN AN UNCONTROLLED RELEASE OF GAS WITHOUT IGNITION CAUSING INJURIES TO ONE COWORKER IN THE FORM OF METAL SHAVINGS LODGED IN THEIR FACE AND EYES. THE INJURED COWORKER WAS ALSO POTENTIALLY STRUCK IN THE HEAD WITH EITHER A TIGHTENING WRENCH AND OR THE COMPLETION PLUG WHEN THE COMPLETION PLUG BECAME DISLODGED. TWO COWORKERS WORKING IN THE TRENCH WERE EVACUATED AND THE CREWS WERE MOVED A SAFE DISTANCE FROM THE GAS STREAM. EMERGENCY RESPONDERS ARRIVED AND INJURED COWORKER WAS TRANSPORTED TO A LOCAL HOSPITAL FOR TREATMENT. THE CAUSE EVALUATION (CE) TEAM CONDUCTED INTERVIEWS WITH THE INJURED COWORKER (ICW) ALONG WITH OTHER COWORKERS (CW1, CW2) WHO WERE AT THE WORK SITE AT THE TIME OF INCIDENT. THE CE TEAM COMPLETED A HAZARD BARRIER ANALYSIS OF THE EXPECTED CONTROLS AROUND THE WORK TASK TO DETERMINE HUMAN PERFORMANCE PRECURSORS THAT MAY HAVE CONTRIBUTED TO THE EVENT. AFTER REVIEWING THE COLLECTED INFORMATION, DOCUMENTATION AND RELATED FACTORS, THE DIRECT CAUSE FOR THIS INCIDENT IS INADEQUATE THREAD ENGAGEMENT DUE TO DEBRIS. THIS IS BASED ON THE SME EVALUATION OF THE EQUIPMENT POST INCIDENT WHERE MINIMAL THREAD DAMAGE IS PRESENT, AND THE EQUIPMENT PERFORMED AS DESIGNED. THE FIRST APPARENT CAUSE (AC1) IS WORKERS WERE QUALIFIED BUT NOT PROFICIENT WITH THE MUELLER LINE STOPPER PROCESS CONTAINED IN UTILITY PROCEDURE. THE SECOND APPARENT CAUSE (AC2) IS LESS THAN ADEQUATE (LTA) JOB PREPARATION PROVIDED TO WORKERS. A LACK OF PROFICIENCY COMBINED WITH THE FAILURE TO IDENTIFY AN AOC LED THEM TO FURTHER TIGHTEN THE COMPLETION PLUG, WHICH DISLODGED. ADDITIONAL DETAILS AND RESULTS OF THE CAUSAL ANALYSIS ARE DOCUMENTED IN THE CAUSE EVALUATION REPORT THAT HAS PREVIOUSLY BEEN SUBMITTED TO PHMSA AND CPUC.
2026-06-30 10:38 | NO | YES | NO | 20230033 | 38576 | 2023-07-07 14:07 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | 3600 MIDTOWN DR. | TAMPA | FL | 33607 | 2023-06-07 09:31 | EASTERN | YES | 2023 | STATE ROAD 31 & STATE ROAD 80 | FT.MYERS | USA | FL | 33905 | 26.7014 | -81.7602 | [7 empty] | YES | LOWERED PRESSURE AT SUPPLYING GATE FROM 350 PSI TO 250 PSI. | 2023-06-07 10:05 | 1369358 | 1369590 | NATURAL GAS |  | 4797 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-06-07 02:00 | YES | OPERATOR | 2023-06-07 06:46 | 2023-06-07 02:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 162 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2000 | UNKNOWN |  |  |  |  | 8 | API 5L X52 | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 354400 | 368756.8105246270712 | 37000 | 38498.876945291201 | 0 | 0 |  | 9 | 43173 | 37659.9010791366906474820143884892086331 | 0 | 0 | 434573 | 196041.5765284451708964028776978417266187 | 444915.5885490549628474820143884892086331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 350 | 476 | 192.619(A)(2) | 2013-02-15 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | OTHER | WATER DEPARTMENT |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXCAVATOR DAMAGE TO FACILITY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DRILLING | ENGINEERING/SURVEYING | YES | 132300796 |  |  | FACILITY OWNER | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | IYANNA JONES | COMPLIANCE ANALYST | iejones@tecoenergy.com | 407-420-6617 |  |  |  |  | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | 407-420-6667 | rharris@tecoenergy.com | ON JUNE 7, 2023, AT APPROXIMATELY 02:00 HOURS, PGS WAS NOTIFIED THAT A THIRD-PARTY CONTRACTOR HAD STRUCK A GAS PIPELINE AT STATE ROAD 31 & STATE ROAD 80 IN FT MYERS, FLORIDA. RESPONDING CREWS WERE DISPATCHED AND ARRIVED TO FIND A SOIL SAMPLING RIG WAS THE CAUSE OF THE DAMAGED PIPELINE AND ESCAPING GAS. AN ASSESSMENT WAS MADE OF THE SCENE, INCLUDING THE ABILITY TO SAFELY MANAGE THE SITE. AN EVALUATION OF OPTIONS FOR THE ONE-WAY-FED 8" STEEL PIPELINE, CONCLUDED THAT THE PIPELINE WOULD REMAIN IN SERVICE TO CONTINUALLY SUPPLY APPROXIMATELY 25,300 CUSTOMERS DOWNSTREAM, UNTIL A BYPASS COULD BE INSTALLED TO ISOLATE THE DAMAGED SECTION OF PIPELINE. OVER THE FOLLOWING DAYS, CREWS WORKED TO INSTALL 750' OF 8" STEEL BYPASS AROUND THE DAMAGED SECTION OF PIPELINE. THE BYPASS WAS ABLE TO ISOLATE THE DAMAGED SECTION OF PIPELINE ON JUNE 10, 2023, AT 13:25, AND COMPLETE STOPPAGE OF THE ESCAPING GAS. A ROOT CAUSE INVESTIGATION WAS CONCLUDED AND FOUND TWO PRIMARY CONTRIBUTING FACTORS: 1. THE GAS PIPELINE IN THE LOCATION OF THIS INCIDENT WAS/IS CLASSIFIED AS A "HIGH PRIORITY SUBSURFACE INSTALLATION (HPSI)" BY PGS THROUGH THE POSITIVE RESPONSE CODE OF "2C". PER FLORIDA STATUE CHAPTER 556 HPSI REQUIRES SPECIAL PROCEDURES WHEN DIGGING NEAR AN HPSI. WITH THIS CLASSIFICATION, BEFORE ANY DIGGING OR DEMOLITION, THE EXCAVATOR MUST NOTIFY THE MEMBER OPERATOR OF THE START DATE AND TIME OF THE EXCAVATION. IN ACCORDANCE WITH F.S. 556, THIS HPSI WAS MARKED BY PGS, AND A RESPONSE COMMUNICATED BACK TO THE REQUESTING EXCAVATOR USING A 2C (MARKED WITH EXCEPTIONS: HIGH PROFILE SUBSURFACE INSTALLATION IN CONFLICT). THE INSTRUCTIONS PROVIDED AND COMMUNICATED TO THE EXCAVATOR INDICATED, "EXCAVATOR MUST NOTIFY THE MEMBER OPERATOR OF THE EXCAVATION OR DEMOLITION START DATE AND TIME" WHICH THE EXCAVATOR FAILED TO DO. IN ADDITION, PEOPLES GAS ALSO SENT AN E-MAIL TO THE EXCAVATOR NOTIFYING THE EXCAVATOR ABOUT THE HPSI AND REQUESTING THE START DATE AND TIME. THE FAILURE BY THE EXCAVATOR TO NOTIFY PGS OF THE TIMING OF THEIR EXCAVATION AND THE SPECIFIC LOCATION DID NOT ALLOW PGS TO GIVE ADDITIONAL LOCATION INFORMATION AND SPECIFICATIONS RELATED TO THE PIPELINE IDENTIFIED AS "IN CONFLICT". THE FAILURE ALSO PREVENTED THE POSSIBILITY OF A PEOPLES GAS LOCATOR BEING ON-SITE DURING THE EXCAVATION. 2. THE DEPTH OF THE PIPELINE AT THE DAMAGED LOCATION WAS OVER THIRTEEN FEET DEEP. WHEN PGS' LOCATOR PERFORMED THE INITIAL LOCATE MARKING, THE LOCATE SIGNAL UNKNOWINGLY JUMPED OFF THE GAS PIPELINE ONTO AN ADJACENT TELECOMMUNICATION FACILITY. THIS CAUSED THE LOCATE MARKINGS TO VEER OFF THE GAS PIPELINE BY APPROXIMATELY 36" TO 48" AT THE DAMAGED LOCATION.
2026-06-30 10:38 | NO | YES | NO | 20230034 | 38874 | 2023-07-11 17:38 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2023-06-12 14:35 | CENTRAL | YES | 2023 | HIGHWAY 108 AT BAYOU DINDE | SULPHUR | CALCASIEU | LA | 70665 | 30.2031 | -93.3253 | YES | [8 empty] | 2023-06-12 14:35 | 1369874 | 1369973, 1370823 | NATURAL GAS |  | 384.72 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-06-09 13:36 | YES | OPERATOR | 2023-06-09 20:56 | 2023-06-09 13:36 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | UNDER WATERWAY | 48 | NO | YES | [6 empty] | YES | UNCASED | BAYOU DINDE | 13 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | INVESTOR OWNED |  | MAIN |  | 1982 | 1981 |  |  |  |  | 6 | API 5L GRADE B | JONES AND LAUGHLIN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.28 | [6 empty] | LEAK |  |  | OTHER | NOT EXCAVATED | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 1213000 | 1262138.857692925049 | 20594 | 21428.266805711540362 | 12540 | 13047.99775389058542 | BOOM RENTAL TO CONTAIN AREA FOR MONITORING. | 3.7 | 1423 | 1241.285971223021582733812949640287769784 | 0 | 0 | 1247557 | 527514.0549457114241807625899280575539568 | 1297856.40822375019636473381294964028777 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 430 | 430 | 500 | 192.619(A)(2) | 1982-06-17 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | REPLACED MAIN AND ABANDONED STEEL MAIN IN PLACE. LOCATION OF LEAK IS UNDER WATER CROSSING AND WAS NOT VERIFIED. DECISION WAS MADE NOT TO REMOVE PIPE DUE TO EXCESSIVE COSTS AND ENVIRONMENTAL CONCERNS. | [45 empty] | JAMES TODD HEBERT | OPERATIONS SPECIALIST | james.hebert@centerpointenergy.com | 337-256-2161 | 337-373-1520 | DOUGLAS BOUDREAUX JR | douglas.boudreauxjr@centerpointenergy.com | 337-475-6362 | DOUGLAS BOUDREAUX JR | REGION OPERATIONS DIRECTOR | 337-475-6362 | douglas.boudreauxjr@centerpointenergy.com | REPORTED INDICATION OF LEAK ON FRIDAY JUNE 9, 2023. AFTER INITIAL INVESTIGATION AND SQUEEZING 2" MAIN, IT WAS DETERMINED THAT LEAK WAS PROBABLE ON 6" STEEL MAIN. MORE INVESTIGATION REVEALED THAT WE WOULD HAVE TO BORE IN NEW PIPE TO REPLACE LEAKING FACILITY. IT WAS THEN DISCOVERED THAT COST WOULD EXCEED REPORTABLE CRITERIA AND A CALL TO THE NRC WAS PLACED ON MONDAY JUNE 12, 2023 AT 14:35 PM CENTRAL TIME. ONGOING REPAIRS AND 24 HOUR MONITORING CONTINUED UNTIL WEDNESDAY JUNE 21, 2023 WHEN INDICATIONS REVEALED THAT LEAK MAY BE GETTING WORSE AND A DECISION WAS MADE TO TURN SYSTEM OFF. SYSTEM WAS COMPLETELY PURGED @ 1:20 AM THURSDAY JUNE 22, 2023. REPAIRS WERE COMPLETE AND SYSTEM RETURNED TO SERVICE ON FRIDAY JUNE 23, 2023.
2026-06-30 10:38 | NO | YES | YES | 20230035 | 39742 | 2023-07-14 09:26 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2023-06-14 18:12 | CENTRAL | YES | 2023 | 1025 W LOOP 820 N | FORT WORTH | TARRANT | TX | 76108 | 32.7782 | -97.4755 | [5 empty] | YES |  |  |  | 2023-06-14 19:54 | 1370100 | 1370268 | NATURAL GAS |  | 88 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2023-06-14 18:12 | OPERATOR/CONTRACTOR |  | 88 | NO | 0 | 2023-06-14 18:27 |  |  |  | 2023-06-14 19:03 | 2023-06-14 19:03 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2006 | 2005 | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 1 LOCATION | 18500 | 19249.4384726456005 | 7897 | 8216.908952350394981 | 5359 | 5576.094095940960707 | 0 | 0 |  | 6.4084 | 564 | 491.978417266187050359712230215827338129 | 0 | 0 | 32320 | 13817.8864052669328279424460431654676259 | 33534.4199382031432383597122302158273381 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 29 | 29 | 60 | 192.619(A)(1) | 2006-06-20 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 30 | YES | YES | [141 empty] | STEVE KLEIN | FIELD SUPERVISOR | william.klein@atmosenergy.com | 469-261-2011 |  | STEVE KLEIN | william.klein@atmosenergy.com | 469-261-2011 | JEFF KNIGHTS | SR. V.P. TECHNICAL SERVICES | 214-206-2701 | jeff.knights@atmosenergy.com | ON JUNE 14, 2023, AT APPROXIMATELY 6:12 PM, AN ATMOS ENERGY SERVICE TECH RECEIVED A PHONE CALL FROM DISPATCH INFORMING HIM OF A VEHICLE STRIKING A METER. UPON ARRIVAL AT THE SITE AT APPROXIMATELY 6:27 PM, THE TECH CONFIRMED THE ADDRESS WAS 1025 W LOOP 820 N. THE GAS METER HAD BEEN STRUCK BY A VEHICLE, AND THE FIRE DEPARTMENT WAS PRESENT AT THE SITE WHEN THE TECH ARRIVED. THE POLICE REPORT STATES: "[THE VEHICLE] STRUCK TWO METAL POST[S] AND A NATURAL GAS PIPELINE. [THE VEHICLE] CAME TO REST ON TOP OF THE NATURAL GAS PIPELINE. THE NATURAL GAS PIPELINE RUPTURED AND BEGAN LEAKING NATURAL GAS. [THE VEHICLE] AND THE LEAKING NATURAL GAS CAUGHT FIRE." THE TECH REQUESTED ADDITIONAL OPERATOR RESOURCES. A CONSTRUCTION CREW ARRIVED AT APPROXIMATELY 7:03 PM. TO ELIMINATE THE GAS FLOW, THE CONSTRUCTION CREW SQUEEZED OFF THE 6-INCH POLY MAIN AT APPROXIMATELY 8:03 PM. TO RESTORE SERVICE, THE STATION WAS REBUILT IN A DIFFERENT LOCATION, AND SERVICE WAS RESTORED AT 2:15 PM ON JUNE 16, 2023.
2026-06-30 10:38 | NO | YES | NO | 20230036 | 38450 | 2023-07-20 16:44 | SUPPLEMENTAL | 32074 | SUMMIT NATURAL GAS OF MISSOURI | 116 CHIEFS COURT | BRANSON | MO | 65616 | 2023-06-27 17:30 | CENTRAL | YES | 2023 | WEST 4TH STREET | MOUNTAIN GROVE | WRIGHT | MO | 65711 | 37.1318 | -92.2638 |  | YES | [7 empty] | 2023-06-27 17:35 | 1371439 | 1371439 | NATURAL GAS |  | 152 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-06-26 17:50 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | NO | 6 | 2023-06-26 17:35 | YES | OPERATOR | 2023-06-26 17:45 | 2023-06-26 17:42 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 72 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 2 | ASTM D2513 - SDR 11 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 250000 | 260127.54692764325 | 4500 | 4682.2958446975785 | 15000 | 15607.652815658595 | 0 | 0 |  | 10.529 | 1600 | 1395.683453237410071942446043165467625899 | 0 | 0 | 271100 | 115002.9268098436588884892086330935251799 | 281813.1790412368335719424460431654676259 | 3 | 0 | 3 | 0 | 0 | 3 | 3 | 38 | 38 | 50 | 192.619(A)(1) | 1995-05-15 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.6 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS CAUSED BY MECHANICAL DAMAGE OF BLIND BORING | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 231690282 |  |  | FACILITY OWNER | YES | YES | 26 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [143 empty] | YES | [26 empty] | JORDAN SLAYTON | OPERATIONS MANAGER | jslayton@summitnaturalgas.com | 417-349-0512 |  | JORDAN SLAYTON | jslayton@summitnaturalgas.com | 417-349-0512 | MITCH PEBLEY | DIRECTOR OF OPERATIONS - MISSOURI | 720-981-2116 | mpebley@summitutilities.com | ON JUNE 26TH, 2023, A&A CABLE WAS INSTALLING A NEW FIBER OPTIC LINE IN MOUNTAIN GROVE, MISSOURI. A&A WAS SUBCONTRACTING FOR MASTEC DOING FIBER INSTALLATIONS. A&A WAS BLIND BORING APPROXIMATELY 300 FEET, CROSSING MULTIPLE NATURAL GAS LINES, COMMUNICATIONS LINES, A SEWER MAIN, AND A WATER MAIN WITHOUT EXPOSING OR POTHOLING ANY OF THE UTILITIES BEFORE EXCAVATION TOOK PLACE. DURING THIS BLIND BORE SHOT A 2' PE NATURAL GAS MAIN OPERATED BY SUMMIT NATURAL GAS WAS STRUCK. THE GAS LINE WAS LOCATED ACCURATELY BY A SNGMO TECHNICIAN UNDER THE LOCATE REQUEST NUMBER 231690282. ONCE THE GAS LINE WAS STRUCK BY THE BORING MACHINE THE NATURAL GAS MIGRATED FOLLOWING THE PATH OF A SEWER DRAIN AND ENTERED AN EMPTY DETACHED GARAGE / WASH BAY OWNED AND OPERATED BY CRAIG HURT FUNERAL HOME. THE GARAGE CONTAINED A HANGING STYLE FURNACE WITH A STANDING PILOT. ONCE AN ADEQUATE VOLUME OF GAS HAD ENTERED THE STRUCTURE TO REACH THE LEL THE GAS IGNITED, AND A HARD IGNITION AND FIRE WAS THE RESULT. THE LACK OF DEBRIS FIELD AND REVIEW OF VIDEO INDICATED THERE WAS NO SUDDEN AND VIOLENT RELEASE OF ENERGY CONSTITUTING AN EXPLOSION. APPROXIMATELY 152 MCF OF NATURAL GAS WAS LOST DUE TO THE RUPTURE OF THE GAS MAIN. TWO VEHICLES AND OTHER PRIVATELY OWNED MATERIALS WERE LOST IN THE SUBSEQUENT FIRE IN THE GARAGE. THE STRUCTURE AND CONTENTS WERE A TOTAL LOSS.
2026-06-30 10:38 | NO | YES | YES | 20230038 | 38430 | 2023-07-25 12:06 | SUPPLEMENTAL FINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2023-06-26 08:30 | CENTRAL | YES | 2023 | 10412 PACIFIC ST | OMAHA | DOUGLAS | NE | 68114 | 41.2493 | -96.0763 |  |  |  | YES | [5 empty] | 2023-06-26 13:30 | 1371294 | 1371476 | NATURAL GAS |  | 0.1 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2023-06-26 08:30 | OPERATOR/CONTRACTOR |  | 0.1 | NO | 0 | 2023-06-26 08:30 | YES | OPERATOR | 2023-06-26 08:40 | 2023-06-26 08:55 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | OTHER | OPERATOR OWNED | SERVICE VALVE |  | 1973 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.133 | [6 empty] | OTHER | [8 empty] | RESIDUAL GAS, AFTER SERVICE VALVE WAS REPLACED AND GAS WAS OFF. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 200 | 208.1020375421146 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 200 | 84.5018450184502 | 208.1020375421146 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 60 | 60 | 60 | 192.619(A)(3) | 1973-09-06 | PRESSURE DID NOT EXCEED MAOP | DRIP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS NOT RELATED TO NOR IDENTIFIABLE BY SCADA. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | DURING SERVICE VALVE REPLACEMENT, ENVIRONMENTAL CONDITIONS ALLOWED FOR RESIDUAL GAS TO BE IGNITED. |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | TYSON ROBARDS | CLAIMS ADJUSTER | tyson_robards@mudnebr.com | 4025047108 |  | TYSON ROBARDS | tyson_robards@mudnebr.com | 4025047108 | TYSON ROBARDS | CLAIMS ADJUSTER | 4025047108 | tyson_robards@mudnebr.com | FOLLOWING A SERVICE VALVE REPLACEMENT, ENVIRONMENTAL CONDITIONS ALLOWED FOR RESIDUAL GAS TO BE IGNITED AND RESULTED IN BURNS ON TWO EMPLOYEES. NOTE - FOR QUESTION A4 THE DISTRICT USED 8:30 AM AT THE DIRECTION OF PHMSA. THIS WAS NOT THE TIME THAT THE INCIDENT BECAME REPORTABLE. THAT TIME WAS WHEN THE EMPLOYEE WAS HOSPITALIZED WHICH OCCURED AT 13:30. NOTE - FOR QUESTIONS A7 & A21 THE DISTRICT USED 0.1 AT THE DIRECTION OF PHMSA. ALL GAS RELEASED PRIOR TO THIS INCIDENT WAS INTENTIONAL.
2026-06-30 10:38 | NO | YES | NO | 20230039 | 38330 | 2023-07-27 13:14 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2023-06-27 16:25 | EASTERN | YES | 2023 | GRANVILLE ST. AND SARATOGA AVE. | NEWARK | LICKING | OH | 43055 | 40.0663 | -82.4178 | YES | [8 empty] | 2023-06-27 17:09 | 1371435 | 1371598 | NATURAL GAS |  | 1813.8 | 17 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 200 | 2023-06-27 16:25 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-06-26 10:00 | 2023-06-26 11:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 7 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 2.4 | [6 empty] | MECHANICAL PUNCTURE | 6 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 279186 | 290495.877266164033578 | 2800 | 2913.4285255896044 | 0 | 0 |  | 5.04 | 9142 | 7974.586330935251798561151079136690647482 | 86 | 75.01798561151079136690647482014388489209 | 291214 | 125697.5496562160084716115107913669064748 | 301458.9101083004005679280575539568345324 | 18 | 0 | 793 | 0 | 0 | 200 | 0 | 45 | 45 | 55 | 192.619(A)(3) | 1969-07-11 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  | YES |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | MILLING EQUIPMENT | MILLING | YES | A317201755 | OHIO 811 |  | CONTRACT LOCATOR | YES | YES | 75 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | rrsmith@nisource.com | 1-614-460-5491 |  | ROB R. SMITH | rrsmith@nisource.com | 1-614-460-5491 | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | 1-614-460-5491 | rrsmith@nisource.com | ON JUNE 26, 2023, A ROADWAY MILLING CONTRACTOR DAMAGED AN 8" BARE STEEL MAIN THAT HAD BEEN IMPROPERLY LOCATED BY COLUMBIA'S SECOND-PARTY LOCATOR. THE MAINLINE WAS SHUT OFF FOR SAFETY RESULTING IN AN 811-CUSTOMER OUTAGE. THE FOLLOWING DAY, COLUMBIA BEGAN CALCULATING THE COST OF RESTORATION TO THESE 811 CUSTOMERS AND DETERMINED THAT THE COST EXCEEDED THE REPORTABLE CRITERIA ESTABLISHED IN 49 CFR PART 191.3. THEREFORE, COLUMBIA PROMPTLY REPORTED THIS EVENT WHEN THE CRITERIA WAS MET. PLEASE CONSIDER THIS A FINAL REPORT.
2026-06-30 10:38 | NO | YES | NO | 20230041 | 38369 | 2023-08-09 13:34 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2023-07-14 20:17 | PACIFIC | NO | 2023 | 343 N. LIMA STREET | SIERRA MADRE | PASADENA | CA | 91024 | 34.168 | -118.06 | [7 empty] | YES | INSTALLED/WELDED 2-2" TOP HALVE PRESSURE CONTROL FITTINGS. | 2023-07-14 20:17 | 1373115 | 48hr update NRC#1373261 | NATURAL GAS |  | 464 | 0.05 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-07-14 06:05 | NO |  |  | 2023-07-14 06:26 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1956 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | A WATER MAIN CROSSING OVER A SOCALGAS GAS MAIN BORED A HOLE INTO THE GAS MAIN AND FILLED THE NATURAL GAS MAIN WITH WATER. GAS PRESSURE WAS OVERCOME BY WATER PRESSURE. | CLASS 3 LOCATION | 0 | 0 | 6367 | 6624.928365153218291 | 233048 | 242488.818225573616504 | 0 | 0 |  | 6 | 2784 | 2428.489208633093525179856115107913669065 | 0 | 0 | 242199 | 103132.887852079978200971223021582733813 | 251542.2357993599283201798561151079136691 | 19 | 0 | 652 | 0 | 0 | 645 | 26 | 42 | 42 | 50 | 192.621 M | 1956-05-15 | PRESSURE DID NOT EXCEED MAOP | OTHER | SELF SEASONED |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | WATER MAIN LEAK CAUSED DAMAGED TO NATURAL GAS PIPELINE. | [136 empty] | YES | [17 empty] | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | jjcervantes@socalgas.com | 310-970-4854 | 909-335-7895 | JAMES CERVANTES | jjcervantes@socalgas.com | 310-970-4854 | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 310-970-4854 | jjcervantes@socalgas.com | ON 07/14/2023 SOCALGAS CREWS RESPONDED TO AN UNDER-PRESSURE CONDITION AT 343 N. LIMA STREET, SIERRA MADRE, PASADENA. ON INVESTIGATION COMPLETED TO DATE REGARDING THE UNDER-PRESSURE CONDITION, SOCALGAS IDENTIFIED A LEAKING 6-INCH WATER MAIN AT THE CROSS POINT OF A 2" STEEL GAS MAIN THAT BORE A HOLE INTO THE GAS MAIN AND FILLED THE GAS MAIN WITH WATER, THE GAS PRESSURE WAS OVERCOME BY THE WATER PRESSURE, AFFECTING MULTIPLE SERVICES AND THE MAIN. THIS INCIDENT WAS REPORTED TO THE CPUC DUE TO UNDER-PRESSURE. THIS WAS REPORTED TO THE DOT DUE TO GAS RELEASE AND DAMAGE EXCEEDING $139,700.
2026-06-30 10:38 | NO | YES | NO | 20230042 | 40059 | 2023-08-15 14:41 | SUPPLEMENTAL FINAL | 18584 | SPRINGFIELD, CITY UTILITIES OF | 301 E. CENTRAL | SPRINGFIELD | MO | 65802 | 2023-07-17 11:25 | CENTRAL | YES | 2023 | 5012 S. CHARLESTON | SPRINGFIELD | GREENE | MO | 65804 | 37.1229 | -93.2632 | YES | YES |  | YES | [5 empty] | 2023-07-17 13:25 | 1373341 | 1373504 | NATURAL GAS |  | 1210 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-07-17 11:25 | ALLOWED TO BURN OUT |  | 1087 | NO | 4 | 2023-07-17 11:20 | YES | OPERATOR | 2023-07-17 11:21 | 2023-07-17 11:45 | 2023-07-17 13:05 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | TRANSITION AREA | OTHER | UNEXPOSED FITTING NEAR EXPOSED VALVE |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1968 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.25 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 100000 | 104051.0187710573 | 250000 | 260127.54692764325 | 10000 | 10405.10187710573 | 0 | 0 |  | 6.86 | 8301 | 7240.980215827338129496402877697841726619 | 0 | 0 | 368301 | 158000.6141986779858992805755395683453237 | 381824.6477916336181294964028776978417266 | 0 | 0 | 4 | 4 | 0 | 4 | 0 | 134 | 148 | 200 | 192.619(A)(3) | 1987-07-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ASPECT OF THE CONTROL ROOM OPERATIONS WERE A CONTRIBUTING FACTOR TO THE INCIDENT AND THERE WERE NO ACTIONS THAT THE CONTROLLER COULD HAVE TAKEN THAT WOULD HAVE CHANGED THE OUTCOME OF THE INCIDENT. | [12 empty] | YES | 7 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | CITY UTILITIES PERSONNEL FAILED TO LOCATE AND REVIEW THE AS-BUILT DRAWING OF THE CROSS-FITTING LOCATION, WHICH SHOWED THE PRESENCE OF A DRESSER COUPLING NEAR THE FITTING. |  | YES |  |  |  | OTHER MAINTENANCE | NO | [50 empty] | JACOB ANDERSON | NATURAL GAS CODE COMPLIANCE ENGINEER | jacob.anderson@cityutilities.net | 4177662756 |  | JACOB ANDERSON | jacob.anderson@cityutilities.net | 4177662756 | DUFFY MOONEY | DIRECTOR - SUPPLY AND DELIVERY | 417-831-8462 | duffy.mooney@cityutilities.net | A NATURAL GAS CONSTRUCTION CREW WAS PERFORMING MAINTENANCE ON A DISTRIBUTION LINE BEHIND 5012 S CHARLESTON AVENUE. AT THAT LOCATION, A FLANGED CROSS FITTING CONNECTED SECTIONS OF GAS PIPELINE VIA VALVES TO THE NORTH, WEST, AND SOUTH IN AN EXPOSED VALVE CLUSTER PIT. IN PREPARATION FOR MAINTENANCE, THE VALVES TO EACH OF THE NORTH, WEST, AND SOUTH PIPELINES WERE CLOSED. GAS REMAINED IN THE NORTH AND WEST PIPELINE BUT HAD ALREADY BEEN PURGED FROM THE SOUTH PIPELINE. CREWS REMOVED THE FLANGED CROSS FITTING AND THE VALVE TO THE SOUTH. THOUGH THE VALVE TO THE NORTH WAS EXPOSED, IT WAS ATTACHED TO A SECTION OF PIPE CONNECTED TO THE UPSTREAM PIPELINE BY A COMPRESSION COUPLING THAT WAS UNDERGROUND AND NOT VISIBLE TO THE CREW. SHORTLY AFTER THE CREW REMOVED THE FLANGED CROSS FITTING, THEY HEARD A SOUND THEY RECOGNIZED TO BE A GAS LEAK, SO THEY BEGAN TO EVACUATE THE AREA AND CONTACTED EMERGENCY SERVICES. WITHIN APPROXIMATELY 5 MINUTES, THE BLOWING GAS IGNITED. GAS WAS THEN SHUT OFF FROM THE INCIDENT SITE AND THE FLAMES WERE EXTINGUISHED. EVENTUALLY IT WAS DISCOVERED THAT THE NORTH VALVE AND SECTION OF PIPE IT WAS ATTACHED TO HAD PULLED OUT OF THE COMPRESSION COUPLING CONNECTING IT WITH THE REST OF THE NORTH PIPELINE.
2026-06-30 10:38 | NO | YES | YES | 20230043 | 39130 | 2023-08-15 17:44 | SUPPLEMENTAL FINAL | 32513 | AMEREN ILLINOIS COMPANY | 10 EXECUTIVE DR. | COLLINSVILLE | IL | 62234 | 2023-07-15 09:24 | CENTRAL | YES | 2023 | 500 MILL ST | GEORGETOWN | VERMILLION | IL | 61846 | 39.9784 | -87.6295 | YES | [8 empty] | 2023-07-15 10:23 | 1373141 | 1373156, 1373298 | NATURAL GAS |  | 182 | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | NO | [5 empty] | 0 | YES | 2023-07-15 07:49 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 182 | NO | 0 | 2023-07-15 08:21 |  |  |  | 2023-07-15 09:10 | 2023-07-15 09:52 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1954 | 1954 | [7 empty] | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.237 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 4 | 4 |  | CLASS 3 LOCATION | 15000 | 15607.652815658595 | 309635 | 322178.371971763270855 | 800000 | 832408.1501684584 | 0 | 0 |  | 4.054 | 738 | 643.758992805755395683453237410071942446 | 0 | 0 | 1125373 | 475692.9609227747825216906474820143884892 | 1170837.93394868602125068345323741007194 | 50 | 0 | 1280 | 0 | 0 | 1280 | 50 | 118 | 118 | 125 | 192.621 M | 1954-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A VEHICLE HIT A PRESSURE REGULATOR STATION AND GAS CONTROL HAD NO CAUSE OR CONTRIBUTING FACTORS IN THAT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | 35 | PASSENGER CAR | ROADWAY | 271 | YES |  | YES | [116 empty] | YES | [23 empty] | JOHN BOZARTH | DIRECTOR PIPELINE SAFETY AND QUALITY MANAGMENT | jbozarth@ameren.com | 2176256854 |  |  |  |  | JOHN BOZARTH | DIRECTOR PIPELINE SAFETY AND QUALITY MANAGMENT | 2176256854 | jbozarth@ameren.com | AMEREN ILLINOIS RECEIVED NOTIFICATION THAT A CAR HAD LEFT THE ROADWAY AND DROVE INTO A FENCED REGULATOR STATION IN GEORGETOWN, IL. IGNITION OF THE GAS AT THIS ABOVE GRADE FACILITY OCCURRED UPON IMPACT. THE DISTANCE TRAVELLED BETWEEN THE LOCATION WHERE THE CAR LEFT THE ROADWAY AND THE FENCE AROUND THE REGULATOR STATION IS APPROXIMATELY 261 FEET. THE DRIVER AND THE ONE OTHER PASSENGER BOTH WERE PRONOUNCED DECEASED. THE INLET SUPPLY OF GAS WAS STOPPED BY CLOSING AN UPSTREAM VALVE. GAS PRESSURE WAS LOST ON THE DOWNSTREAM SIDE OF THE REGULATOR STATION, WHICH WAS A ONE WAY FEED TO THE TOWN OF GEORGETOWN. THE RESULT WAS A LOSS OF SERVICE TO 1330 GAS CUSTOMERS, FOLLOWED BY REPAIRS TO THE GAS SYSTEM AND SUBSEQUENT RESTORATION OF GAS SERVICE. *REVISED AND FINAL INCLUDE COSTS RELATED TO PERMANENT REBUILD OF REGULATOR STATION.
2026-06-30 10:38 | NO | NO | NO | 20230044 | 38425 | 2023-08-18 13:59 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2023-07-20 11:11 | EASTERN | YES | 2023 | N. GRAND AVENUE & SAGINAW STREET | LANSING | INGHAM | MI | 48933 | 42.7408 | -84.5511 | [5 empty] | YES | YES |  |  | 2023-07-20 17:01 | 1373673 | 1373742 | NATURAL GAS |  | 6728 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 1 | 2023-07-20 11:11 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-07-20 11:34 | 2023-07-20 11:34 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 92 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2003 | UNKNOWN |  |  |  |  | 6 | D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.602 |  | 2708 | MECHANICAL PUNCTURE | 2 | 29.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 39409 | 41005.465987485971357 | 35 | 36.417856569870055 | 0 | 0 |  | 2.2 | 14802 | 12911.8165467625899280575539568345323741 | 0 | 0 | 54246 | 27181.2632270567340555107913669064748201 | 53953.7003908184313400575539568345323741 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 55 | 55 | 60 | 192.619(A)(2) | 2003-01-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | YES | YES | STATE HIGHWAY | [12 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 2023070500130 |  |  | FACILITY OWNER | YES | YES | 17 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | CARMELLA Q. KING | PRINCIPAL ENGINEER TECHNICAL ANALYST | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | SENIOR MANAGER ENGINEERING | 989-598-5031 | jason.pionk@cmsenergy.com | ON JULY 20, 2023, AT APPROXIMATELY 11:11 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE NEAR THE INTERSECTION OF N. GRAND AVENUE & SAGINAW STREET, LANSING (INGHAM COUNTY) MICHIGAN. THE GAS DISTRIBUTION CREW ARRIVE ONSITE AT APPROXIMATELY 11:34 HOURS AND A GAS SERVICE WORKER (GSW) ARRIVED ONSITE AT APPROXIMATELY 11:43 HOURS. GAS DISTRIBUTION CREW CONFIRMED A GAS CONSTRUCTION (FIRST PARTY) EMPLOYEE DAMAGED A 6-INCH PLASTIC MEDIUM PRESSURE PIPELINE WHILE INSTALLING SHORING EQUIPMENT TO PERFORM TIE-IN WORK. THE GSW BEGAN MONITORING THE AREA FOR GAS MIGRATION AND GAS SERVICE EMPLOYEE(S) REMAINED ONSITE AND MONITORED THE AREA UNTIL THE GAS WAS CONTAINED. POLICE AND FIRE PERSONNEL WERE ONSITE AND EVACUATED ONE COMMERCIAL BUILDING BEFORE THE CREW ARRIVED. IT IS UNKNOWN THE NUMBER OF OCCUPANTS WITHIN THE BUILDING AT THE TIME IT WAS EVACUATED. POLICE AND FIRE ALSO ASSISTED CONSUMERS ENERGY EMPLOYEES WITH ROAD CLOSURES TO ENSURE THE SAFETY OF PEDESTRIANS AND VEHICLE TRAFFIC. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE DAMAGE AND SUBSEQUENT NATURAL GAS RELEASE. THE DISTRIBUTION CREW DEVELOPED A PLAN TO ISOLATE AND ARREST THE BLOWING GAS. BECAUSE THE LOCATION HAD A FOUR-WAY BACK-FEED TO THE DAMAGE LOCATION, EXCAVATION AT MULTIPLE LOCATIONS WAS REQUIRED. TWO PLASTIC PIPELINES WERE SQUEEZED, AND EXISTING CONTROL FITTINGS WERE UTILIZED AT TWO ADDITIONAL LOCATIONS TO STOP THE GAS FROM BLOWING. BECAUSE THE PIPELINE DEPTH WAS GREATER THAN 6-FEET, SHORING EQUIPMENT WAS NEEDED TO SAFELY ACCESS THE PIPELINE TO COMPLETE THE REPAIR. THE DAMAGE SEGMENT WAS CUT OUT AND REPLACED WITH 3-FOOT OF 6-INCH PLASTIC PIPELINE. THE PIPELINE WAS PURGED, AND NORMAL OPERATIONS RESUMED ON JULY 21, 2023, AT 04:20 HOURS.
2026-06-30 10:38 | NO | YES | NO | 20230045 | 39096 | 2023-08-25 16:06 | SUPPLEMENTAL FINAL | 32198 | MINNESOTA ENERGY RESOURCES CORPORATION | 2685 145TH STREET WEST | ROSEMOUNT | MN | 55068 | 2023-07-26 01:37 | CENTRAL | NO | 2023 | 19210 EUCLID PATH | FARMINGTON | DAKOTA | MN | 55024 | 44.6709 | -93.1789 |  |  |  | YES | [5 empty] | 2023-07-26 15:00 | 1374754 | 1374279 | NATURAL GAS |  | 0.25 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-07-27 01:37 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.25 | NO | 2 | 2023-07-26 01:37 |  |  |  | 2023-07-26 02:47 | 2023-07-26 01:37 | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2008 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ALUMINUM | [9 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 346700 | 360744.8820792556591 | 500 | 520.2550938552865 | 500 | 520.2550938552865 | 0 | 0 |  | 3.91 | 1 | 0.8723021582733812949640287769784172661871 | 0 | 0 | 347701 | 146907.1679962303489589928057553956834532 | 361786.2645691245054812949640287769784173 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 2 | 5 | 192.623 | 2008-01-11 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [218 empty] | LINDSAY K LYLE | ENGINEERING MANAGER | lindsay.lyle@minnesotaenergyresources.com | 651-322-8909 | 920-272-4000 | SHAWN WALLS | shawn.walls@minnesotaenergyresources.com | 651-322-8942 | LINDSAY LYLE | ENGINEERING MANAGER | 651-322-8909 | lindsay.lyle@minnesotaenergyresources.com | EMPLOYEE RESPONDED TO HOUSE FIRE THAT RESULTED IN FIRE DEPARTMENT SHUTTING OFF METER STOP VALVE. LIGHTNING STRIKE HIT A NEARBY TREE. BACK OF THE METER WAS CRACKED. UNSURE IF SECOND LIGHTNING STRIKE HIT METER DIRECTLY OR THE FIRE CAUSED A CRACK TO IGNITE.
2026-06-30 10:38 | NO | NO | NO | 20230046 | 38482 | 2023-08-31 11:24 | ORIGINAL FINAL | 30750 | MIDAMERICAN ENERGY COMPANY | 401 DOUGLAS STREET PO BOX 778 | SIOUX CITY | IA | 51101 | 2023-08-02 21:45 | CENTRAL | YES | 2023 | 1400 NW 86TH STREET | CLIVE | POLK | IA | 50325 | 41.6031 | -93.7365 | YES | YES | [7 empty] | 2023-08-02 22:33 | 1375040 | 1375241 | NATURAL GAS |  | 6771 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 17 | 2023-08-02 17:09 |  |  |  | 2023-08-02 17:56 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1968 | UNKNOWN |  |  |  |  | 16 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 4 | 2 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 2000 | 2081.020375421146 | 36755 | 38243.951949302110615 | 0 | 0 |  | 2.3395 | 15841 | 13818.1384892086330935251798561151079137 | 0 | 0 | 54596 | 27628.2928601768062100359712230215827338 | 54143.1108139318897085251798561151079137 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 90 | 90 | 125 | 192.619(A)(4) | 1988-10-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | CABLE TV | YES | 232061755 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CHRISTOPHER PAYER | GAS STANDARDS ENGINEER | chris.payer@midamerican.com | 7122777941 | 7122527369 | CHRISTOPHER PAYER | chris.payer@midamerican.com | 7122777941 | NICK NATION | VICE PRESIDENT GAS DELIVERY | 5156973256 | nick.nation@midamerican.com | HARTCO CABLE, INC. (THIRD PARTY CONTRACTOR) BORED INTO A 16-INCH NATURAL GAS STEEL MAIN WHILE INSTALLING CABLE TV AT 1400 NW 86TH STREET IN CLIVE, IOWA ON AUGUST 2, 2023. THE BORING HEAD PUNCTURED A FOUR-INCH BY TWO-INCH HOLE IN THE LOWER THIRD OF THE MAIN THAT WAS AT A SIX-FOOT DEPTH. NO SERVICES WERE INTERRUPTED AND THERE WAS NO IGNITION OR INJURIES. DUE TO THE SIZE AND DEPTH OF THE MAIN, IT TOOK A SIGNIFICANT AMOUNT OF TIME TO REPAIR THE DAMAGE AND 6.771 MCF OF NATURAL GAS WAS RELEASED TO ATMOSPHERE. THE NRC WAS INITIALLY NOTIFIED (REPORT 1375040) ON AUGUST 2 AND A 48-HOUR FOLLOW-UP REPORT WAS SUBMITTED (REPORT 1375241).
2026-06-30 10:38 | NO | YES | NO | 20230047 | 40057 | 2023-08-31 14:50 | SUPPLEMENTAL FINAL | 35505 | HASKINS GAS SERVICE | 1791 ROUTE 30 | DORSET | VT | 05251 | 2023-07-11 04:30 | EASTERN | YES | 2023 | 20 INNOVATION DRIVE | NORTH CLARENDON | RUTLAND | VT | 05759 | 43.5286 | -72.9561 | YES | YES |  | YES | YES |  |  |  |  | 2023-08-25 11:00 | 1377516 |  | PROPANE GAS |  | 181.81 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 30 | 2023-07-11 04:30 |  |  |  | 2023-07-11 05:00 | 2023-07-11 05:10 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | YES | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | UG 30,000 PROPANE TANK | 2005 | 1974 | [7 empty] | STEEL |  | CONTINUOUS WELDED |  | 0.05 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | 7000 | 7283.571313974011 | 200000 | 208102.0375421146 | 6000 | 6243.061126263438 | 50000 | 52025.50938552865 | CRANE & EXCAVATION | 1.5 | 273 | 238.138489208633093525179856115107913669 | 0 | 0 | 263273 | 111313.8740409886317050359712230215827338 | 273892.3178570893320935251798561151079137 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 9 | 9 | 14 | 192.619(A)(1) | 2005-07-09 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | AREA RECEIVED UNUSUAL AMOUNT OF RAIN IN SHORT PERIOD OF TIME, 9" IN A 12 HOUR PERIOD OF TIME. THIS HEAVY RAIN CAUSED SOIL TO BECOME OVER SATURATED WITH WATER AND FLOAT THE TANK. | NO | [183 empty] | YES | [34 empty] | VICKIE HASKINS | PRESIDENT | hasgas@aol.com | 802-867-5741 |  |  |  |  | VICKIE HASKINS | PRESIDENT | 8028675741 | hasgas@aol.com | RECEIVED A CALL FROM CLARENDON, VERMONT FIRE CHIEF, FOR SMELL OF PROPANE AT 20 INNOVATION DRIVE. UPON ARRIVAL THE GAS WAS SHUT OFF, NO LONGER RELEASING GAS. THE UNDERGROUND 30,000 GALLON PROPANE TANK HAD BECOME UNEARTHED ON ONE END. THE SUPPLY LINE TO REGULATOR CRACKED, AS TANK FLOATED OUT OF GROUND. NO DAMAGE TO CONTAINER OCCURRED. WE HAD EXCESSIVE RAIN AND FLOODING IN THE AREA IN VERMONT. THE TANK HAS BEEN BURIED AT THIS LOCATION FOR OVER 20 YEARS WITHOUT ISSUE. WE EVACUATED PRODUCT FROM THE TANK, THEN FLARED OFF REMAINING PROPANE VAPOR.
2026-06-30 10:38 | NO | YES | NO | 20230049 | 39871 | 2023-09-06 17:02 | SUPPLEMENTAL FINAL | 12878 | MOUNTAINEER GAS CO | 501 56TH ST. SE | CHARLESTON | WV | 25304 | 2023-08-07 17:58 | EASTERN | YES | 2023 | 1321 VIRGINIA AVE | DUNBAR | KANAWHA | WV | 25064 | 38.3647 | -81.7418 | [7 empty] | YES | FULL CIRCLE LEAK CLAMP | 2023-08-07 19:18 | 1375509 | 1375718 | NATURAL GAS |  | 209 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-08-07 17:58 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.56 | YES | 3 | 2023-08-07 19:30 | YES | OPERATOR | 2023-08-07 17:58 | 2023-08-07 14:40 | 2023-08-07 19:02 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 32 | YES | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1968 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 8.5 | 4 | [7 empty] | CLASS 3 LOCATION | 200000 | 208102.0375421146 | 3000 | 3121.530563131719 | 14000 | 14567.142627948022 | 10000 | 10405.10187710573 | EMERGENCY RESPONDERS | 6.739 | 1408 | 1228.201438848920863309352517985611510791 | 0 | 0 | 228408 | 96909.8818657251496618705035971223021583 | 237424.0140491489918633093525179856115108 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0.5 | 0.5 | 0.5 | 192.623 | 1968-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CAUSED BY EXCAVATION DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | YES | 18” – 36” |  | UTILITY | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2321330168 |  | Unknown | FACILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | PHILIP KINGREY | MANAGER-ENGINEERING AND COMPLIANCE | philipkingrey@mgcwv.com | 8884204427 |  | RICKY DYE | rickydye@mgcwv.com | 8884204427 | THOMAS WESTFALL | VP GAS SUPPLY AND TECHNICAL SERVICES | 8884204427 | thomaswestfall@mgcwv.com | 3J UNDERGROUND LLC WORKING FOR B N D SERVICES LLC WORKING FOR FIBER MANAGEMENT SERVICES LLC/SECURENET FIBER INTERNET TO INSTALL FIBER CONDUIT WITH A DIRECTIONAL BORE MACHINE. 3J FAILED TO HAND-DIG OR SPOT THE GAS FACILITIES WHILE BORING. ON THE FIRST OF TWO TRIES, THE BORING HEAD PUNCHED THROUGH THE CENTER OF THE 4 STEEL MAIN AND GAS MIGRATED INTO A NEARBY DAMAGED SEWER LINE. 3J THEN BORED A SECOND HOLE ABOVE THE MGC PIPE AND INSTALLED THE PLASTIC CONDUIT, CALLED MGC'S LOCATOR DIRECTLY TO REPORT AN ODOR OF GAS, AND LEFT THE SCENE BEFORE MGC LOCATOR ARRIVED ON SCENE AND NOTIFIED MGC DISPATCH. WHILE MGC PERSONNEL WERE INVESTIGATING THE ODOR OF GAS, THE HOUSE AT 1321 VIRGINIA AVE EXPLODED AND CAUGHT FIRE. ADDITIONAL MGC PERSONNEL AND EQUIPMENT WERE CALLED IN TO FIND AND REPAIR THE DAMAGED PIPE. DAMAGE TO THE PIPE SHOWS EVIDENCE OF MULTIPLE POINTS OF CONTACT.
2026-06-30 10:38 | NO | YES | NO | 20230050 | 38536 | 2023-09-12 16:02 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2023-08-14 10:46 | EASTERN | YES | 2023 | 24244 STATE ROUTE 37 | WATERTOWN | JEFFERSON | NY | 13601 | 44.0165 | -75.9016 | [5 empty] | YES |  |  |  | 2023-08-14 17:50 | 1376286 | 1376491 | NATURAL GAS |  | 223 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-08-14 10:57 | YES | OPERATOR | 2023-08-14 15:05 | 2023-08-14 10:57 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1987 | UNKNOWN |  |  |  |  | 6 | ASTM D2513 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 24 | 4 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 70134 | 72975.141504893326782 | 309939 | 322494.687068827285047 | 0 | 0 |  | 3.48 | 776 | 676.906474820143884892086330935251798561 | 0 | 0 | 380849 | 161135.6436725158913014172661870503597122 | 396146.7350485407557138920863309352517986 | 39 | 2 | 214 | 0 | 0 | 214 | 41 | 40 | 40 | 45 | 192.621 M | 1986-10-30 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROL ROOM ISSUES WERE THE CAUSE OF OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | TRENCHER | WATER | YES | 08083001181 | U-DIG |  | CONTRACT LOCATOR | NO | YES | 18 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 5169030596 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | CONTRACTOR STRUCK AND DAMAGED NATIONAL GRID'S 6-INCH PLASTIC DISTRIBUTION MAIN, WHILE TRENCHING TO INSTALL A NEW WATER MAIN. THIS CAUSED AN UNPLANNED INTERRUPTION OF OVER 230 CUSTOMERS IN THE AREA. THE 6-INCH MAIN WAS PROPERLY MARKED OUT, AND HAD INTACT TRACER WIRE OVER IT. THE CONTRACTOR DID NOT FOLLOW PROPER HAND EXCAVATING AND DID NOT KEEP MARKINGS VISIBLE AS THEY PROGRESSED IN EXCAVATING. THE INCIDENT OCCURRED ON MONDAY 8/14 AT APPROX. 10:49 AM, AND NATIONAL GRID ARRIVED AT 10:57; HOWEVER, WE WERE NOT AWARE THAT THIS INCIDENT WOULD POTENTIALLY MEET PHMSA REPORTING LIMITS OF $137K MINIMUM THRESHOLD UNTIL TUESDAY 8/15 AT 4:20 PM. UPON CONFIRMATION, THE NRC WAS NOTIFIED AT 5:50 PM. AS OF SEPTEMBER 9, ALL CUSTOMERS HAVE BEEN RESTORED EXCEPT FOR INACTIVE/REMOVED METERS. TOTAL INACTIVE/REMOVED METERS IS 8. SUPPLEMENTAL REPORT FILED 9/13/2023 TO REVISE INCIDENT REPORTING TIME TO 10:46 ON 8/14/2023.
2026-06-30 10:38 | NO | YES | NO | 20230051 | 38532 | 2023-09-13 09:58 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2023-08-27 02:40 | CENTRAL | YES | 2023 | 1630 12TH AVENUE NORTH | NASHVILLE | DAVIDSON | TN | 37208 | 36.1782 | -86.8042 | [5 empty] | YES |  |  |  | 2023-08-27 07:59 | 1377405 | 1377582 | NATURAL GAS |  | 6.706 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-08-27 02:40 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 6.7 | NO | 3 | 2023-08-27 02:40 |  |  |  | 2023-08-27 03:28 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2002 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | VEHICLE BROKE RISER VALVE OFF. | [5 empty] | CLASS 3 LOCATION | 150000 | 156076.52815658595 | 0 | 0 | 5000 | 5202.550938552865 | 0 | 0 |  | 3.3 | 22 | 19.19064748201438848920863309352517985612 | 0 | 0 | 155022 | 65504.5593857017826978417266187050359712 | 161298.2697426208293884892086330935251799 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 60 | 60 | 75 | 192.619(A)(2) | 2002-04-03 | PRESSURE DID NOT EXCEED MAOP | NONE |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VEHICLE HIT A GAS METER TO A HOME. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | NO | UNKNOWN | PASSENGER CAR | ROADWAY | 30 | NO | [142 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER-PIPELINE SAFETY GOVERNANCE | 704-731-4618 | farris.berry@duke-energy.com | A DRIVER TRAVELING AT A HIGH RATE OF SPEED, LOST CONTROL OF HIS VEHICLE, RUNNING INTO THE GAS METER AND HOME CAUSING A NATURAL GAS FED HOUSE FIRE. BOTH THE GAS METER AND HOME WAS DESTROYED.
2026-06-30 10:38 | NO | YES | NO | 20230052 | 38876 | 2023-09-15 17:50 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2023-08-16 22:00 | CENTRAL | YES | 2023 | 1202 FRANKIE ST | NEW IBERIA | IBERIA | LA | 70560 | 29.9772 | -91.8305 |  |  |  | YES | [5 empty] | 2023-08-17 14:08 | 1376485 | 1376682 | NATURAL GAS |  | 0.824 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-08-16 21:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.03 | NO | 0 | 2023-08-16 21:07 |  |  |  | 2023-08-16 21:36 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | METER INSTALLATION HIT BY VEHICLE. | CLASS 3 LOCATION | 450000 | 468229.58446975785 | 0 | 0 | 291 | 302.788464623776743 | 0 | 0 |  | 4.05 | 3 | 2.61690647482014388489208633093525179856 | 0 | 0 | 450294 | 190254.2327709788238179784172661870503597 | 468534.9898408564468868848920863309352518 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 20 | 20 | 60 | 192.619(A)(4) | 2000-01-03 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 8 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | SMALL TRUCK | ROADWAY | 14 | NO | [142 empty] | JAMES TODD HEBERT | OPERATIONS SPECIALIST | james.hebert@centerpointenergy.com | 337-256-2161 | 337-373-1520 | DOUGLAS BOUDREAUX JR. | douglas.boudreauxjr@centerpointenergy.com | 337-475-6362 | DOUGLAS BOUDREAUX JR. | REGIONAL OPERATIONS DIRECTOR | 337-475-6362 | douglas.boudreauxjr@centerpointenergy.com | CALL RECEIVED @ 21:07 ON AUGUST 16, 2023. NEW IBERIA POLICE DEPT REPORTING THAT TRAILER BACKED OVER GAS METER. CALL WAS THEN UPDATED TO STATE THAT HOME IS NOW ON FIRE AND FIRE DEPT IS IN ROUTE. EMERGENCY ORDER CREATED AND DISPATCHED TO CNP FIRST RESPONDER @ 21:16. CNP FIRST RESPONDER ARRIVED 21:36, METER WAS OFF BY FIRE DEPT UPON ARRIVAL. UPON FURTHER INVESTIGATION, THE REGULATOR WAS DAMAGED BY THE VEHICLE THAT STRUCK IT AND WAS REMOVED AT THE REQUEST OF THE FIRE DEPARTMENT LATER THAT EVENING. DURING THE CNP INVESTIGATION IT WAS DETERMINED THAT THE NEIGHBOR STRUCK THE METER INSTALLATION CAUSING THE LEAK THAT WAS ORIGINALLY REPORTED. UPON RECEIVING ESTIMATED DAMAGES FROM FIRE REPORT ON AUGUST 17, 2023, IT WAS DETERMINED THAT INCIDENT CRITERIA WAS MET AND CALL WAS MADE TO NRC.
2026-06-30 10:38 | NO | NO | NO | 20230053 | 38666 | 2023-09-20 14:23 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2023-08-25 03:10 | EASTERN | YES | 2023 | 14249 SPERRY ROAD | NEWBURY | GEAUGA | OH | 44065 | 41.4793 | -81.2881 |  |  | YES | YES | [5 empty] | 2023-08-25 03:25 | 1377222 | 1377291 | NATURAL GAS |  | 2178 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-08-25 12:20 | OPERATOR/CONTRACTOR |  | 2178 | NO | 3 | 2023-08-25 02:53 |  |  |  | 2023-08-25 02:47 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | OTHER | HP FIRST CUT REGULATOR |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | HP FIRST CUT REGULATOR | UNKNOWN | UNKNOWN | [7 empty] | OTHER | HP FIRST CUT REGULATOR | [9 empty] | OTHER | [8 empty] | ELECTRICAL ARCING FROM DOWN POWER LINE. | CLASS 3 LOCATION | 0 | 0 | 3000 | 3121.530563131719 | 5000 | 5202.550938552865 | 0 | 0 |  | 4.3223 | 9414 | 8211.852517985611510791366906474820143885 | 0 | 0 | 17414 | 10068.077397860310158273381294964028777 | 16535.9340196701955107913669064748201439 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 50 | 50 | 60 | 192.619(C) | 1969-07-25 | PRESSURE DID NOT EXCEED MAOP | DRIP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [136 empty] | YES | [31 empty] | ALLISON WALTERS-THOMPSON | MANAGER GAS OPERATIONS | a.walters-thompson@dominionenergy.com | 2167899152 |  | ALLISON WALTERS-THOMPSON | a.walters-thompson@dominionenergy.com | 2167899152 | ALLISON S WALTERS-THOMPSON | MANAGER GAS OPERATIONS | 2167899152 | a.walters-thompson@dominionenergy.com | DURING SEVERE WINDS OCCURRING IN NE OHIO, A LIVE POWER LINE FELL ONTO AN HP FIRST CUT REGULATOR AT 14249 SPERRY RD NEWBURY, OH CAUSING APPROXIMATELY A 2-INCH DIAMETER HOLE IN THE TOP OF THE RELIEF VALVE. THE HOLE CAUSED MP GAS TO ESCAPE AND IGNITE. ALTHOUGH THERE WAS AN IGNITION OF NATURAL GAS, THERE WAS NO EXPLOSION. DAMAGES DID NOT EXCEED $139,700, NOR DID GAS LOSS EXCEED 3 MILLION CUBIC FEET, AND THERE WERE NO INJURIES NOR FATALITIES. RESIDENTS AT 14249 SPERRY ROAD (A FEMALE AND TWO CHILDREN) WERE EVACUATED. GAS WAS ISOLATED AT 9:23AM. THE CAUSE FOR THE DELAY IN GAS SHUT OFF WAS DUE TO LIVE POWER LINES LAYING IN WATER NEXT TO THE HP FIRST CUT REGULATOR. ONCE THE POWER COMPANY (THE ILLUMINATING COMPANY) CONFIRMED IT WAS SAFE TO ENTER THE YARD, DEO FIRST RESPONDERS EXTINGUISHED THE FLAME AND ISOLATED THE LEAK. REPAIRS WERE MADE AND THE CUSTOMER WAS BACK IN-SERVICE THE SAME DAY.
2026-06-30 10:38 | NO | YES | NO | 20230054 | 38726 | 2023-09-20 18:01 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2023-08-21 12:17 | PACIFIC | YES | 2023 | MISSION LAKES BLVD & WESTERN AVE | DESERT HOT SPRINGS | SAN BERNARDINO | CA | 92240 | 33.9763 | -116.5537 | YES |  |  |  |  | YES |  |  |  | 2023-08-21 10:26 | 1376821 | 1377032 | NATURAL GAS |  | 8436 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-08-21 09:58 | NO |  |  | 2023-08-21 09:58 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 46 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1964 | UNKNOWN |  |  |  |  | 6 | 5LX-42 | UNKNOWN | STEEL |  | OTHER | DT-ERW / SMLS | 0.16 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 6 | 6 |  | CLASS 1 LOCATION | 0 | 0 | 3500000 | 3641785.6569870055 | 60000 | 62430.61126263438 | 0 | 0 |  | 6 | 50616 | 44152.4460431654676258992805755395683453 | 0 | 0 | 3610616 | 1540092.04996150708517985611510791366906 | 3748368.71429280534762589928057553956835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 385 | 395 | 192.619(A)(2) | 2012-09-04 | PRESSURE DID NOT EXCEED MAOP | OTHER | SELF-SEASONED |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, DAMAGE CAUSED BY STORM-RELATED EVENT. THUS THERE WERE NO ISSUES FROM THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | HURRICANE HILLARY | YES | YES | [217 empty] | SANDIE TO | PIPELINE SAFETY AND COMPLIANCE ADVISOR | slto1@socalgas.com | 978-719-3485 | 909-335-3989 | SANDIE TO | slto1@socalgas.com | 978-719-3485 | SANDIE TO | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 978-719-3485 | slto1@socalgas.com | ON 8/21/2023, SOCALGAS CREWS RESPONDED TO A PIPELINE RUPTURE ON SL 41-53 AT MISSION LAKES BLVD & WESTERN AVE, DESERT HOT SPRINGS, SAN BERNARDINO. UPON INVESTIGATION, THE 6-INCH DISTRIBUTION LINE RUPTURED FROM RUSHING WATER FOUND IN AREA WITH DEBRIS AND EARTH IN THE EXTREME WEATHER CONDITIONS OF HURRICANE HILLARY. THE DISTRIBUTION PIPELINE HAD BEEN ISOLATED AND IS STILL CURRENTLY OUT OF SERVICE WITH REPAIRS ONGOING. NO INJURIES OR FATALITIES RESULTED FROM THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO GAS RELEASE AND DAMAGES EXCEEDING $139,700. UPDATE 10/27/2023: > PART A4 EARLIEST LOCAL TIME INCIDENT REPORTING CRITERIA WAS MET: 12:17 > REPAIRS HAVE BEEN COMPLETED AS OF 09/22/2023, AND SERVICE HAD BEEN RESTORED AS OF 09/25/2023. > PART G2 NATURAL FORCE DAMAGE SUB-CAUSE CHANGED TO "HEAVY RAINS/FLOODS". SPECIFICATION: "OTHER, HURRICANE HILLARY". UPDATE 10/31/2023: > UPDATED REPORT TYPE TO "FINAL"
2026-06-30 10:38 | NO | YES | YES | 20230056 | 38597 | 2023-09-28 09:51 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2023-08-31 17:11 | CENTRAL | YES | 2023 | 200 S. AVENUE A | LONGVIEW | GREGG | TX | 75604 | 32.5053 | -94.7927 | [5 empty] | YES |  |  |  | 2023-08-31 20:29 | 1377864 |  | NATURAL GAS |  | 53.47 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2023-08-31 17:11 | ALLOWED TO BURN OUT |  | 53.47 | NO | 0 | 2023-08-31 17:11 | YES | OPERATOR | 2023-08-31 17:11 | 2023-08-31 17:11 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1925 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.094 | [6 empty] | OTHER | [8 empty] | RUBBER STOPPER BLEW OUT RELEASING GAS AS WELDER WAS INSTALLING END CAP. | CLASS 3 LOCATION | 0 | 0 | 2500 | 2601.2754692764325 | 2500 | 2601.2754692764325 | 0 | 0 |  | 2.82 | 151 | 131.717625899280575539568345323741007194 | 0 | 0 | 5151 | 2219.821305317370107913669064748201438849 | 5334.268564452145575539568345323741007194 | 2 | 0 | 3 | 1 | 0 | 3 | 2 | 48 | 48 | 60 | 192.619(A)(3) | 1925-01-01 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | INCORRECT OPERATION | INCORRECT EQUIPMENT | [222 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED |  |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [45 empty] | YES |  |  | YES | LESLIE DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 | CLINT GOEN | clinton.goen@centerpointenergy.com | 832-374-0745 | JERRY GANN | DIRECTOR REGIONAL OPERATIONS | 713-967-7101 | jerry.gann@centerpointenergy.com | ON AUGUST 31ST, 2023, A CONSTRUCTION CREW FROM CENTERPOINT ENERGY INITIATED REPAIRS TO CORRECT A NON-HAZARDOUS GRADE C LEAK. A DECISION WAS MADE TO ELIMINATE THE AFFECTED PIPE BY ABANDONING THE DEAD-END SECTION. THE CREW HAD SUCCESSFULLY STOPPED THE FLOW OF GAS AND USED A 4-WHEEL CUTTER TO REMOVE THE PIPE. ONCE THE PIPE WAS CUT, THE CREW BEGAN TO INSTALL THE WELD CAP, AT WHICH TIME THEY EXPERIENCED AN IGNITION OF GAS. THE IGNITION RESULTED IN THE INJURY OF ONE CENTERPOINT ENERGY EMPLOYEE. THE EMPLOYEE WAS TRANSPORTED TO GOOD SHEPHERD HOSPITAL IN LONGVIEW, TX, FOR TREATMENT, THEN AT 20:04, EMPLOYEE WAS TRANSFERRED TO PARKLAND HOSPITAL IN DALLAS, TX FOR FURTHER EVALUATION.
2026-06-30 10:38 | NO | YES | NO | 20230057 | 39364 | 2023-10-06 15:50 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD N.E. SUITE 20 | ALBUQUERQUE | NM | 87109 | 2023-09-07 14:18 | MOUNTAIN | YES | 2023 | 4100 RIDGELEY DR NE | ALBUQUERQUE | BERNALILLO | NM | 87108 | 35.0804 | -106.5988 | [5 empty] | YES |  | YES | 2X3 LEAK CLAMP ON MAIN AND PLUGGED OFF RISER | 2023-09-07 18:30 | 1378470 | 1378626 | NATURAL GAS |  | 1 | 0.083 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-09-07 14:18 | OTHER | NO RESIDUAL FIRE AFTER INITIAL IGNITION EVENT. | 1 | YES | 19 | 2023-09-07 18:16 |  |  |  | 2023-09-07 14:52 | 2023-09-07 18:00 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 45 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2017 | 2017 |  |  |  |  | 2 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | LEAK |  |  | OTHER | LACK OF COMPLETE FUSION | [5 empty] | CLASS 3 LOCATION | 500000 | 520255.0938552865 | 0 | 0 | 11250 | 11705.73961174394625 | 0 | 0 |  | 4.99 | 5 | 4.36151079136690647482014388489208633094 | 0 | 0 | 511255 | 216011.3934866867050449640287769784172662 | 531965.1949778218131564748201438848920863 | 0 | 0 | 10 | 2 | 0 | 10 | 0 | 56 | 56 | 60 | 192.619(A)(3) | 2015-11-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXISTING SCADA EQUIPMENT WOULD HAVE GIVEN NO INDICATION OF AN ISSUE AT THIS LOCATION. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 2017 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [7 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | ROBERT R SMITH | MANAGER PSMS TECHNICAL TRAINING | robert.smith@nmgco.com | 5056973169 |  |  |  |  | ANDREA MARTINEZ | DIRECTOR SAFETY PIPELINE SAFETY TECH TRAINING | 5056973518 | andrea.martinez@nmgco.com | ON SEPTEMBER 7, 2023, AN EXPLOSION OCCURRED AT 14:18 AT 4100 RIDGELEY AVE NE IN ALBUQUERQUE, NM 87108. AT 14:37, NMGC WAS NOTIFIED BY ALBUQUERQUE FIRE AND RESCUE OF A HOUSE EXPLOSION. NMGC ARRIVED AT THE PROPERTY AT 14:52. GAS WAS ESCAPING FROM THE RISER WHEN THE NMGC TECHNICIAN ARRIVED. GAS WAS UNDER CONTROL AT 15:33 AT THE RISER. NMGC BEGAN PROBING FOR GAS AT 15:33. THE NMGC RESPONDING CREW DISCOVERED GAS CONCENTRATION READINGS OF 100% GAS IN THE STREET DIRECTLY IN FRONT OF 4100 RIDGELEY AVE NE. NMGC EXPOSED THE 2-INCH PE PIPE, WHERE THE SECTION OF MAIN WAS OFFSET WITH A DOGLEG THAT WAS INSTALLED IN 2017. A 2X3-INCH LEAK CLAMP WAS INSTALLED AS A TEMPORARY REPAIR. THE SECTION OF MAIN WAS SQUEEZED OFF AT 21:30 AND CAPPED AS A PERMANENT REPAIR. THERE WERE TWO RESIDENTS OF 4100 RIDGELEY AVENUE WHO WERE TREATED FOR NON-LIFE THREATENING INJURIES AND RELEASED. AT 17:15, GAS ODORANT TESTING WITH A HEATH ODOROMETER WAS CONDUCTED REVEALING SUFFICIENT ODORANT AT 0.50% GAS-IN-AIR (12.5% LEL). ADDITIONAL GAS ODORANT TESTING WITH A HEATH ODOROMETER WAS PERFORMED SHOWING APPROPRIATE ODORANT LEVELS. LABORATORY TESTS WERE CONDUCTED ON OCTOBER 25, 2023 WHICH REVEALED A LACK OF COMPLETE FUSION ON BUTT WELD. REGARDING QUESTIONS PART A #7 AND PART A #21C, THE FORM DOES NOT ALLOW AN ENTRY OF "UNKNOWN" BECAUSE A CALCULATION CANNOT BE PERFORMED DUE TO LIMITED OR UNKNOWN INFORMATION NEEDED TO PERFORM THE CALCULATION.
2026-06-30 10:38 | NO | YES | NO | 20230058 | 39469 | 2023-10-09 16:08 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2023-09-09 05:58 | EASTERN | YES | 2023 | 532 WEST ELM STREET | ONEIDA | MADISON COUNTY | NY | 13421 | 43.2233 | -75.4601 | [5 empty] | YES |  |  |  | 2023-09-09 10:12 | 1378590 | 1378603, 1378732 | NATURAL GAS |  | 13.24 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-09-09 05:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 4.51 | YES | 7 | 2023-09-09 03:14 |  |  |  | 2023-09-09 04:05 | 2023-09-09 04:05 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1990 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.063 |  | 3408 | MECHANICAL PUNCTURE | 0.8 | 0.8 | [7 empty] | CLASS 1 LOCATION | 140000 | 145671.42627948022 | 1700 | 1768.8673191079741 | 2800 | 2913.4285255896044 | 0 | 0 |  | 3.06 | 41 | 35.76438848920863309352517985611510791367 | 0 | 0 | 144541 | 61081.7107236719961187050359712230215827 | 150389.4865126670071330935251798561151079 | 0 | 0 | 6 | 0 | 0 | 7 | 0 | 41.5 | 41.5 | 45 | 192.621 M | 1990-08-27 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO CONTROLLER ACTIONS THAT COULD BE TAKEN TO PREVENT THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  |  |  | YES | POLICE ON-SITE. DAMAGE BY PRIVATE VEHICLE (NON-HOME OWNER). DETAILS OF CITATION UNKNOWN. | NO | UNKNOWN | PASSENGER CAR | OFF-ROAD | 162 | YES |  |  |  |  | YES | YES | METER LOCATED AT BUILDING WALL, OFF ROAD/DRIVEWAY. | [135 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5164924469 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 5169030596 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | ON SATURDAY, SEPTEMBER 9, 2023, AT 03:14, THE NIAGARA MOHAWK POWER CORPORATION D/B/A NATIONAL GRID ("NATIONAL GRID" OR THE "COMPANY") UPSTATE NY (UNY) GAS DISPATCH WAS NOTIFIED BY THE MADISON COUNTY 911 CALL CENTER THAT A MEMBER OF THE PUBLIC (WHO WAS SUBSEQUENTLY ARRESTED AND CHARGED WITH 30 SEPARATE CRIMES, INCLUDING GRAND LARCENY 3RD AND 4TH DEGREE, CRIMINAL POSSESSION OF STOLEN PROPERTY, CRIMINAL MISCHIEF, RECKLESS ENDANGERMENT, UNAUTHORIZED USE OF A MOTOR VEHICLE, DWI, AND TRAFFIC VIOLATION) DROVE A VEHICLE INTO THE GAS METER OF A RESIDENCE AT 532 WEST ELM STREET. THE GAS SYSTEM AT THE LOCATION BEGAN TO LEAK GAS. THE UNY GAS DISPATCH ORGANIZATION INITIATED ITS AFTER-HOURS CALL-OUT PROCEDURES. A REPRESENTATIVE FROM NATIONAL GRID'S CUSTOMER METER SERVICE (CMS) ORGANIZATION ACCEPTED THE CALL OUT AT 03:24 AND ARRIVED AT THE SITE AT 04:05 AFTER THE LOCAL FIRE DEPARTMENT HAD EVACUATED SIX OF THE NEIGHBORING HOMES AT 521, 526, 529, 531, 537, AND 538 WEST ELM STREET. THE CMS REPRESENTATIVE CONFIRMED THAT GAS AT 532 WEST ELM STREET WAS BEING RELEASED AND DETERMINED THAT THE VEHICLE DESTROYED THE RISER CAUSING GAS TO BE RELEASED UNCONTROLLABLY. THE CMS REPRESENTATIVE FOLLOWED STANDARD OPERATING PROCEDURES TO LOCATE AN ALTERNATIVE POINT OF SHUT OFF (THE PRIMARY SHUT OFF AT THE RISER WAS DESTROYED) AND DETERMINED THERE WAS NO CURB VALVE PRESENT. AT 04:25 THE CMS REPRESENTATIVE CALLED FOR ADDITIONAL RESOURCES FROM GAS FIELD OPERATIONS (GFO). UNY GAS DISPATCH INITIATED ITS AFTER-HOURS CALL-OUT PROCEDURES FOR GFO SUPPORT AT 04:41. A REPRESENTATIVE FROM NATIONAL GRID'S GFO ORGANIZATION ACCEPTED THE CALL OUT AT 04:46 AND ARRIVED AT THE REPORTED SITE AT 06:31. WHILE THE GFO CREW WAS EN ROUTE, AN EXPLOSION OCCURRED AT APPROXIMATELY 05:55. THE CMS FIRST RESPONDER NOTIFIED UNY GAS DISPATCH OF THE EXPLOSION AT 05:58. FOLLOWING GAS FIELD OPERATIONS (GFO) ARRIVAL AT THE SCENE AT 06:31, THE CREW EXCAVATED THE SERVICE TO ACCESS THE GAS DISTRIBUTION SERVICE PIPE AND SHUT OFF GAS SUPPLY TO THE INCIDENT LOCATION AT 532 WEST ELM STREET. GAS WAS CONTROLLED AT 07:10. AFTER WITNESSING THE EXPLOSION, THE CMS FIRST RESPONDER CALLED FOR FURTHER CMS SUPPORT. ADDITIONAL CMS PERSONNEL ARRIVED ON SCENE TO ASSIST AND THEN RELIEVE THE INITIAL FIRST RESPONDER AND TO SHUT OFF GAS SERVICE TO FIVE OF THE SURROUNDING HOMES AT: 526, 529, 531, 537 AND 538 WEST ELM STREET AND REMOVE THE GAS METERS. THE HOUSE LOCATED AT 521 WEST ELM STREET WAS EVACUATED BUT GAS SERVICE WAS NOT SHUT OFF. IT WAS LATER REPORTED THAT THE VEHICLE INVOLVED IN THE ACCIDENT WAS STOLEN. NATIONAL GRID DETERMINED THAT THE VEHICLE HAD SEVERED THE SERVICE RISER IN ADDITION TO DAMAGING THE METER. NOTE, PART A, QUESTION 22, REPRESENTS A MINIMUM ESTIMATE OF 1 CUSTOMER PER RESIDENCE EVACUATED.
2026-06-30 10:38 | NO | YES | NO | 20230059 | 38679 | 2023-10-20 10:36 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2023-09-20 11:27 | EASTERN | YES | 2023 | 2049 SYLVAN ROAD SW | ATLANTA | FULTON | GA | 30310 | 33.6983 | -84.4182 | YES | YES |  |  |  | YES |  |  |  | 2023-09-20 11:35 | 1379609 | 1379789 | NATURAL GAS |  | 500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-09-20 10:48 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 500 | NO | 3 | 2023-09-20 10:48 |  |  |  | 2023-09-20 10:54 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2001 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 3.7 | 3.7 | [7 empty] | CLASS 3 LOCATION | 300000 | 312153.0563131719 | 87500 | 91044.6414246751375 | 68196 | 70958.632761110236308 | 0 | 0 |  | 2.815 | 1408 | 1228.201438848920863309352517985611510791 | 0 | 0 | 457104 | 193536.0516074225843578705035971223021583 | 475384.5319378061946713093525179856115108 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 45 | 60 | 192.619(A)(2) | 2001-04-16 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 5.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TRAFFIC SIGNAL | YES | 230731005543 |  |  | CONTRACT LOCATOR | YES | YES | 24 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [169 empty] | YES | RALPH MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK LONN | DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@southernco.com | A THIRD-PARTY PARTY EXCAVATOR (CABLE EAST) STRUCK AND DAMAGED AN ATLANTA GAS LIGHT COMPANY (AGLC) 4-INCH PLASTIC GAS MAIN WHILE DIRECTIONALLY BORING TO INSTALL TRAFFIC SIGNAL CONDUIT LINES NEAR 2049 SYLVAN ROAD SW, ATLANTA. ESCAPING GAS FROM THE DAMAGE WAS IGNITED BY AN UNKNOWN IGNITION SOURCE AND A SUBSEQUENT FIRE OCCURRED AT THE STREET RESULTING IN SIGNIFICANT PROPERTY DAMAGE. AT LEAST ONE VEHICLE AS WELL AS A TRACTOR AND THE DIRECTIONAL BORING RIG WERE DAMAGED IN THE FIRE; THERE WAS ALSO HEAT DAMAGE TO A LARGE COMMERCIAL SIGN AND A DIESEL PUMP AT A NEARBY CHEVRON GASOLINE STATION. UPON ARRIVAL, AGLC PERSONNEL SECURED THE AREA AND MONITORED THE SURROUNDING AREA FOR GAS. GAS WAS SHUT-OFF TO THE DAMAGED AREA AT 12:06 PM BY OPERATING TWO (2) VALVES AND PERFORMING ONE (1) SQUEEZE OFF OPERATION. A LOCATE REQUEST WAS MADE ON SEPTEMBER 6, 2023, BY CABLE EAST (EXCAVATOR) TO "LOCATE THE INTERSECTION OF SR 166 RAMPS EAST BOUND OFF & ON AND SYLVAN RD SW 200' IN ALL DIRECTION ENTIRE ROW". AGLC FACILITIES WERE MARKED BY STAKE CENTER LOCATING TO SATISFY THIS REQUEST ON SEPTEMBER 20, 2023, AT 10:19 AM. INVESTIGATION OF THE SITE REVEALED THAT THE LOCATE MARKS WERE NOT ACCURATE AT THE POINT OF DAMAGE; THE NEAREST LOCATE MARK TO WHERE THE 4-INCH PLASTIC MAIN WAS DAMAGED WAS APPROXIMATELY SEVEN (7) FEET AWAY. BECAUSE THE EXCAVATOR DID NOT VERIFY THE LOCATION OF AGLC FACILITIES BY POT HOLING AND INSTEAD BLINDLY CROSSED THE MARKS ON THE GROUND WHICH RAN PARALLEL TO THE ACTUAL LOCATION OF THE GAS MAIN, THE GAS MAIN WAS DAMAGED. HAD THE EXCAVATOR POTHOLED, IT WOULD HAVE DETERMINED THE LOCATION OF THE MAIN WAS NOT CONSISTENT WITH THE MARKS ON THE GROUND AT THE POINT OF CROSSING AND TAKEN STEPS TO DETERMINE THE ACTUAL LOCATION OF THE GAS MAIN. ADDITIONAL NRC REPORT NUMBER 1379789 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2026-06-30 10:38 | NO | YES | NO | 20230060 | 39040 | 2023-10-20 16:32 | SUPPLEMENTAL FINAL | 2188 | CENTRAL FLORIDA GAS CORP | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2023-09-21 11:38 | EASTERN | YES | 2023 | TURKEY CREEK RD. | PLANT CITY | HILLSBOROUGH | FL | 33566 | 27.9888 | -82.1705 | YES | YES | [7 empty] | 2023-09-21 17:40 | 1379739 | 1379888 | NATURAL GAS |  | 98 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-09-21 11:38 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-09-21 12:25 | 2023-09-21 12:25 | 2023-09-21 12:25 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 96 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2010 | 2010 |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 160000 | 166481.63003369168 | 1000 | 1040.510187710573 | 0 | 0 |  | 3.8 | 372 | 324.496402877697841726618705035971223022 | 0 | 0 | 161372 | 68288.2658153919793453237410071942446043 | 167846.636624279950841726618705035971223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 165 | 175 | 192.619(A)(2) | 2010-05-06 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 251301840 |  | NO | CONTRACT LOCATOR | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [169 empty] | YES | MICHAEL MCCARTY |  | mmccarty@fpuc.com | 863 224 0417 |  | MICHAEL MCCARTY | mmccarty@fpuc.com | 863 224-0417 | MICHAEL MCCARTY |  | 863 224-0417 | mmccarty@fpuc.com | A SUB-CONTRACTOR FOR A SITE CONTRACTOR WAS DRIVING STEEL SHEET SHORING IN THE GROUND ON TURKEY CREEK RD. THE SHEET SHORING STOPPED ABOUT 8' DEEP AND WOULD NOT DRIVE ANY FURTHER. THE SITE CONTRACTOR USED A TRACK HOE TO DIG DOWN TO SEE WHAT THE OBSTRUCTION WAS AND STRUCK A 6" STEEL GAS MAIN AND POKED A SMALL HOLE IN THE PIPE. FLORIDA PUBLIC UTILITIES (CENTRAL FLORIDA GAS) TECHNICIANS WERE DISPATCHED AND CLOSED A KEY VALVE AND A SYSTEM VALVE ON EITHER SIDE OF THE DAMAGE, STOPPING THE ESCAPING NATURAL GAS. DUE TO THE DEPTH OF THE PIPE AND EXTENSIVE GROUND WATER, A NEW SECTION OF STEEL PIPE WILL NEED TO BE INSTALLED BY DIRECTIONAL BORE. THE SUB-CONTRACTOR DID NOT HAVE A VALID LOCATE TICKET, THE SITE CONTRACTOR WHO HIT AND PUNCTURED THE LINE DID HAVE MULTIPLE VALID LOCATE TICKETS. A CONTRACT LOCATOR FOR FPU HAD PREVIOUSLY MARKED MULTIPLE TICKETS BUT DID NOT MARK THE LAST UPDATE TICKET AND PUT IN THE NOTES THAT IT WAS AN ONGOING PROJECT. A CONTRACTOR FOR CENTRAL FLORIDA GAS BEGAN REPLACING THE DAMAGED PIPE BY DIRECTIONAL BORE ON 9/26/23. THE NEW 6" MAIN WAS INSTALLED, PIGGED, TESTED, TIED IN, PURGED AND PUT BACK IN SERVICE ON 10/17/23. 12/29/2023 - FINAL REPORT. NO SIGNIFICANT CHANGES TO PREVIOUSLY SUBMITTED INFORMATION. 1/4/2024 - NEW SUPPLEMENTAL AND FINAL TO MAKE CHANGES TO A (4) AND C (3A) SUGGESTED BY PHMSA SENIOR INVESTIGATOR, ACCIDENT INVESTIGATION DIVISION.
2026-06-30 10:38 | NO | YES | NO | 20230061 | 40078 | 2023-10-23 13:56 | SUPPLEMENTAL FINAL | 15462 | PECO ENERGY CO | 2301 MARKET STREET, S9-1 | PHILADELPHIA | PA | 19103 | 2023-09-23 13:15 | EASTERN | YES | 2023 | 14 W PROVIDENCE ROAD | YEADON | DELAWARE | PA | 19050 | 39.9297 | -75.2709 | [7 empty] | YES | NONE | 2023-09-23 16:39 | 1379904 | 1380020 | NATURAL GAS |  | 470 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-09-23 10:25 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 121 | 2023-09-23 10:25 |  |  |  | 2023-09-23 10:49 | 2023-09-23 10:49 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | ELECTRICAL ARCING - SEE PART H | [5 empty] | CLASS 3 LOCATION | 350000 | 364178.56569870055 | 10582 | 11010.678806353283486 | 75703 | 78769.742740253507819 | 0 | 0 |  | 6.31 | 2966 | 2587.248201438848920863309352517985611511 | 0 | 0 | 439251 | 186441.5775571425117076618705035971223022 | 456546.2354467461902258633093525179856115 | 0 | 0 | 6 | 0 | 0 | 7 | 0 | 57 | 57 | 99 | 192.619(C) | 1969-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 7.2 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | WAS NOT RELATED TO ABNORMAL PRESSURE CONDITION | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [138 empty] | YES | [29 empty] | JOHN STAUDENMAYER | SENIOR ENGINEER | john.staudenmayer@exeloncorp.com | 856-313-6432 |  |  |  |  | ROBERT EDLING | MANAGER GAS STANDARDS AND COMPLIANCE | 215-341-6934 | robert.edling@exeloncorp.com | ON SEPTEMBER 23, 2023, AT APPROXIMATELY 10:25, PECO WAS NOTIFIED BY THE FIRE DEPARTMENT OF A FIRE IN THE ROADWAY ON PROVIDENCE RD IN YEADON, PENNSYLVANIA. UPON ARRIVAL, IT WAS DETERMINED THAT A TREE CAME DOWN DUE TO STORMS IN THE AREA WHICH CAUSED A PRIMARY ELECTRIC WIRE TO FALL INTO THE STREET. IT IS BELIEVED AT THIS TIME THE DOWNED ELECTRICAL WIRE ENERGIZED A FOREIGN FACILITY, WHICH CAUSED AN ELECTRICAL ARC BETWEEN THE FOREIGN FACILITY AND PECO GAS MAIN, WHICH BURNED HOLES IN THE BURIED 6" GAS MAIN AND IGNITED AT THE LOCATION OF THE DOWN WIRE. ALL 6 HOMES IN THAT IMMEDIATE AREA WERE EVACUATED. GAS FROM THE DAMAGED 6" MAIN THEN MIGRATED INTO 14 W. PROVIDENCE RD AND AT APPROXIMATELY 1315 THERE WAS AN IGNITION INSIDE THE HOME. PECO GAS CREWS THEN EXCAVATED DOWN AND INSTALLED A CLAMP OVER THE DAMAGED SECTION OF 6" MAIN AT APPROXIMATELY 1545. PECO INVESTIGATION IS CONTINUING.
2026-06-30 10:38 | NO | YES | NO | 20230062 | 38702 | 2023-10-26 12:39 | ORIGINAL FINAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY | CANONSBURG | PA | 15317 | 2023-09-27 02:16 | EASTERN | YES | 2023 | WASHINGTON PIKE AND VANADIUM ROAD | BRIDGEVILLE | ALLEGHENY | PA | 15017 | 40.3702 | -80.1008 | YES | YES | [7 empty] | 2023-09-27 02:29 | 1380223 | 1380525 | NATURAL GAS |  | 4970 | 48.5 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 69 | 2023-09-27 00:25 | NO |  |  | 2023-09-27 00:44 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | YES |  |  |  |  | YES | CASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1955 | UNKNOWN |  |  |  |  | 10 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.279 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 128591 | 133800.245547890292643 | 31608 | 32888.446013155791384 | 0 | 0 |  | 4.88 | 24254 | 21156.8165467625899280575539568345323741 | 237 | 206.735611510791366906474820143884892086 | 184690 | 85084.7370052297769418057553956834532374 | 188052.2437193194653219640287769784172662 | 2 | 0 | 17 | 0 | 0 | 67 | 2 | 171 | 175 | 200 | 192.619(A)(1) | 1982-06-03 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 33 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA TELEMETRY DID NOT TRIGGER ALERTS OR ALARMS AT THE TIME OF THE INCIDENT. GAS CONTROL WAS NOTIFIED BY COLUMBIA'S INTEGRATION CENTER AT THE TIME OF THE INCIDENT. THE INCIDENT WAS CLEARLY THE RESULT OF EXCAVATOR DAMAGE BY A THIRD-PARTY CONTRACTOR. NO INVESTIGATION WAS WARRANTED. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2023553872 |  |  | FACILITY OWNER | YES | YES | 45 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | RICHARD BURKE | OPERATIONS COMPLIANCE MANAGER | rburke@nisource.com | 7243217155 |  | RICHARD BURKE | rburke@nisource.com | 7243217155 | BRIAN MCCAUL | VICE PRESIDENT GAS OPERATIONS | 4129926929 | bmccaul@nisource.com | AT 00:15 ON SEPTEMBER 27, 2023, COLOSIMO CONSTRUCTION, A THIRD-PARTY SUBCONTRACTOR WORKING FOR PENNSYLVANIA AMERICAN WATER INSTALLING A WATER MAIN STRUCK AND DAMAGED A 10 INCH HIGH PRESSURE STEEL MAIN WITH A HYDRAULIC HAMMER CAUSING A GAS LOSS OF 4.9 MILLION CUBIC FEET OF GAS. COLUMBIA'S FACILITY LOCATORS CORRECTLY MARKED THE SECTION OF MAINLINE THAT WAS DAMAGED. BECAUSE OF THIS DAMAGE, APPROXIMATELY 69 BUILDINGS WERE EVACUATED, AND COLUMBIA HAD TO SHUT OFF SERVICE TO 19 CUSTOMERS FOR 45 HOURS WHILE REPAIRS WERE MADE.
2026-06-30 10:38 | NO | NO | NO | 20230063 | 38704 | 2023-10-26 14:46 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2023-09-26 23:04 | PACIFIC | YES | 2023 | 9208 ATLANTIC AVE | SOUTH GATE | LOS ANGELES | CA | 90280 | 33.948 | -118.1804 | [6 empty] | YES |  |  | 2023-09-27 05:55 | 1380225 | 1380442 | NATURAL GAS |  | 6700 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-09-26 17:00 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-09-26 16:58 | 2023-09-26 17:17 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 46 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1980 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 6 | 6 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 15000 | 15607.652815658595 | 0 | 0 | 0 | 0 |  | 6 | 40200 | 35066.5467625899280575539568345323741007 | 6 | 5.23381294964028776978417266187050359712 | 55206 | 34901.2534842974340647482014388489208633 | 50679.4333911981633453237410071942446043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 60 | 192.619(A)(1) | 1980-06-01 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | GRADER/SCRAPER | BUILDING CONSTRUCTION | NO | [5 empty] | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [143 empty] | YES | [26 empty] | FRANK SANTA CRUZ |  | fsantacruz@socalgas.com | 2134070168 |  |  |  |  | FRANK SANTA CRUZ |  | 2134070168 | fsantacruz@socalgas.com | ON 9/26/2023 SOCALGAS RESPONDED TO AN EXCAVATION INCIDENT. A THIRD-PARTY CONTRACTOR STRUCK A 6IN STEEL GAS MAIN WITH GRADING EQUIPMENT WHICH CAUSED THE RELEASE OF NATURAL GAS. SOCALGAS CREWS CONTROLLED THE FLOW OF GAS AND ABANDONED THE MAIN AS PART OF THE PERMANENT REPAIRS. UPON INVESTIGATION OF THE INCIDENT, IT WAS DISCOVERED THAT THE THIRD-PARTY CONTRACTOR WAS PERFORMING EXCAVATION ACTIVITIES WITHOUT A VALID USA TICKET. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE CPUC ONCE SOCALGAS WAS MADE AWARE OF MEDIA COVERAGE AND THEN REPORTED TO DOT ONCE GAS RELEASE REACHED 3MM.
2026-06-30 10:38 | NO | YES | YES | 20230064 | 40343 | 2023-11-06 17:38 | SUPPLEMENTAL FINAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2023-10-05 15:00 | CENTRAL | YES | 2023 | 310 SE OLD CANNON BALL RD | HOLT | CLINTON COUNTY | MO | 64048 | 39.4575 | -94.3359 | [6 empty] | YES |  |  | 2023-10-05 18:29 | 1380998 | 1381071 | NATURAL GAS |  | 56 | 0 | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2023-10-05 15:09 | YES | OPERATOR | 2023-10-05 15:15 | 2023-10-05 15:15 | 2023-10-05 15:09 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 63 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | COLD ROLLED SEAM | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | GAS BLEEDING BY STOPPLE | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 261 | 271.573158992459553 | 500 | 520.2550938552865 | 0 | 0 |  | 10.96 | 614 | 535.593525179856115107913669064748201439 | 0 | 0 | 1375 | 757.73455626642603258273381294964028777 | 1327.421778027602168107913669064748201439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 125 | 150 | 192.619(A)(3) | 1962-04-09 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | INCORRECT OPERATION | INCORRECT EQUIPMENT | [222 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED |  |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ERIN MILKERT | MANAGER DISTRIBUTION INTEGRITY | erin.milkert@spireenergy.com | 314-349-2932 |  | ERIN MILKERT | erin.milkert@spireenergy.com | 314-349-2932 | CRAIG HOEFERLIN | VP OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A COMPANY CONTRACTOR CREW WAS A PERFORMING A 12-INCH STEEL MAIN RELOCATION AND RETIRING A SECTION OF MAIN BETWEEN 2 STOPPLE FITTINGS. THE STOPPLES WERE IN POSITION TO SHUT OFF THE FLOW OF GAS AND THE PIPE HAD BEEN CUT BETWEEN THE STOPPLES AND BLOWN DOWN. THE CONTRACTOR EMPLOYEE WAS PREPARING TO CAP DOWNSTREAM OF ONE STOPPLE. TWO VENT STACKS (V1 & V2) WERE INSTALLED DOWNSTREAM OF THE STOPPLE WITH A VALVE AND AIR HANDLER ON THE VENT NEAREST THE STOPPLE FITTING (V1). THE CONTRACTOR EMPLOYEE INSERTED A GRIPPER PLUG IN THE 12-INCH MAIN UP TO THE V1 VENT STACK LOCATION. GAS WAS BLEEDING PAST THE STOPPLE FITTING. THE VALVE ON V1 VENT STACK WAS CLOSED. THIS RESULTED IN A PRESSURE BUILD-UP BETWEEN THE STOPPLE FITTING AND THE GRIPPER PLUG AND CAUSED THE GRIPPER PLUG TO BE EJECTED FROM THE OPEN-CUT END OF THE 12-INCH STEEL MAIN. THE GRIPPER PLUG CAUSED A HAND INJURY WITH THE CONTRACTOR EMPLOYEE AND HE WAS ADMITTED TO THE HOSPITAL FOR TREATMENT. A 48-HOUR UPDATE TO THE NRC WAS MADE ON OCTOBER 5, 2023 AT 18:49 - REPORT NUMBER 1380998. SUPPLEMENTAL REPORT CREATED: PART E.1, ESTIMATED PRESSURE AT TIME OF INCIDENT UPDATED FROM 56.0 PSIG TO 125PSIG. SUPPLEMENTAL REPORT CREATED 12/12/2024: PART G, UPDATING TO MOST APPLICABLE SUB-CAUSE OF "WRONG EQUIPMENT SPECIFIED OR INSTALLED"
2026-06-30 10:38 | NO | YES | NO | 20230065 | 39249 | 2023-11-09 18:13 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2023-10-09 14:36 | CENTRAL | YES | 2023 | 321 LINCOLN AVE. | WOODSTOCK | MCHENRY | IL | 60098 | 42.3167 | -88.4507 | [5 empty] | YES |  |  |  | 2023-10-09 15:10 | 1381297 | 1381456 | NATURAL GAS |  | 238 | 0.152 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-10-09 14:36 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 52 | 2023-10-09 13:09 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-10-09 14:53 | 2023-10-09 13:09 | 2023-10-09 14:36 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2018 | 2018 |  |  |  |  | 2 | ASTM D2513 | DURA-LINE POLYPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | MECHANICAL PUNCTURE | 1.5 | 7 | [7 empty] | CLASS 3 LOCATION | 1700000 | 1768867.3191079741 | 20000 | 20810.20375421146 | 5000 | 5202.550938552865 | 0 | 0 |  | 4.36 | 1038 | 905.449640287769784172661870503597122302 | 1 | 0.8723021582733812949640287769784172661871 | 1726039 | 729566.5517733416080935251798561151079136 | 1795786.39574318446816546762589928057554 | 8 | 0 | 44 | 2 | 0 | 44 | 8 | 22.2 | 23 | 25 | 192.619(A)(2) | 2018-10-09 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 11 | 1 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | SEWER LATERAL CLEANING | [153 empty] | YES | LETICIA QUEZADA | DIR COMPLIANCE AND PIPELINE RISK MANAGEMENT | lquezad@southernco.com |  |  | LETICIA QUEZADA | dir compliance and pipeline risk management |  | LETICIA QUEZADA | DIR COMPLIANCE AND PIPELINE RISK MANAGEMENT | 6305142036 | lquezad@southernco.com | THE CITY OF WOODSTOCK HIRED A SEWER CONTRACTOR TO PERFORM SEWER CLEANOUT WORK. AT APPROXIMATELY 12:35PM CST, A REPRESENTATIVE FROM THE CITY OF WOODSTOCK CALLED A COMPANY SUPERVISOR DIRECTLY AND INFORMED HIM THE MAIN WAS HIT IN THE SEWER BY THEIR CONTRACTOR. AT APPROXIMATELY 12:50 PM CST, COMPANY CUSTOMER SERVICE REPRESENTATIVE RECEIVES PHONE CALL FROM THE SEWER CONTRACTOR REPORTING THE DAMAGE. INITIAL INVESTIGATIONS INDICATE THAT WHILE PERFORMING CONTRACTED DUTIES, THE CONTRACTOR DAMAGED A NATURAL GAS MAIN AT THE INTERSECTION OF TRYON ST. AND LINCOLN AVE. WHILE COMPANY CREWS WERE IN THE PROCESS OF SHUTTING OFF THE FLOW OF GAS, AN EXPLOSION OCCURRED AT 321 LINCOLN AVE. IT IS BELIEVED THAT THE GAS FROM THE DAMAGED MAIN TRAVELED THROUGH THE SEWER AND INTO THE PREMISE, CAUSING A SUBSEQUENT HOUSE EXPLOSION. NO ONE WAS INSIDE THE PREMISE AT THE TIME OF THE EXPLOSION. THERE WERE NO FATALITIES AND THE ONLY REPORTED INJURIES WERE TO TWO FIREFIGHTERS THAT WERE TAKEN TO THE HOSPITAL FOR OBSERVATION AND WERE RELEASED. GAS MAIN WAS PREVIOUSLY INSTALLED THROUGH THE SANITARY SEWER BY A SECOND PARTY CONTRACTOR IN 2018. NOTE: IN PART F, THE INDIVIDUAL THAT FAILED DRUG SCREEN WAS A MANAGEMENT EMPLOYEE AND WAS NOT PART OF THE CREWS PERFORMING EMERGENCY RESPONSE AND REPAIR ACTIVITIES.
2026-06-30 10:38 | NO | NO | NO | 20230066 | 38816 | 2023-11-10 17:23 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2023-10-13 11:44 | PACIFIC | YES | 2023 | 4200 VALLEY BLVD | WALNUT | LOS ANGELES | CA | 91789 | 34.035 | -117.825 |  | YES |  | YES | [5 empty] | 2023-10-13 20:57 | 1381706 | 48hr update NRC#1381791 | NATURAL GAS |  | 3664 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-10-13 11:44 | NO |  |  | 2023-10-13 11:58 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 15 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1959 | UNKNOWN |  |  |  |  | 8 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.322 | [6 empty] | OTHER | [8 empty] | THIRD PARTY DIG IN DAMAGE | CLASS 3 LOCATION | 0 | 0 | 15000 | 15607.652815658595 | 20000 | 20810.20375421146 | 0 | 0 |  | 6 | 21984 | 19176.6906474820143884892086330935251799 | 0 | 0 | 56984 | 30405.9523746316626978417266187050359712 | 55594.5472173520693884892086330935251799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 47 | 52 | 192.621 M | 2013-01-07 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | YES | B230670145 | N/A |  | FACILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [143 empty] | YES | [26 empty] | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | jjcervantes@socalgas.com | 310-970-4854 | 909-335-7895 | JAMES CERVANTES | jjcervantes@socalgas.com | 310-970-4854 | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 310-970-4854 | jjcervantes@socalgas.com | ON 10-13-2023, A THIRD-PARTY CONTRACTOR DAMAGED AN 8-INCH STEEL GAS MAIN AT 4200 VALLEY BLVD, WALNUT, CA WHILE GRADING. SOCALGAS CREW RESPONDED AND CONTROLLED THE RELEASE OF GAS. THERE WERE NO INJURIES OR FURTHER DAMAGE RESULTING FROM THIS INCIDENT. INVESTIGATION OF THE INCIDENT SHOWED THERE WAS A VALID USA TICKET. HOWEVER, THE CONTRACTOR'S EXCAVATION PRACTICES WERE INADEQUATE AS IT FAILED TO POT-HOLE THE 8-INCH MAIN. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO GAS RELEASE EXCEEDING 3,000,000 CUBIC FEET. NOTE: ON 11-16-2023 A CHANGE WAS MADE TO PART A 4 TO REFLECT THE REQUEST FROM PHMSA TO CHANGE THE TIME FROM TIME INCIDENT BECAME REPORTABLE TO THE TIME THE COMPANY WAS NOTIFIED. PER PHMSA NOTE "EARLIEST TIME WOULD BE THE TIME THE 3RD PARTY NOTICED THE LEAK. A4 IS NOT TO BE CONFUSED WITH THE TIME OF CONFIRMED DISCOVERY."
2026-06-30 10:38 | NO | YES | NO | 20230067 | 39889 | 2023-11-15 16:31 | SUPPLEMENTAL FINAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY | CANONSBURG | PA | 15317 | 2023-10-15 14:55 | EASTERN | YES | 2023 | TEVEBAUGH ROAD | FREEDOM | BEAVER | PA | 15042 | 40.666 | -80.2159 |  |  |  | YES | [5 empty] | 2023-10-15 16:56 | 1381816 | 1381956 | NATURAL GAS |  | 0 | 48 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-10-15 14:55 | NO |  |  | 2023-10-15 15:00 | 2023-10-15 15:00 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1985 | UNKNOWN | [7 empty] | OTHER | NO ISSUE WITH MATERIAL FOR THIS EVENT | [9 empty] | OTHER | [8 empty] | THERE WAS NO RELEASE OF GAS. THIS INCIDENT WAS REPORTED AS A SIGNIFICANT EVENT BECAUSE GAS SERVICE WAS SHUT OFF FOR SAFETY TO 3,728 CUSTOMERS. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 2209692 | 2299207.037702551473516 | 89181 | 92793.739050216610713 | LODGING, MEALS, ETC. FOR RESPONDING EMPLOYEES. | 4.88 | 0 | 0 | 234 | 204.118705035971223021582733812949640288 | 2299107 | 971461.2908226925777273165467625899280576 | 2392204.89545780405545202158273381294964 | 37 | 0 | 3691 | 0 | 0 | 3691 | 37 | 15 | 15 | 18 | 192.619(A)(4) | 1999-06-07 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | OTHER | CUSTOMER NO GAS CALLS |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | SLUG OF AIR ENTERED COLUMBIA'S SYSTEM FROM THE MERIDIAN WELL PURCHASE POINT. | [47 empty] | MATTHEW MICELI | OPERATIONS COMPLIANCE MANAGER | mmiceli@nisource.com | 7248122844 |  | MATTHEW MICELI | mmiceli@nisource.com | 7248122844 | BRIAN MCCAUL | VICE PRESIDENT GAS OPERATIONS | 4129926929 | bmccaul@nisource.com | ON OCTOBER 15, 2023, COLUMBIA BEGAN RECEIVING "NO GAS" CALLS FROM CUSTOMERS IN ECONOMY, PA. SERVICE TECHNICIANS REPORTED NORMAL PRESSURE BUT ALSO REPORTED EVIDENCE OF AIR IN THE SYSTEM. THIS CONTINUED THROUGHOUT THE MORNING. COLUMBIA'S SYSTEMS WERE SUPPLIED BY A LOCAL PRODUCER IN CLOSE PROXIMITY TO THE MEDIUM PRESSURE SYSTEMS. IT WAS CONCLUDED THAT A SLUG OF AIR ENTERED COLUMBIA'S SYSTEM FROM THE MERIDIAN WELL PURCHASE POINT, AND THEREFORE, FOR SAFETY REASONS, GAS WAS TURNED OFF TO THE TWO MEDIUM PRESSURE SYSTEMS SO THE AIR COULD BE PURGED FROM THE SYSTEMS. THIS AFFECTED 3,728 CUSTOMERS. THERE WERE TWO MEDIUM PRESSURE SYSTEMS AFFECTED. PART E (ADDITIONAL OPERATING INFORMATION) DOES NOT ALLOW THE INCLUSION OF TWO SYSTEMS. BELOW IS THE REQUIRED INFORMATION FOR THE SECOND SYSTEM: E1. ESTIMATED PRESSURE AT THE POINT AND TIME OF THE INCIDENT (PSIG) 21 E2. NORMAL OPERATING PRESSURE AT THE POINT AND TIME OF THE INCIDENT (PSIG) 21 E3. MAXIMUM ALLOWABLE OPERATING PRESSURE (MAOP) AT THE POINT AND TIME OF THE INCIDENT (PSIG) 40 E3A. MAOP ESTABLISHED BY 49 CFR SECTION: 192.619 (A)(4) E3B. DATE MAOP ESTABLISHED: 03/20/09. E4. DESCRIBE THE PRESSURE ON THE SYSTEM RELATING TO THE INCIDENT: PRESSURE DID NOT EXCEED MAOP. E5. TYPE OF ODORIZATION SYSTEM FOR GAS AT POINT OF FAILURE: NONE. E6. ODORANT LEVEL NEAR THE POINT OF FAILURE MEASURED AFTER FAILURE: NOT MEASURED E7. WAS SUPERVISORY CONTROL DATA ACQUISITION (SCADA)-BASED SYSTEM IN PLACE ON THE PIPELINE OR FACILITY INVOLVED IN THE INCIDENT? NO. E8. WAS AN INVESTIGATION INITIATED INTO WHETHER OR NOT THE CONTROLLER(S) OR CONTROL ROOM ISSUES WERE THE CAUSE OF OR A CONTRIBUTING FACTOR TO THE INCIDENT? NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT.
2026-06-30 10:38 | NO | YES | NO | 20230068 | 38814 | 2023-11-16 15:35 | ORIGINAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2023-10-17 12:45 | EASTERN | YES | 2023 | 565 E MILWAUKEE AVE | DETROIT | WAYNE | MI | 48202 | 42.3719 | -83.0656 | [6 empty] | YES |  |  | 2023-10-19 08:15 | 1382137 | 1382278 | NATURAL GAS |  | 4872 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-10-17 12:45 | NO |  |  | 2023-10-17 12:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1900 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | MECHANICAL PUNCTURE | 4 | 12 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 53500 | 55667.2950425156555 | 67600 | 70338.4886892347348 | 0 | 0 |  | 3.1 | 15103 | 13174.3794964028776978417266187050359712 | 0 | 0 | 136203 | 61895.5164392471356683453237410071942446 | 139180.1632281532679978417266187050359712 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 7.5 | 10 | 10 | 192.619(A)(3) | 1/1/1899 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | OTHER | NOTIFICATION FROM 2ND PARTY CONTRACTOR |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | NATURAL GAS | YES | 2023080805604 |  |  | FACILITY OWNER | YES | YES | 34 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | UNMAPPED 6" STUB EXTENDING 4' SOUTH OFF OF 12" CAST IRON MAIN INSTALLED IN 1899 | [169 empty] | JUSTIN MORRIS |  | justin.morris@dteenergy.com | [5 empty] | MARINA DARLING |  | 5868724760 | marina.darling@dteenergy.com | 2ND PARTY CONTRACTOR IMPACTED AN OBJECT WHILE BORING FOR NEW GAS MAIN AT 12:45 ON 10/17/23. THIS OBJECT IN-TURN IMPACTED A REDUCING FITTING ON A 12" 10 PSI CAST-IRON MAIN THAT WAS ADJACENT TO THE BORE PATH, CAUSING A CRACK AND A LEAK. THE REDUCING FITTING WAS ON AN UNMAPPED STUB FROM ACTIVITY DONE IN YEAR 1950. GAS WAS SHUT OFF AT 02:28 ON 10/18/23. REPAIR ACTIVITIES WERE INITIALLY NOT EXPECTED TO EXCEED $10K TOTAL COST, NOR ANY OTHER REPORTING THRESHOLD, SO MICHIGAN PUBLIC SERVICE COMMISSION WAS NOT INITIALLY NOTIFIED. OPERATIONS UPDATED AT 07:33 THE FOLLOWING MORNING THAT A DECISION HAD BEEN MADE TO REPLACE 25' OF THE MAIN RATHER THAN PERFORM THE INITIALLY INTENDED REPAIR, IN ORDER TO AVOID CUSTOMER OUTAGES. THIS CHANGE CAUSED THE REPAIR COST TO EXCEED THE $10K THRESHOLD AND THE MPSC INCIDENT REPORTING LINE WAS NOTIFIED AT 08:19 ON 10/18/23. AFTER REPAIR, GAS LOSS WAS CALCULATED AND ESTIMATED AT 4872MCF, WHICH CAUSED THIS INCIDENT TO BE PHMSA REPORTABLE. ALSO NOTIFIED CHEMICAL SAFETY BOARD (CSB).
2026-06-30 10:38 | NO | NO | NO | 20230069 | 38836 | 2023-11-20 13:40 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2023-10-12 17:15 | EASTERN | YES | 2023 | 11301 MAPLEVIEW DRIVE | SILVER SPRING | MONTGOMERY COUNTY | MD | 20902 | 39.0427 | -77.0688 | YES |  |  |  |  | YES | YES |  |  | 2023-11-03 13:40 | 1383374 | 1383517 | NATURAL GAS |  | 5950 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-10-12 17:15 | NO |  |  | 2023-10-12 17:46 |  | NO | PUBLIC PROPERTY | UNDERGROUND | OTHER | IN A WATER FLOODED EXCAVATION | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1978 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN FREQUENCY OR SEAMLESS | UNKNOWN | [6 empty] | OTHER | [8 empty] | WATER MAIN LINE AT A 100-PSI BURST CREATING A HOLE AT THE BOTTOM OF THE 4-INCH GAS MAIN. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 10947 | 11390.465024867642631 | 383 | 398.515401893149459 | ADMINISTRATIVE COSTS | 1.26 | 7497 | 6539.649280575539568345323741007194244604 | 0 | 0 | 18827 | 10113.1356354031174990647482014388489209 | 18328.6297073363316583453237410071942446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 25 | 192.619(A)(2) | 1978-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE 4-INCH STEEL NATURAL GAS LINE WAS A TWO-WAY FEED SYSTEM AND PRESSURE DID NOT DROP BELOW ALARM SET POINT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | WATER ESCAPING FROM A BURST WATER MAIN. | [154 empty] | ARTHUR M GROFF | SUPERVISOR DOT PIPELINE SAFETY | agroff@washgas.com | 5713187993 |  | ART GROFF | agroff@washgas.com | 5713187993 | SHANNON MALONEY | MANAGER DOT PIPELINE SAFETY | 7037505558 | smaloney@washgas.com | ON OCTOBER 12, 2023, AT APPROXIMATELY 17:15 HOURS WASHINGTON GAS WAS NOTIFIED OF A POSSIBLE LEAK AT 11301 MAPLEVIEW DR SILVER SPRING MD. WASHINGTON GAS DISPATCHED CREWS TO THE LOCATION WHO ARRIVED AND PERFORMED AN ASSESSMENT OF SITUATION, WHICH RESULTED IN THE IDENTIFICATION OF A LEAKING 4-INCH STEEL MAIN LINE. WASHINGTON SURBURBAN SANITARY COMMISSION WAS WORKING ON A LEAKING WATER MAIN IN THE AREA THAT EVENTUALLY CAUSED THE GAS MAIN LEAK. THE CAUSE OF THE LEAK ON THE 4-INCH GAS MAIN LINE WAS A LEAK THAT ORIGINATED ON A 30-INCH WATER MAIN LINE AT A 100 PSI WHICH CREATED AN APPROXIMATELY 3-INCH DIAMETER HOLE AT THE BOTTOM OF THE 4-INCH GAS MAIN. THE GAS MAIN WAS SUBMERGED IN THE EXCAVATION DUE TO THE WATER LEAK. ON OCTOBER 14 AT APPROXIMATELY 1220 HOURS THE GAS WAS TURNED OFF UTILIZING VALVES, STOPPLE FITTING AND SQUEEZE OFF METHOD.
2026-06-30 10:38 | NO | YES | YES | 20230070 | 38870 | 2023-11-30 09:15 | ORIGINAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2023-10-16 11:18 | CENTRAL | YES | 2023 | 800 WEST MAIN STREET | ANOKA | ANOKA | MN | 55303 | 45.2085 | -93.4079 | [5 empty] | YES |  |  |  | 2023-10-31 15:12 | 1383136 | 1383193 | NATURAL GAS |  | 576 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | NO | [5 empty] | 8 | 2023-10-16 11:18 |  |  |  | 2023-10-16 11:33 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2021 | 2021 |  |  |  |  | 6 | PE2708,SDR11.5 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2708 | MECHANICAL PUNCTURE | 4 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 969 | 1008.254371891545237 | 2350 | 2445.19894111984655 | 0 | 0 |  | 4.2717 | 2460 | 2145.86330935251798561151079136690647482 | 0 | 0 | 5779 | 3149.969988584778191302158273381294964029 | 5599.31662236390977261151079136690647482 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 50 | 66 | 192.619(A)(2) | 2021-11-05 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 232842550 |  |  | CONTRACT LOCATOR | YES | YES | 2 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | dean.headlee@centerpointenergy.com | 612.321.5366 | 612.321.0000 | DEAN HEADLEE | dean.headlee@centerpointenergy.com | 612.321.5366 | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 612.321.5366 | dean.headlee@centerpointenergy.com | SHAFER CONTRACTING CO., INC. DAMAGED AN UNMARKED 6" PLASTIC CLASS 6 (50-55PSIG) GAS MAIN WITH A BACKHOE DURING ROAD RECONSTRUCTION WHILE WORKING UNDER GSOC TICKET #232891215. THE EXCAVATOR WAS WORKING ON A ROAD PROJECT FOR MNDOT WITH A PROJECT START OF EXCAVATION ON 04/03/23. DURING THIS TIME THERE WERE MULTIPLE UPDATE TICKETS AND FIELD MEETS WITH THE LINE LOCATOR(S) AND THE EXCAVATOR(S). ON THE MORNING OF THE DAMAGE DURING A SITE MEET WITH THE EXCAVATOR AND THE LINE LOCATOR, THE LINE LOCATOR WAS ALLEGED TO HAVE CLEARED THE WORK AREA IN THE STREET WHERE THE MAIN WAS CONTACTED, TELLING THE EXCAVATOR THAT THE LIVE MAIN WAS BEHIND THE CURB (SOUTH OF THE CURB) WHERE YELLOW HARD MARKS DENOTED THE PRESENCE OF GAS FACILITIES. AS A RESULT, THE LOCATOR FAILED TO MARK THE LIVE GAS MAIN, AND IT WAS SUBSEQUENTLY DAMAGED WITH MECHANIZED EQUIPMENT. THE CONTRACT LOCATE VENDOR WAS UNABLE TO PROVIDE SUFFICIENT DOCUMENTATION OF THE SITE MEETING THAT WOULD COUNTER THE ALLEGATIONS OF THE EXCAVATOR. NOTE, AT THE TIME OF THE DAMAGE THERE WAS NO EVIDENCE OF MINIMUM REPORTABLE CRITERIA FOR A MNOPS OR FEDOPS REPORT. IT WASN'T UNTIL A FIELD MEETING WITH MNDOT (JULIE) ON 10/24/23 THAT CENTERPOINT ENERGY'S DAMAGE PREVENTION COORDINATORS WERE MADE AWARE OF THE INJURY THAT OCCURRED ON THE DAY OF THE DAMAGE.
2026-06-30 10:38 | NO | YES | YES | 20230071 | 40903 | 2023-12-01 13:54 | SUPPLEMENTAL FINAL | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | NY | 12601 | 2023-11-02 12:12 | EASTERN | NO | 2023 | 7 BRICK ROW | WAPPINGERS FALLS | DUTCHESS | NY | 12590 | 41.6014 | -73.918 |  | YES | [7 empty] | 2023-11-02 12:54 | 1383286 | 1383403, 1383446 | NATURAL GAS |  | 13.1 | 0 | NO | [5 empty] | 0 | YES | 0 | 5 | 0 | 0 | 4 | 9 | YES | 2023-11-02 12:15 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 13.1 | YES | 25 | 2023-11-02 12:15 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-11-02 12:18 | 2023-11-02 12:15 | 2023-11-02 12:15 | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1952 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 1 | [7 empty] | CLASS 3 LOCATION | 1899000 | 1975928.846462378127 | 53220 | 55375.95218995669506 | 25867 | 26914.877025509391791 | 2250 | 2341.14792234878925 | CONTRACTOR CHARGES FOR LEAK SURVEY. | 3.7871 | 50 | 43.61510791366906474820143884892086330935 | 0 | 0 | 1980387 | 836746.1728742468815366402877697841726619 | 2060604.43870810667216574820143884892086 | 0 | 0 | 6 | 1 | 5 | 9 | 0 | 24 | 24 | 30 | 192.619(C) | 1952-05-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2.5 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | YES | 3 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [6 empty] | NO | NO | 18” – 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 0918300138801 | UDIG NY | Unknown | CONTRACT LOCATOR | YES | YES | 9 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | JERRY AMATO | MANAGER OF GAS COMPLIANCE | jamato@cenhud.com | 845-416-3887 |  | JERRY AMATO | jamato@cenhud.com | 845-416-3887 | ERIC KISZKIEL | VICE PRESIDENT OF OPERATIONS AND SAFETY | 845-486-5472 | ekiszkiel@cenhud.com | A CONTRACTOR WAS PERFORMING WORK FOR CENTRAL HUDSON THAT INCLUDED A MAIN AND SERVICE REPLACEMENTS ON BRICK ROW IN WAPPINGERS FALLS. THE SCOPE OF WORK CONSISTED OF REPLACING APPROXIMATELY 200 FT. OF 2-INCH STEEL MAIN AND 6 SERVICES. THE MAOP OF THE MAIN IS 30 PSIG. THE GAS SERVICES ON THE STREET WERE EITHER STEEL OR PLASTIC. ON THURSDAY, NOVEMBER 2, 2023, AT APPROXIMATELY 12:15 PM, CENTRAL HUDSON WAS NOTIFIED FROM A CENTRAL HUDSON EMPLOYEE AT 7 BRICK ROW, WAPPINGERS FALLS, OF A GAS LINE THAT WAS HIT WHERE THE COMPANY CONTRACTOR WAS EXCAVATING, WHICH RESULTED IN AN EXPLOSION AND STRUCTURE FIRE. MULTIPLE REPORTS OF A POSSIBLE GAS EXPLOSION WERE RECEIVED AFTER THIS CALL BY OUR DISPATCH CENTER. THE RESPONDING FIRE DEPARTMENTS PERFORMED EVACUATIONS AND THEN A SEARCH AND RESCUE EFFORT FOR THE PUBLIC AND WORKERS ON SITE WAS COMPLETED. A TOTAL OF 15 PEOPLE WERE TREATED FOR MEDICAL EVALUATION BY EMERGENCY MEDICAL SERVICES AND TRANSPORTED IF NECESSARY. IN PART A22 OF THIS REPORT, THE GENERAL PUBLIC EVACUATED IS ESTIMATED AT 25 PEOPLE AND CANNOT BE CONFIRMED DUE TO THE FIRE DEPARTMENT RESPONSE AND CENTRAL HUDSON CREWS ARRIVING AFTER THE RESIDENTS HAVE BEEN EVACUATED ALREADY. A CENTRAL HUDSON GAS FOREMAN WAS ON SITE AT THE TIME OF DAMAGE AND DURING THE IGNITION. THE FIRST CENTRAL HUDSON RESPONDER ARRIVED ON SITE AT 12:19 PM AND THE BUILDING WAS ON FIRE. ADDITIONAL CENTRAL HUDSON PERSONNEL INCLUDING COMMERCIAL REPRESENTATIVES, GAS CONSTRUCTION CREWS, AND SUPERVISORS WERE CONTACTED AND ARRIVED TO THE SITE. AT 12:30, THE GAS CREW SHUT GAS OFF TO BRICK ROW BY CLOSING A DISTRIBUTION LINE VALVE. AT 12:43 PM, THE ELECTRICITY WAS SHUT OFF THAT SERVICES BRICK ROW AND THE ADJACENT AREA. THE NATURAL GAS MAIN AND SERVICES WERE RETIRED AND ABANDONED ON BRICK ROW FOLLOWING THIS INCIDENT. ONCE THE FIRE WAS CONTAINED, CENTRAL HUDSON AND CONTRACTOR CREWS PERFORMED LEAK SURVEYS OF THE IMMEDIATE AND SURROUNDING AREAS TO ENSURE THERE WERE NO ADDITIONAL RISKS. GAS ODORANT READINGS WERE TAKEN IN THE SURROUNDING AREAS TO VERIFY APPROPRIATE ODORIZATION OF GAS AND WAS CONFIRMED.
2026-06-30 10:38 | NO | YES | NO | 20230072 | 40634 | 2023-12-04 12:02 | SUPPLEMENTAL FINAL | 2652 | NSTAR GAS COMPANY | 157 CORDAVILLE ROAD | SOUTHBOROUGH | MA | 01772 | 2023-11-04 08:00 | EASTERN | YES | 2023 | 126 PRINCE ST | NEEDHAM | NORFOLK | MA | 02492 | 42.276 | -71.2219 |  |  | YES | [6 empty] | 2023-11-04 09:31 | 1383441 | 1383554 | NATURAL GAS |  | 72 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-11-04 07:51 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 72 | YES | 0 | 2023-11-04 07:48 | YES | OPERATOR | 2023-11-04 07:52 | 2023-11-04 08:16 | 2023-11-04 07:48 | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 19 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1963 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES | 1 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.133 | [6 empty] | OTHER | [8 empty] | EXCAVATION DAMAGE FROM CONTACT WITH SMALL EXCAVATOR | CLASS 3 LOCATION | 350900 | 365115.0248676400657 | 2771 | 2883.253730145997783 | 37907 | 39442.619685544690711 | 0 | 0 | 2A: BASED ON ASSESSED DWELLING VALUE. RESPONSIBILITY FOR REIMBURSEMENT TBD. | 7.68 | 553 | 482.383093525179856115107913669064748201 | 0 | 0 | 392131 | 165838.1860482094333010215827338129496403 | 407923.2813768559340501151079136690647482 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 55.9 | 55.9 | 60 | 192.619(A)(2) | 1963-06-10 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS AN EXCAVATOR DAMAGE BY 2ND PARTY CONTRACTOR. | [12 empty] | NO |  |  | YES | 3 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) |  |  |  |  | YES | YES | YES | YES |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [6 empty] | NO | NO | 18” – 36” |  | CONTRACTOR | UNKNOWN/OTHER | NATURAL GAS | YES | 2023431452 |  | Unknown | CONTRACT LOCATOR | NO | UNKNOWN/OTHER |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [142 empty] | YES | [27 empty] | KATHERINE SILVER | MANAGER COMPLIANCE | katherine.silver@eversource.com | 5088641836 |  | KATHERINE SILVER | katherine.silver@eversource.com | 5088641836 | KATHERINE SILVER | MANAGER COMPLIANCE | 5088641836 | katherine.silver@eversource.com | DURING A PLANNED SERVICE LINE REPLACEMENT, A SECOND PARTY CONTRACTOR STRUCK A SERVICE LINE CAUSING AN IGNITION AND HOUSE FIRE. THE RESIDENTS WERE NOT HOME AT THAT TIME. A CONTRACTOR EMPLOYEE SUSTAINED A MINOR INJURY. THE SERVICE LINE WAS CUT OFF AT THE MAIN WHEN THE SITUATION WAS DEEMED SAFE. THE BUILDING WAS DEMOLISHED THE DAY OF THE INCIDENT. G3.7: MINI EXCAVATOR WAS BEING UTILIZED. G3.12: ON NOVEMBER 4, THE ORIGINAL MARKS IN THE PUBLIC WAY SHOWING THE SERVICE LINE FROM THE SERVICE TEE TO THE PROPERTY LINE AT THE LEFT SIDE OF THE PROPERTY WERE VISIBLE AND ACCURATE. THERE WERE NO VISIBLE MARKINGS OR FLAGS ON THE PRIVATE PROPERTY. PRIVATE PROPERTY MARKINGS WERE EITHER NOT APPLIED OR NOT MAINTAINED. G3.14 THE CREW WAS MECHANICALLY EXCAVATING THE TRENCH FOR THE NEW SERVICE ON THE PRIVATE PROPERTY WHEN THEY STRUCK THE ACTIVE 1" STEEL SERVICE.
2026-06-30 10:38 | NO | YES | NO | 20230073 | 39481 | 2023-12-06 16:03 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2023-11-09 18:45 | EASTERN | NO | 2023 | NORTHSIDE DRIVE NW AT OLD POWERS FERRY ROAD | SANDY SPRINGS | FULTON | GA | 30339 | 33.9018 | -84.4275 | YES |  |  |  |  | YES |  |  |  | 2023-11-09 18:49 | 1383916 | 1384000 | NATURAL GAS |  | 17423 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-11-08 15:53 |  |  |  | 2023-11-08 16:13 | 2023-11-09 18:49 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 66 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1968 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 2 | 2.5 | [7 empty] | CLASS 3 LOCATION | 2734 | 2844.754853200706582 | 3480 | 3620.97545323279404 | 75278 | 78327.525910476514294 | 0 | 0 |  | 1.83 | 31884 | 27812.4820143884892086330935251798561151 | 0 | 0 | 113376 | 57082.5246489155602186187050359712230216 | 112605.7382312985041246330935251798561151 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 230 | 300 | 192.619(A)(4) | 1968-03-13 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 15.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | ELECTRIC | YES | 231102003911 |  | Unknown | CONTRACT LOCATOR | YES | YES | 24 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | RALPH MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | ON NOVEMBER 8, 2023, AT APPROXIMATELY 15:53 HOURS, A THIRD-PARTY PARTY EXCAVATOR (WASHINGTON COMMUNICATION) STRUCK AND DAMAGED AN ATLANTA GAS LIGHT COMPANY (AGLC) 6-INCH STEEL GAS MAIN WHILE DIRECTIONALLY BORING TO INSTALL ELECTRIC CONDUIT LINES AT THE INTERSECTION OF NORTHSIDE DRIVE AND OLD POWERS FERRY ROAD, SANDY SPRINGS, GA. UPON ARRIVAL, AGLC PERSONNEL SECURED THE AREA AND MONITORED THE SURROUNDING AREA FOR GAS MIGRATION. BASED ON A FIELD ASSESSMENT OF CONDITIONS SURROUNDING THE LOCATION OF THE INCIDENT AND TO NOT SHUT DOWN A LARGE METRO AREA SHOULD AN EXISTING VALVE NORTH OF THE DAMAGE BEEN USED IN CONJUNCTION WITH THE OTHER TWO VALVES OPERATED, A DECISION WAS MADE TO SQUEEZE THE PIPE AT A SAFE DISTANCE NORTH OF THE DAMAGE. UPON EXCAVATING TO EXPOSE THE EXISTING PIPE, IT WAS DISCOVERED THAT THE PIPE WAS APPROXIMATELY 66 INCHES DEEP AND UNDER APPROXIMATELY 36-INCHES OF ASPHALT, GAS WAS SHUT-OFF TO THE DAMAGED AREA ON NOVEMBER 8, 2023, AT 23:54 HOURS BY OPERATING TWO (2) VALVES AND PERFORMING ONE (1) SQUEEZE OFF OPERATION. A LOCATE REQUEST WAS MADE ON NOVEMBER 2, 2023, BY WASHINGTON COMMUNICATION (EXCAVATOR) TO LOCATE "W NORTHSIDE DR, OLD POWERS FERRY RD, LOCATE THE ENTIRE INTERSECTION FOR 50FT IN ALL DIRECTIONSBOTH SIDES OF THE RD AND WITHIN THE R/O/W ON BOTH SIDES OF THE ST, THIS IS A 3 LEG INT, IT DOES NOTINCLUDE LOCATING ALONG RIVERVIEW RD NW". AGLC FACILITIES WERE MARKED BY USIC LOCATING COMPANY TO SATISFY THIS REQUEST ON NOVEMBER 6, 2023, AT 11:26 HOURS. ON NOVEMBER 8, 2023, AT 13:00 HOURS, USIC REMARKED AGLC'S FACILITIES AS REQUESTED BY THE EXCAVATOR DUE TO FACILITY MARKINGS NO LONGER BEING VISIBLE. INVESTIGATION OF THE SITE REVEALED THAT THE LOCATE MARKS WERE ACCURATE AT THE POINT OF DAMAGE. HAD THE EXCAVATOR POTHOLED, IT WOULD HAVE DETERMINED THE LOCATION OF THE GAS MAIN. ONCE THE DAMAGED SECTION OF MAIN WAS EXPOSED AND ALL THE VARIABLES WERE OBTAINED TO PERFORM THE GAS LOSS CALCULATION, IT WAS IDENTIFIED THAT THE AMOUNT OF GAS RELEASED EXCEEDED THE THRESHOLD FOR REPORTING AND THE NATIONAL RESPONSE CENTER (NRC) WAS NOTIFIED AT THAT TIME ON NOVEMBER 9, 2023, AT 18:49 HOURS WHERE AN INITIAL NRC REPORT NUMBER 1383916 WAS CREATED. AN ADDITIONAL NRC REPORT NUMBER 1384000 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2026-06-30 10:38 | NO | YES | NO | 20230074 | 39866 | 2023-12-06 18:18 | SUPPLEMENTAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2023-11-08 18:00 | PACIFIC | NO | 2023 | 24701 US 195 | PULLMAN | WHITMAN | WA | 99163 | 46.7603 | -117.2655 | YES | [6 empty] | YES | WILLIAMS TURNED MAINLINE VALVES OFF, AVISTA TURNED OFF STATION VALVES AS APPLICABLE | 2023-11-08 18:10 | 1383817 | 1383977 | OTHER GAS | N/A - NO GAS RELEASED | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-11-08 12:42 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-11-08 12:54 | 2023-11-08 13:08 | 2023-11-08 12:54 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 41 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | GAS CUSTOMER OUTAGE | UNKNOWN | UNKNOWN | [7 empty] | STEEL |  | OTHER | INTERSTATE PIPELINE PIPE | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | OTHER | TOP OF THE INTERSTATE PIPELINE (WILLIAMS) PIPE WAS DAMAGED BY PLOW. NO RELEASE OF AVISTA GAS - REPORTABLE DUE TO LOSS OF SERVICE TO ~36,000 CUSTOMERS. | 12 | 12 |  | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 9750000 | 10144974.33017808675 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 9750000 | 4119464.94464944725 | 10144974.33017808675 | 3665 | 26 | 31588 | 0 | 0 | 0 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1971-06-15 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE GAS OUTAGE WAS BEYOND OPERATOR'S CONTROL | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | LOSS OF GAS SUPPLY FROM INTERSTATE TRANSMISSION PIPELINE (WILLIAMS) AS A RESULT OF PIPELINE RUPTURE AND ISOLATION. SEE WILLIAMS NRC CASE #1383793. | [20 empty] | YES | [26 empty] | JOSHUA FORT | SR. GAS ENGINEER | josh.fort@avistacorp.com | 509-495-2656 |  | RANDY BAREITHER | randy.bareither@avistacorp.com | 509-434-6783 | CARIE MOURIN | MANAGER - NATURAL GAS COMPLIANCE AND INTEGRITY | 509-495-2224 | carie.mourin@avistacorp.com | ON WEDNESDAY 11/8/23, AT 1242 PACIFIC TIME, AVISTA BECAME AWARE OF PRESSURE ISSUES IN OUR SE WASHINGTON SERVICE AREA (PULLMAN GATE STATION). AT 1254 THE AVISTA GAS CONTROL ROOM (GCR) RECEIVED NOTIFICATION FROM WHITMAN COUNTY (WA) EMERGENCY DISPATCH THAT AN EXCAVATOR HAD HIT A GAS LINE AND GAS WAS BLOWING NEAR US HIGHWAY 195 MILEPOST 27 AND THAT THE HIGHWAY HAD BEEN SHUT DOWN. AT THE SAME TIME, THE AVISTA GCR RECEIVED NOTIFICATION FROM WILLIAMS PIPELINE GCR THAT THEY WERE EXPERIENCING GAS PRESSURE ISSUES WITH THEIR LEWISTON LATERAL GAS LINE AND HAD A TECH IN ROUTE TO INVESTIGATE. AVISTA PROVIDED WILLIAMS SOME OF THE DETAIL WE HAD JUST LEARNED FROM WHITMAN COUNTY DISPATCH. WITHIN A SHORT TIME, IT BECAME KNOWN THAT A FARMER HAD HIT WILLIAMS PIPELINE'S 12" TRANSMISSION LINE AND AVISTA WOULD LIKELY LOSE ALL GAS CUSTOMERS IN THE REGION. AVISTA MANAGEMENT PROCEEDED TO "STAND UP" ITS EMERGENCY OPERATING PLAN (EOP) TO RESPOND TO THE INCIDENT. (WILLIAMS NRC CASE #1383793) WITHIN A MATTER OF HOURS, AVISTA HAD LOST GAS SERVICE TO ROUGHLY 36,000 CUSTOMERS IN THE WASHINGTON TOWNS/CITIES OF PULLMAN, PALOUSE, ALBION, UNIONTOWN, COLTON, CLARKSTON AND ASOTIN AND THE IDAHO TOWNS/CITIES OF MOSCOW, TROY, DEARY, BOVILL, GENESEE, AND LEWISTON. AVISTA IMMEDIATELY CONTACTED THE AMERICAN GAS ASSOCIATION (AGA) TO SEEK THEIR ASSISTANCE IN MOBILIZING MUTUAL AID RESOURCES FROM OTHER GAS PROVIDERS IN THE REGION. AT APPROXIMATELY 1800, AVISTA CONTACTED THE NATIONAL RESPONSE CENTER AND REPORTED THE INCIDENT (AVISTA NRC CASE #1383817) DUE TO EXCESSIVE COSTS THAT WOULD BE EXPENDED TO RESOLVE THE OUTAGE. OVER THE NEXT TWO DAYS, A MASSIVE EFFORT WAS UNDERTAKEN TO TURN OFF ALL THE AFFECTED GAS CUSTOMERS, PRIMARILY WITH AVISTA PERSONNEL RESOURCES. ONCE WILLIAMS HAD COMPLETED THEIR REPAIRS AND REPRESSURIZED THEIR PIPELINE, AVISTA PROCEEDED TO REPRESSURE ITS HIGH- PRESSURE PIPELINE NETWORK. PURGE PLANS WERE ESTABLISHED AND RELIGHT AREAS WERE FORMALIZED BY GAS ENGINEERING AND GAS OPERATIONS PERSONNEL. THANKS TO GREAT ASSISTANCE FROM AGA, AVISTA'S MUTUAL AID REQUEST WAS ANSWERED BY EIGHT GAS COMPANIES AND MUNICIPALITIES FROM AS FAR AWAY AS SOUTH DAKOTA AND CALIFORNIA. ALTHOUGH SOME RELIGHTS HAD BEGUN AS EARLY AS FRIDAY 11/10/23, THE MAJOR RELIGHT EFFORTS BEGAN THE MORNING OF SATURDAY 11/11/23 WITH ASSISTANCE FROM MUTUAL AID PERSONNEL AND SOME LOCAL HVAC CONTRACTOR RESOURCES. RELIGHTS CONTINUED OVER THE COURSE OF THE NEXT FOUR DAYS. BY THE END OF THE DAY ON TUESDAY 11/14/23, THE FIRST WAVE OF VISITING ALL CUSTOMERS HAD BEEN COMPLETED AND OVER 95% OF CUSTOMERS WERE BACK IN SERVICE. CUSTOMERS WHO WERE NOT PRESENT DURING THE FIRST VISIT RECEIVED A DOORHANGER AND WERE INSTRUCTED HOW TO CONTACT AVISTA TO GET THEIR GAS SERVICE REESTABLISHED AT THEIR CONVENIENCE.
2026-06-30 10:38 | NO | YES | YES | 20230075 | 38940 | 2023-12-07 17:29 | SUPPLEMENTAL FINAL | 31159 | KANSAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2023-11-08 15:46 | CENTRAL | NO | 2023 | 7700 E 13TH, #69 | WICHITA | SEDGWICK | KS | 67206 | 37.7115 | -97.2472 | [5 empty] | YES |  |  |  | 2023-11-08 17:50 | 1383808 | 1383811, 1383997 | NATURAL GAS |  | 29.9 | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-11-08 15:46 | YES | OPERATOR | 2023-11-08 16:28 | 2023-11-08 16:07 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1998 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 2406 | OTHER | [8 empty] | AFTER INITIAL MECHANICAL PUNCTURE, THE LINE WAS CUT BY THIRD PARTY EXCAVATOR IN AN ATTEMPT TO INSERT A REPAIR FITTING. | CLASS 3 LOCATION | 0 | 0 | 500 | 520.2550938552865 | 1000 | 1040.510187710573 | 159 | 165.441119845981107 | GAS LOST | 5.31 | 159 | 138.696043165467625899280575539568345324 | 0 | 0 | 1818 | 813.901437521569588856115107913669064748 | 1864.902444577308232899280575539568345324 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 18 | 18 | 60 | 192.619(A)(2) | 1998-10-08 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.9 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | YES | OTHER | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | AUGER | FENCING | NO | [5 empty] | YES | 2 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | RANDY SPECTOR | DIRECTOR OF ENGINEERING | randy.spector@onegas.com | 9135303219 |  | RANDY SPECTOR | randy.spector@onegas.com | 9135303219 | RANDY SPECTOR | DIRECTOR OF ENGINEERING | 9135303219 | randy.spector@onegas.com | ON NOVEMBER 18, 2023, AN INDIVIDUAL STRUCK A SERVICE LINE WHILE REPAIRING A PRIVACY FENCE. A LOCAL HANDYMAN WAS REPAIRING A PRIVACY FENCE AT 7700 E. 13TH STREET, UNIT 69, IN WICHITA, KANSAS, WHICH INVOLVED EXCAVATING AROUND KANSAS GAS SERVICE FACILITIES. THE HANDYMAN DID NOT LIVE AT THE RESIDENCE AND HAD NOT REQUESTED KANSAS GAS SERVICE LOCATE ITS FACILITIES BEFORE STARTING THE REPAIR. WHILE EXCAVATING WITH A 6" AUGER, THE HANDYMAN STRUCK A KANSAS GAS SERVICE SERVICE LINE. BASED ON A REVIEW OF THE SITE, IT APPEARS THE HANDYMAN ATTEMPTED TO REPAIR THE DAMAGED SERVICE LINE. WHEN KANSAS GAS SERVICE TECHNICIAN ARRIVED ON-SITE AS A RESULT OF A THIRD-PARTY LEAK CALL, THEY FOUND THE HANDYMAN UNCONSCIOUS IN THE EXCAVATION AREA. KANSAS GAS SERVICE'S TECHNICIAN MOVED THE HANDYMAN AWAY FROM THE EXCAVATION AREA AND CALLED 911. EMERGENCY SERVICES ARRIVED AT THE SCENE AND TRANSPORTED THE HANDYMAN TO A LOCAL HOSPITAL. KANSAS GAS SERVICE WAS ADVISED THE HANDYMAN PASSED AWAY APPROXIMATELY FOUR DAYS LATER AT THE HOSPITAL.
2026-06-30 10:38 | NO | YES | YES | 20230076 | 39967 | 2023-12-12 15:07 | SUPPLEMENTAL FINAL | 2364 | DUKE ENERGY OHIO | 139 EAST FOURTH STREET PO BOX 960 - ROOM 460-ANNEX | CINCINNATI | OH | 45202 | 2023-11-13 14:46 | EASTERN | NO | 2023 | 3332 WALWORTH AVENUE | CINCINNATI | HAMILTON | OH | 45226 | 39.118 | -84.4417 | [5 empty] | YES |  |  |  | 2023-11-13 17:35 | 1384207 | 1384233 | NATURAL GAS |  | 10 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2023-11-13 14:46 | OTHER | FIRE EXTINGUISHED ITSELF AFTER THE INITIAL BURST OF FLAME. | 10 | NO | 0 | 2023-11-13 14:46 | NO |  |  | 2023-11-13 14:46 | 2023-11-13 14:46 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1975 | UNKNOWN |  |  |  |  | 3 | PE-2306 | DUPONT ALDYL-A | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2306 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 15000 | 15607.652815658595 | 0 | 0 | 0 | 0 |  | 5.79 | 58 | 50.59352517985611510791366906474820143885 | 0 | 0 | 15058 | 6378.84341235498802158273381294964028777 | 15658.2463408384511151079136690647482014 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 24.95 | 24.95 | 35 | 192.619(A)(2) | 1975-10-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.1 |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE WAS NOT A FACTOR | [12 empty] | YES | 3 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | CREW DID NOT FOLLOW ESTABLISHED PROCEDURES. |  |  | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | CREW WAS ON SITE INVESTIGATING A GRADE 2 LEAK. WHILE CONDUCTING THE LEAK ANALYSIS AND TRYING TO PINPOINT THE LEAK'S LOCATION, A DAMAGE OCCURRED BY PROBING THROUGH THE 3" PLASTIC MAIN CREATING A GRADE 1 LEAK. THE CREW BEGAN TO EXCAVATE TO MAKE REPAIRS ON THE GRADE 1 LEAK. AT THIS TIME, THE CREW DID NOT FOLLOW ESTABLISHED PROCEDURES WHILE ATTEMPTING TO MAKE AN UNAUTHORIZED REPAIR BY INSTALLING A MECHANICAL "TEE" ON AN UNCONTROLLED RELEASE OF GAS ON THE MAIN. THE GAS IGNITED CAUSING BURN INJURIES TO 2 EMPLOYEES. ONE OF THE EMPLOYEE'S INJURIES REQUIRED OVERNIGHT HOSPITALIZATION. THE GRADE 1 LEAK WAS REPAIRED THE SAME DAY. THE GRADE 2 LEAK WAS REPAIRED AT A LATER DATE.
2026-06-30 10:38 | NO | YES | YES | 20230077 | 39070 | 2023-12-15 14:09 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2023-11-17 08:30 | CENTRAL | YES | 2023 | 1801 KIPLING @ WOODHEAD | HOUSTON | HARRIS | TX | 77098 | 29.7405 | -95.4047 | [5 empty] | YES | YES |  |  | 2023-11-17 11:00 | 1384557 | 1384618 | NATURAL GAS |  | 1280.452 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2023-11-17 08:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1280 | NO | 4 | 2023-11-17 09:00 |  |  |  | 2023-11-17 09:00 | 2023-11-17 10:40 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 8 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2023 | UNKNOWN |  |  |  |  | 2 | ASTM D2513 | CENTRAL | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 12258 | 12754.573880956203834 | 761900 | 792764.7120166855687 | DAMAGE TO EQUIPMENT AND HOME | 6.452 | 8261 | 7206.088129496402877697841726618705035971 | 0 | 0 | 782419 | 332957.7725782474251975683453237410071942 | 812725.374027138175411697841726618705036 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 44 | 44 | 60 | 192.619(A)(1) | 2023-07-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED THE THRESHOLD | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | < 18” |  | CONTRACTOR | GRADER/SCRAPER | ROAD WORK | YES | 2381471224 | TEXAS 811 | Unknown | CONTRACT LOCATOR | YES | YES | 16 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | LESLIE J DAVENPORT | SR COMPLIANCE COORDINATOR | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 | SAM COOK | sam.cook@centerpointenergy.com | 713-967-8026 | JERRY GANN | REGIONAL OPERATIONS DIRECTOR | 713-967-7101 | jerry.gann@centerpointenergy.com | ON NOVEMBER 17, 2023, AT APPROXIMATELY 8:30AM, THE HOUSTON FIRE DEPARTMENT NOTIFIED CENTERPOINT ENERGY ABOUT A GAS LEAK AT THE 3600 BLOCK OF WOODHEAD AND KIPLING STREET IN HOUSTON TEXAS. ONCE CENTERPOINT ARRIVED ON SITE IT IDENTIFIED A GAS LINE HAD BEEN STRUCK BY MECHANIZED EQUIPMENT OPERATED BY MAIN LINE INDUSTRIES (MC2). THE DAMAGE OCCURRED ON A 2" POLYETHYLENE GAS LINE WHICH WAS AN OFFSET TO DECONFLICT THE 6" STEEL, WITH ANOTHER UTILITY PLACEMENT. WHILE THE CONTRACTOR WAS PREPARING THE SUB-BASE FOR THE PROPOSED ROADWAY, THE CONTRACTOR CAME IN CONTACT WITH CNP FACILITY WITH ROAD RECLAIMER (ASPHALT GRINDER). AFTER INITIAL REVIEW, IT WAS DETERMINED THAT MC2 HAD A VALID ONE CALL TICKET (NO. 2381471224) FOR THIS WORK, AND THE LOCATE VENDOR RESPONDED TO THE LOCATE REQUEST IN THE REQUIRED TIME. AFTER FURTHER REVIEW IT WAS DETERMINED THAT THIS 2" POLYETHYLENE LINE WAS NOT AVAILABLE IN CNP MAPPING SYSTEM.
2026-06-30 10:38 | NO | YES | YES | 20230078 | 39090 | 2023-12-19 08:09 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2023-11-19 20:00 | EASTERN | NO | 2023 | 3405 E 139TH STREET | CLEVELAND | CUYAHOGA | OH | 44120 | 41.4664 | -81.5857 |  |  | YES | [6 empty] | 2023-11-19 22:18 | 1384728 | 1384755 | NATURAL GAS |  | 27 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2023-11-19 20:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 27 | YES | 4 | 2023-11-19 20:00 |  |  |  | 2023-11-19 20:07 | 2023-12-19 21:50 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES |  |  |  | OTHER | METER AND METER MANIFOLDS | [9 empty] | OTHER | [8 empty] | OUT OF CONTROL VEHICLE STRUCK OUTSIDE WALL OF BUILDING DIRECTLY OPPOSITE INDOOR METER MANIFOLD, CAUSING UNKNOWN SCOPE OF DAMAGE TO METERING EQUIPMENT AND HOUSELINE THAT BEGAN TO LEAK. | CLASS 3 LOCATION | 119600 | 124445.0184501845308 | 2000 | 2081.020375421146 | 5000 | 5202.550938552865 | 0 | 0 |  | 3.445 | 93 | 81.1241007194244604316546762589928057554 | 0 | 0 | 126693 | 53555.7380405638686863309352517985611511 | 131809.7138648779662604316546762589928058 | 0 | 0 | 2 | 2 | 0 | 2 | 0 | 0.28 | 0.28 | 1 | 192.619(A)(4) | 1970-11-12 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.3 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 50 | YES |  |  |  |  | YES | YES | LOW PRESSURE METER MANIFOLD WAS LOCATED INSIDE OF STRUCTURE.. | [135 empty] | DANIEL EVANS | SUPERVISOR PIPELINE COMPLIANCE | daniel.a.evans@dominionenergy.com | 13305715796 |  | DANIEL EVANS | daniel.a.evans@dominionenergy.com | 13305715796 | DANIEL EVANS | SUPERVISOR PIPELINE COMPLIANCE | 13305715796 | daniel.a.evans@dominionenergy.com | IN THE MINUTES IMMEDIATELY PRECEDING APPROXIMATELY 20:00 ON SUNDAY, NOVEMBER 19TH, AN OUT-OF-CONTROL VEHICLE STRUCK THE FRONT WALL OF AN APARTMENT BUILDING AT ADDRESS 3401/3405 E 139TH STREET IN CLEVELAND, OH (THE APARTMENT BUILDING HAD TWO MAILING ADDRESSES). THE VEHICLE THEN ATTEMPTED TO FLEE THE SCENE AND STRUCK THE NEIGHBORING HOME (3421 E 139TH STREET). THE DRIVER/OCCUPANTS OF THE VEHICLE FLED THE SCENE. RESIDENTS OF THE BUILDINGS THAT HAD BEEN STRUCK BY THE VEHICLE CALLED 911, AND THE CLEVELAND FIRE DEPARTMENT AND CLEVELAND POLICE DEPARTMENT RESPONDED. WHEN THE FIRE DEPARTMENT ARRIVED AT THE SCENE, THEY WITNESSED AN EXPLOSION AT THE APARTMENT BUILDING AT 3401/3405 E 139TH STREET THAT COMPLETELY DESTROYED ONE QUARTER OF THE BUILDING. THE FIRE DEPARTMENT THEN CALLED DEO DISPATCH TO ASSIST WITH SHUTTING OFF THE GAS. DEO EMPLOYEES RESPONDED AND ARRIVED AT THE SCENE AT 20:07 AND SHUT THE GAS OFF AND PERFORMED A FIRE INVESTIGATION AND SHUT OFF GAS TO THE SECOND HOME (3421 E 139TH STREET) THAT HAD BEEN STRUCK BY THE VEHICLE AS A PRECAUTION. DEO PIPELINE SAFETY WAS NOTIFIED AT 21:50 AND THE INCIDENT WAS REPORTED TO PHMSA AND THE PUCO. DURING THE POLICE AND FIRE INVESTIGATION THE FOLLOWING MORNING (MONDAY, NOVEMBER 20TH) THE FIRE DEPARTMENT RECOVERED ONE FATALITY FROM THE DEBRIS WHO MATCHED THE DESCRIPTION OF A RESIDENT REPORTED MISSING BY FAMILY MEMBERS. TWO FD PERSONNEL WERE TREATED AT THE HOSPITAL DUE TO INJURIES SUSTAINED WHILE RESPONDING TO THE EMERGENCY, AND ONE RESIDENT WAS RECOVERED ALIVE FROM THE DEBRIS WHO REFUSED TREATMENT AT THE SCENE IN THE MINUTES IMMEDIATELY AFTER THE INITIAL EXPLOSION. DEO PERSONNEL PARTICIPATED IN THE RECOVERY OF METERING EQUIPMENT FROM THE STRUCTURE, TESTING OF SERVICE LINE, AND TESTING OF ODORIZATION. ALL TESTS SHOWED JURISDICTIONAL FACILITIES WERE IN COMPLIANCE. GAS SERVICE WAS RESTORED TO 3421 E 139TH STREET ON NOVEMBER 20TH AFTER INVESTIGATION SHOWED THAT THE VEHICLE IMPACT DID NOT COMPROMISE ANY GAS FACILITIES. DUE TO EXTENSIVE DAMAGE, NO DATA WAS ABLE TO BE RECOVERED FROM THE METERS AT 3401/3405 E 139TH STREET. BASED ON THE LOCATION OF THE INDOOR METER/MANIFOLD AND VEHICLE TRACKS AND OTHER EVIDENCE AT THE SCENE, IT IS APPARENT THAT THE VEHICLE COLLIDED DIRECTLY WITH THE EXTERIOR BUILDING WALL OPPOSITE THE INDOOR METER MANIFOLD. IT IS MORE THAN LIKELY THAT THE COLLISION CAUSED A RUPTURE AND LEAK IN SOME COMBINATION OF OPERATOR EQUIPMENT AND HOUSELINE PIPING LEADING TO A LEAK. DUE TO THE SUBSEQUENT EXPLOSION AND DAMAGE TO THE BUILDING, METERING EQUIPMENT, AND HOUSELINE, THE EXACT FAILURE LOCATIONS OF THE EQUIPMENT AND SOURCE OF IGNITION IS UNKNOWN. 1/18/2024: FINALIZING REPORT. NO NEW INFORMATION AVAILABLE. NO SUSPECT OR CHARGES ANNOUNCED FOR DRIVER OF VEHICLE THAT INITIATED EVENT.
2026-06-30 10:38 | NO | NO | NO | 20230079 | 39672 | 2023-12-19 15:40 | SUPPLEMENTAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2023-11-20 11:00 | EASTERN | NO | 2023 | 1410 COVENTRY MEADOWS DR. | SYKESVILLE | BALTIMORE | MD | 21784 | 39.332 | -76.492 | YES | [8 empty] | 2023-11-20 14:08 | 1384778 | 1384902 | NATURAL GAS |  | 0 | 19.67 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-11-20 11:00 | NO |  |  | 2023-11-20 11:00 | 2023-11-20 11:00 | NO | PUBLIC PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1992 | 1992 | [7 empty] | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.154 | [6 empty] | OTHER | [8 empty] | INTENTIONAL RELEASE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TOTAL COST UNDER INVESTIGATION | 2.29 | 0 | 0 | 45 | 39.25359712230215827338129496402877697842 | 45 | 31.96942446043165467625899280575539568345 | 39.25359712230215827338129496402877697842 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 259 | 92 | 99 | 192.619(A)(2) | 1992-01-01 | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ISSUE OCCURRED DURING MAINTENANCE OPERATIONS, THE CONDITION WAS NOTED BY THE FIELD TECHNICIANS ALREADY ON SITE. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [222 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED |  | YES |  |  |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [37 empty] | YES | [11 empty] | JEFF WEATHERHOLTZ | MANAGER GAS ENGINEERING AND STANDARDS | jeffrey.weatherholtz@bge.com | 410-598-1601 |  |  |  |  | ROBERT REX | SR. MANAGER GAS ENGINEERING AND ASSET PERFORMANCE | 302-593-3732 | robert.rex@delmarva.com | AT APPROXIMATELY 11:00 AM ON 11/20/2023, DURING A ROUTINE INSPECTION OF A DISTRICT REGULATOR STATION LOCATED AT 1410 COVENTRY-MEADOWS DRIVE IN SYKESVILLE, MD, AN ABNORMAL OPERATING CONDITION OF OVER PRESSURIZATION WAS DISCOVERED ON THE GAS SYSTEM. DURING THE INSPECTION OF THE REGULATOR, A CONTROL LINE VALVE DIDN'T CLOSE PROPERLY DUE TO A BROKEN OPERATING HANDLE. THIS ALLOWED HIGHER PRESSURE GAS (250PSIG) TO FLOW INTO A MAIN WITH AN MAOP OF 99PSIG. THE CREW RECOGNIZED THE PROBLEM, AND THEIR INITIAL REACTIONS OF CLOSING/READJUSTING THE STATION BYPASS THROTTLE VALVE AND RELIEVING THE PRESSURE FROM THE REGULATOR STATION LIKELY CAUSED THE OHP PRESSURE TO ENTER THE DOWNSTREAM SIDE OF THE MAIN THROUGH THE BYPASS AND OVER PRESSURIZE THE MAIN. THE EVENT LASTED LESS THAN 15MIN BEFORE THE CREW WAS ABLE TO STABILIZE PRESSURE IN THE MAIN. A LEAK SURVEY OF THE IMPACTED AREA WAS PERFORMED, AND CREWS CHECKED ALL HOUSES IN THE AREA TO VERIFY PRESSURE AND TURN SERVICES OFF FOR SAFETY. 15 SERVICES WERE IMPACTED IN TOTAL, AND ALL WERE TURNED ON LATER THAT DAY AFTER INSPECTIONS WERE PERFORMED.
2026-06-30 10:38 | NO | YES | NO | 20230080 | 39019 | 2023-12-26 10:47 | ORIGINAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2023-11-28 15:45 | EASTERN | NO | 2023 | 1475 MCNEILL ROAD | SANFORD | LEE | NC | 27330 | 35.5086 | -79.1801 | [5 empty] | YES |  |  |  | 2023-11-28 17:00 | 1385340 | 1385490 | NATURAL GAS |  | 284.63 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-11-28 15:45 | OPERATOR/CONTRACTOR |  | 284.63 | NO | 3 | 2023-11-28 15:32 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-11-28 15:45 | 2023-11-28 15:35 | 2023-11-28 15:35 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1997 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | DRISCOPLEX DRISCO/PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 5 | 0.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 15271 | 15889.631076528160283 | 0 | 0 | 217500 | 226310.9658270496275 | ESTIMATED VEHICLE(S) AND EQUIPMENT DAMAGES | 3.25 | 925 | 806.879496402877697841726618705035971223 | 0 | 0 | 233696 | 99005.0441145238970893453237410071942446 | 243007.4763999806654808417266187050359712 | 1 | 0 | 2 | 0 | 0 | 2 | 1 | 55 | 55 | 60 | 192.621 M | 1997-07-29 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA WAS NOT A CONTRIBUTING FACTOR IN THIS INCIDENT AS THE SYSTEM PRESSURE DID NOT DECREASE TO THE POINT OF PASSING AN ALARM THRESHOLD. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2022-06-29 | NO |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | MEASURED DEPTH FROM GRADE | 36 | UTILITY | BACKHOE/TRACKHOE | WATER | YES | A233322409 |  | Unknown | CONTRACT LOCATOR | YES | YES | 14 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JOHNNIE WALLER | ENGINEER III | johnnie.waller.jr@dominionenergy.com | 803-491-4644 |  | KEN GRIFFIN | ken.griffin@dominionenergy.com | 919-819-9850 | SCOTT SWINDLER | DIRECTOR - GAS OPERATIONS | 704-718-4231 | scott.swindler@dominionenergy.com | THE CITY OF SANFORD WATER DEPARTMENT DAMAGED A 4-INCH PLASTIC GAS MAIN WHILE REPAIRING A WATER LINE NEAR THE INTERSECTION OF MCNEILL ROAD AND HAWKINS AVENUE IN SANFORD, NC. THE GAS MAIN HAD BEEN PROPERLY LOCATED AND MARKED BEFORE THE WATER DEPARTMENT BEGAN ITS WORK. DURING THE COURSE OF THE WATER DEPARTMENT'S EXCAVATION WORK, THE BELL HOLE BECAME MUDDY AND WORKERS LOST SIGHT OF THE GAS LINE, DAMAGING THE GAS MAIN WITH A BACKHOE. OPERATOR RESOURCES WERE DISPATCHED TO THE SCENE AND A REPAIR PLAN INITIATED. OPERATOR ULTIMATELY REPLACED 30 FEET OF PIPE. THE AREA WAS MADE SAFE WITHIN 5 MINUTES OF ARRIVING ONSITE AND FINAL REPAIRS WERE COMPLETED APPROXIMATELY 14 HOURS AFTER THE INITIAL REPORT. PROPERTY DAMAGE EXCEEDING THE REPORTING CRITERIA WAS CONFIRMED AT 4:56 P.M. THE NRC WAS CONTACTED AT 5:00 P.M. AND THE NCUC WAS CONTACTED AT 5:12 P.M. RECORDED ON OUR LDF # 614354.
2026-06-30 10:38 | NO | YES | NO | 20240001 | 39401 | 2024-01-12 18:11 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2023-12-15 15:26 | PACIFIC | NO | 2023 | 3401 W EMPIRE AVE | BURBANK | LOS ANGELES | CA | 91504 | 34.1926 | -118.3491 | [7 empty] | YES | PC FITTINGS | 2023-12-16 18:22 | 1386895 | 1387044 | NATURAL GAS |  | 3528 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-12-15 15:25 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-12-15 15:25 | 2023-12-15 15:25 | 2023-12-16 18:22 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 60 | NO | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | PRIVATELY OWNED |  | MAIN VALVE |  | 1969 | UNKNOWN | [7 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 250000 | 260127.54692764325 | 100000 | 104051.0187710573 | 0 | 0 |  | 6 | 21168 | 18464.8920863309352517985611510791366906 | 0 | 0 | 371168 | 162916.6460484749003597122302158273381295 | 382643.4577850314852517985611510791366906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 110 | 125 | 192.619(A)(2) | 1969-12-01 | PRESSURE DID NOT EXCEED MAOP | OTHER | SCG USES ODORANT INJECTION PUMP SYSTEMS AT POINT OF ENTRY GAS SUPPLIES. | 10 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE IS NO CONTROLLER OR CONTROL ROOM THAT OPERATES THIS ASSET. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | VALVE | MATERIAL/WELD/EQUIP FAILURE | VALVE | EQUIPMENT FAILURE | VALVE | [197 empty] | VALVE | [16 empty] | OTHER | SMALL CRACK IN THE FITTING | [65 empty] | CARLOS CHAVEZ | PIPELINE SAFETY AND COMPLIANCE ADVISOR | cchavez@socalgas.com | 213-264-6814 |  | CARLOS CHAVEZ | cchavez@socalgas.com | (213)264-6814 | CARLOS CHAVEZ | PIPELINE SAFETY AND COMPLIANCE ADVISOR | (213)264-6814 | cchavez@socalgas.com | ON 12/15/2023, SOCALGAS RESPONDED TO A GAS LEAK AT 3401 W EMPIRE AVE, BURBANK, CA. SOCALGAS SAFELY CONTROLLED THE RELEASE OF GAS. UPON CONTROLLING THE GAS, IT WAS DISCOVERED THAT A MATERIAL FAILURE ON A 6-IN VALVE CAUSED THE RELEASE OF NATURAL GAS. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO COSTS ASSOCIATED WITH THE INCIDENT POTENTIALLY EXCEEDING $139,700. THE DAMAGED VALVE WAS REMOVED AND REPLACED WITH NEW PIPE.
2026-06-30 10:38 | NO | YES | NO | 20240002 | 40003 | 2024-01-19 11:26 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | 3600 MIDTOWN DR. | TAMPA | FL | 33607 | 2023-12-18 09:02 | EASTERN | NO | 2023 | 3264 LONGLEAF PINE PKWY | ST JOHNS | ST JOHNS COUNTY | FL | 32259 | 30.0893 | -81.5799 | [5 empty] | YES |  |  |  | 2023-12-18 18:37 | 1387045 | 1387186 | NATURAL GAS |  | 130 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-12-18 15:45 | YES | OPERATOR | 2023-12-18 20:02 | 2023-12-18 09:02 | 2023-12-18 09:02 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 168 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2015 | 2015 |  |  |  |  | 6 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 277633 | 288879.964944649513709 | 0 | 0 | 0 | 0 |  | 10 | 1300 | 1133.992805755395683453237410071942446043 | 0 | 0 | 278933 | 118226.0648411160585736474820143884892086 | 290013.957750404909392453237410071942446 | 84 | 0 | 1450 | 0 | 0 | 0 | 0 | 50 | 50 | 60 | 192.619(A)(2) | 2015-09-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PERIODIC PRESSURE CHECK DURING ROUTINE MAINTENANCE. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 2015 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [7 empty] | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [70 empty] | YES | [15 empty] | IYANNA JONES | COMPLIANCE ANALYST | iejones@tecoenergy.com | (407)-420-6617 |  | JAMES WHITE JR. | jtwhitejr@tecoenergy.com | (904)-219-5163 | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | 407-420-6667 | rharris@tecoenergy.com | ON DECEMBER 18, 2023, AT APPROXIMATELY 09:02 HOURS, PGS WAS NOTIFIED BY THE PUBLIC OF A GAS ODOR AT 3264 LONGLEAF PINE PARKWAY, ST. JOHNS COUNTY FLORIDA. RESPONDING CREWS WERE DISPATCHED AND UPON ARRIVAL, CONFIRMED THERE WAS AN ACTIVE LEAK. THE PIPELINE WAS EXCAVATED AND SQUEEZED OFF, STOPPING THE ESCAPING GAS TO MAKE SAFE AT 15:45. AN ASSESSMENT WAS MADE OF THE SCENE, INCLUDING THE ABILITY TO SAFELY MANAGE THE SITE. AN EVALUATION OF OPTIONS FOR THE ONE-WAY FEED PE PIPELINE CONCLUDED THAT IT WAS SAFER TO TAKE THE LINE OUT OF SERVICE TO SAFELY INSTALL A BYPASS. AS A RESULT, 1,534 CUSTOMERS WERE OUT OF SERVICE. THE REPAIR WAS COMPLETED, AND RESTORATION OF THE AFFECTED CUSTOMERS WAS COMPLETED. PGS CREWS IDENTIFIED THE SOURCE OF THE LEAK AS A PLASTIC FUSION OF THE 6-INCH MAIN. THE FUSION WAS CUT OUT AND SENT TO A TESTING AND ANALYSIS LAB TO IDENTIFY THE CAUSE. THE TESTING FACILITY IDENTIFIED THE PLASTIC FUSION AS A FAILED WELD WITH TWO POTENTIAL CONTRIBUTORS, #1 - SURFACE CONTAMINATION OF THE FUSION INTERFACE PRIOR TO JOINING (E.G., DUST FROM SURROUNDING ENVIRONMENT) AND/OR #2 - REMOVAL OF THE JOINING FORCE SHORTLY AFTER THE BEAD WAS PUSHED OUT (E.G., INADVERTENT SWITCHING OF BUTT-FUSION MACHINE'S HYDRAULIC PRESSURE TOGGLE LEVER) PREMATURELY. PGS HAS IMPLEMENTED THEIR PROCEDURE FOR A FUSION INVESTIGATION OF SEVERAL ADJACENT BUTT-FUSIONS TO CONFIRM PROPER PROCEDURES WERE FOLLOWED FOR A SAFE INSTALLATION OR DETERMINE IF ADDITIONAL FUSIONS NEED TO BE REPLACED. THIS EXERCISE IS EXPECTED TO TAKE SEVERAL MONTHS FOR EXCAVATION, REMOVE/REPLACEMENT AND TESTING OF THE SAMPLE FUSIONS.
2026-06-30 10:38 | NO | NO | NO | 20240003 | 39095 | 2024-01-21 14:44 | ORIGINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2023-12-21 14:00 | EASTERN | NO | 2023 | 9827 LOVE RD. | FORT MEADE | ANNE ARUNDEL | MD | 20755 | 39.1076 | -76.7625 | [5 empty] | YES |  |  |  | 2023-12-22 10:34 | 1387317 | 1387444 | NATURAL GAS |  | 5900 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-12-21 14:20 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-12-21 14:20 | 2023-12-21 16:14 | 2023-12-22 09:45 | YES | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2012 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | CHEVRON PHILLIPS PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | MECHANICAL PUNCTURE | 2 | 4 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 4000 | 4162.040750842292 | 0 | 0 |  | 2.29 | 13511 | 11785.6744604316546762589928057553956835 | 0 | 0 | 17511 | 11288.6789866999392517985611510791366906 | 15947.7152112739466762589928057553956835 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 92 | 92 | 99 | 192.619(A)(2) | 2012-09-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | [8 empty] | YES |  | NO | NO | > 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | STREET LIGHT | YES | 23898792 | MISS UTILITY OF MARYLAND | Unknown | CONTRACT LOCATOR | YES | YES | 24 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | JEFF WEATHERHOLTZ | MANAGER - GAS ENGINEERING AND STANDARDS | jeffrey.weatherholtz@bge.com | 410-598-1601 |  |  |  |  | ROBERT REX | SR. MANAGER GAS ENGINEERING AND ASSET PERFORMANCE | 302-593-3732 | robert.rex@delmarva.com | ON DECEMBER 21, 2023 AT 14:00, A THIRD-PARTY CONTRACTOR STRUCK A 4" PLASTIC HIGH PRESSURE GAS MAIN ON NSA PROPERTY. THE MAIN WAS NOT SHUT OFF UNTIL 24:00, RESULTING IN THE RELEASE OF 5900 MCF OF NATURAL GAS INTO THE ATMOSPHERE. THE MAIN WAS REPAIRED AND SERVICE WAS RESTORED TO CUSTOMER ON DECEMBER 22ND. THE ONE CALL CENTER WAS NOTIFIED PRIOR TO START OF WORK AND THE GAS MAIN WAS MARKED WITHIN TOLERANCE PRIOR TO EXCAVATION.
2026-06-30 10:38 | NO | YES | NO | 20240004 | 39103 | 2024-01-23 10:49 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2023-12-24 11:52 | EASTERN | NO | 2023 | 418 EAST RUSSELL STREET | FAYETTEVILLE | CUMBERLAND | NC | 28301 | 35.0285 | -78.5224 | [5 empty] | YES |  |  |  | 2023-12-25 03:28 | 1387491 | 1387539 | NATURAL GAS |  | 602 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-12-24 11:30 | OTHER | SQUEEZED OFF | 602 | NO | 0 | 2023-12-25 11:52 |  |  |  | 2023-12-25 12:22 | 2023-12-25 12:22 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | OVERHEAD CROSSING |  |  |  | YES | YES | CASED | [9 empty] | INVESTOR OWNED |  | MAIN |  | 1986 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | OTHER | 2" PE MAIN INSERTED IN 4" STEEL CASING | [9 empty] | RUPTURE |  |  |  |  | OTHER | MELTED. | 2 | 2 |  | CLASS 4 LOCATION | 0 | 0 | 2000000 | 2081020.375421146 | 10000 | 10405.10187710573 | 0 | 0 |  | 3 | 1806 | 1575.377697841726618705035971223021582734 | 0 | 0 | 2011806 | 850526.5820037698337410071942446043165468 | 2093000.85499609345661870503597122302158 | 0 | 0 | 3 | 2 | 0 | 3 | 0 | 57 | 57 | 60 | 192.619(A)(4) | 1986-05-08 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | EXPOSED CASING LEAKING AND ON FIRE UNDER A BRIDGE. | [47 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | FAYETTEVILLE FIRE DEPARTMENT RESPONDED TO A FIRE AT 418 EAST RUSSELL STREET AT A FOUR LANE DIVIDED HIGHWAY BRIDGE WITH A TRAIN BRIDGE BETWEEN THE TWO LANES. DURING THE COURSE OF EXTINGUISHING THE FIRE, THE FIRE DEPARTMENT REQUESTED ASSISTANCE FROM PIEDMONT NATURAL GAS, PWC WATER, SPECTRUM, NCDOT, CENTURY LINK, CSX, PWC ELECTRICITY, CITY STREET MAINTENANCE AND THE FAYETTEVILLE POLICE DEPARTMENT. A PIEDMONT TECHNICIAN FOUND THE EXPOSED CASING ON A 4" STEEL DISTRIBUTION PIPELINE LEAKING AND ON FIRE. AFTER BEING DUG UP, THE LINE WAS CLAMPED ON BOTH SIDES OF THE BRIDGE WHILE THE FIRE DEPARTMENT CONTINUED TO SPRAY WATER TO COOL THE BRIDGE. THE WOODED TRAIN TRESTLE HAD DAMAGE AND FIRE WAS ON THE UNDER SIDE. THE LINE WAS ABANDONED. THE CAUSE OF THE FIRE IS UNDETERMINED AFTER INVESTIGATION. THERE WERE HOMELESS PERSONS STAYING UNDER THE BRIDGE AND IT COULD NOT BE RULED OUT THAT A CAMPFIRE OR OTHER OPEN FLAME WAS THE CAUSE.
2026-06-30 10:38 | NO | YES | YES | 20240005 | 41696 | 2024-01-24 13:38 | SUPPLEMENTAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2023-12-24 09:03 | CENTRAL | NO | 2023 | 105 W GULF AVE | ROGERS | BELL | TX | 76569 | 30.9342 | -97.2265 | [5 empty] | YES | YES |  |  | 2023-12-24 11:14 | 1387457 | 1387538 | NATURAL GAS |  | 1 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 2023-12-24 09:03 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 9 | 2023-12-24 09:30 |  |  |  | 2023-12-24 10:45 | 2023-12-24 11:21 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1985 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | PE 2306/2406 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | OTHER | UNDER INVESTIGATION | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 48390 | 50350.28798331462747 | 0 | 0 |  | 9.2031 | 9 | 7.85071942446043165467625899280575539568 | 0 | 0 | 48399 | 20451.6152871061122209352517985611510791 | 50358.1387027390879016546762589928057554 | 0 | 0 | 10 | 4 | 0 | 10 | 0 | 14.5 | 14.5 | 35 | 192.619(A)(2) | 1996-01-09 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 10.8 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | WILLIAM BROOKS | DIRECTOR REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 806-787-9422 |  | DALE GAMBRELL | dale.gambrell@atmosenergy.com | 512-844-8270 | JEFFREY KNIGHTS | SR. VP TECHNICAL AND OPERATING SERVICES | 2142062701 | jeff.knights@atmosenergy.com | UPDATE: DECEMBER 12, 2025 - PART A -10E - NUMBER OF INJURIES UPDATED PART C - 2A - YEAR INSTALLED UPDATED PART C - 3B & 3C - PIPE SPECIFICATIONS UPDATED UPDATE: JANUARY 13, 2025 - THE EVENT REMAINS UNDER INVESTIGATION. ON DECEMBER 24, 2023, AT APPROXIMATELY 9:30 A.M., ATMOS ENERGY RECEIVED A NOTIFICATION OF AN EXPLOSION AND STRUCTURE FIRE. THE FIRST ATMOS ENERGY TECH ARRIVED ON THE SCENE AT 9:34 A.M. AND REQUESTED ADDITIONAL COMPANY RESOURCES. AT 5:43 P.M., THE GAS SYSTEM IN THE VICINITY WAS ISOLATED AND SHUT OFF. ACCORDING TO THE REPORT OF THE BELL COUNTY FIRE MARSHALL'S OFFICE, THERE WAS 1 FATALITY, 1 HOSPITALIZATION, AND 4 OTHER INDIVIDUALS WITH NON-LIFE THREATING INJURIES REPORTED AT THE AFFECTED RESIDENCE. THIS EVENT IS STILL UNDER INVESTIGATION. THE VOLUME OF GAS RELEASED (PART A, 21C) IS STILL UNKNOWN AT THIS TIME. A VALUE OF 1 WAS ENTERED AS IT IS THE LOWEST VALUE THAT WILL VALIDATE IN THE FIELD. THE COST ESTIMATES IN PART D HAVE NOT BEEN FINALIZED.
2026-06-30 10:38 | NO | YES | NO | 20240006 | 39830 | 2024-01-24 14:13 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2023-12-25 23:30 | CENTRAL | NO | 2023 | 241 PLANTATION DRIVE | COPPELL | DALLAS | TX | 75019 | 32.9631 | -96.9997 | [5 empty] | YES |  |  |  | 2023-12-26 01:18 | 1385719 | 1387679 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 11 | 2023-12-25 23:50 |  |  |  | 2023-12-25 23:50 | 2023-12-26 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1989 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 66406 | 69096.119525108310638 | 0 | 0 | 55707 | 57963.701026792890111 | 0 | 0 |  | 9.2031 | 9 | 7.85071942446043165467625899280575539568 | 0 | 0 | 122122 | 51600.2628885821326939352517985611510791 | 127067.6712713256611806546762589928057554 | 0 | 0 | 18 | 0 | 0 | 11 | 0 | 45 | 45 | 60 | 192.619(A)(2) | 1989-07-06 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 3.4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  | CONSTRUCTION | NO | [50 empty] | WILLIAM BROOKS | DIRECTOR REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 806-787-9422 |  | JEFFREY BROWN | jeffrey.brown@atmosenergy.com | 214-208-7729 | JEFFREY KNIGHTS | SR. VP TECHNICAL AND OPERATING SERVICES | 2142062701 | jeff.knights@atmosenergy.com | ON DECEMBER 25, 2023, AT APPROXIMATELY 11:30 P.M., ATMOS ENERGY RECEIVED A NOTIFICATION OF AN EXPLOSION. THE FIRST ATMOS ENERGY TECH ARRIVED ON THE SCENE AT 11:50 P.M. ON DECEMBER 25, 2023, AND REQUESTED ADDITIONAL COMPANY RESOURCES. WHILE ATMOS ENERGY WAS RESPONDING TO THE EVENT AND MAKING THE AREA SAFE, AN ATMOS ENERGY REPRESENTATIVE SPOKE WITH THE RAILROAD COMMISSION OF TEXAS FROM 12:58 A.M. UNTIL 1:16 A.M. TO INFORM THAT STATE REGULATOR AND ANSWER QUESTIONS. AFTER THAT CALL WAS COMPLETE, THE SAME ATMOS ENERGY REPRESENTATIVE CALLED THE NRC TO REPORT THE POTENTIAL INCIDENT AT 1:18 A.M. ON DECEMBER 26. AT 4:42 A.M., ON DECEMBER 26, 2023, THE GAS SYSTEM IN THE VICINITY WAS ISOLATED AND SHUT OFF. BASED ON THE INFORMATION OBTAINED IN THE ONGOING RESPONSE AND EVACUATIONS, ATMOS ENERGY CONFIRMED DISCOVERY THAT THE INCIDENT MET REPORTING CRITERIA ON DECEMBER 27, 2023, AT 3:30 P.M. THERE WERE NO FATALITIES OR INJURIES AT THE AFFECTED RESIDENCE. ON FEBRUARY 20, 2024, ESTIMATES FOR THE HOME'S REPAIR COSTS WERE PROVIDED. WHEN COMBINED WITH THE COMPANY'S COSTS, THE TOTAL AMOUNT WAS BELOW THE REPORTABLE THRESHOLD. THE COMPANY'S INVESTIGATION CONCLUDED THAT THE RELEASE WAS FROM A SERVICE TAP TEE CAP, WHICH WAS OVER-TIGHTENED DURING INSTALLATION BY A LONESTAR GAS CONTRACTOR IN 1989, CAUSING A CRACK AND ULTIMATELY FAILURE. THIS CONSTRUCTION ACTIVITY, WHICH IS REFERENCED IN PART G7, 4, OCCURRED PRIOR TO ATMOS ENERGY'S OWNERSHIP OF THE FACILITIES AND PRIOR TO THE ADOPTION OF THE COMPANY'S OPERATOR QUALIFICATION PLAN. THE VOLUME OF GAS RELEASED (PART A, 21C) IS STILL UNKNOWN. A VALUE OF 1 WAS ENTERED AS IT IS THE LOWEST VALUE THAT WILL VALIDATE IN THE FIELD.
2026-06-30 10:38 | NO | YES | NO | 20240007 | 39135 | 2024-01-30 15:22 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2024-01-04 14:08 | EASTERN | NO | 2024 | 3900 BRAGG BOULEVARD | FAYETTEVILLE | CUMBERLAND | NC | 28303 | 35.0811 | -78.9435 | [6 empty] | YES |  |  | 2024-01-04 16:13 | 1388195 | 1388341 | NATURAL GAS |  | 3735 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 8 | 2024-01-04 14:22 |  |  |  | 2024-01-04 14:22 | 2024-01-04 14:22 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 60 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1958 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | 3RD PARTY DAMAGED 2" TEE TORE OFF OF 12" STEEL MAIN | CLASS 1 LOCATION | 0 | 0 | 300000 | 305991.9792403869 | 100000 | 101997.3264134623 | 0 | 0 |  | 3 | 11205 | 12786.8823529411764705882352941176470588 | 0 | 0 | 411205 | 176082.0622834650117647058823529411764706 | 420776.1880067903764705882352941176470588 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 55 | 60 | 60 | 192.619(A)(1) | 1958-01-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET |  |  | YES | [5 empty] | NO | NO | > 36” |  | UTILITY | BACKHOE/TRACKHOE | STORM DRAIN/CULVERT | YES | C233490205 |  | Unknown | FACILITY OWNER | UNKNOWN/OTHER | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO NO RESPONSE FROM OPERATOR/CONTRACT LOCATOR | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | CONTRACTOR WAS DIGGING UP ASPHALT DURING A STORM DRAIN INSTALLATION AND STRUCK A 2" RETIRED STUB RIPPING THE TEE OFF THE 12" STEEL MAIN WITH A CAT 326 TRACKHOE. INTERNAL LOCATOR DID NOT MARK LINES FOR THIS SPECIFIC TICKET AS THEY WERE ADVISED BY CONTACT ON THE TICKET THAT THE WORK WAS ALREADY COMPLETED. THERE WERE MARKS FROM PREVIOUS LOCATES IN THIS AREA.
2026-06-30 10:38 | NO | YES | NO | 20240008 | 39171 | 2024-02-09 08:53 | ORIGINAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2024-01-12 08:40 | EASTERN | NO | 2024 | 3315 GREENFIELD RD | MELVINDALE | WAYNE COUNTY | MI | 48122 | 42.2895 | -83.1698 | YES | [8 empty] | 2024-01-12 14:58 | 1388827 | 1389180 | NATURAL GAS |  | 4666 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-01-12 08:40 | YES | OPERATOR | 2024-01-12 08:50 | 2024-01-12 08:50 | 2024-01-12 14:51 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 84 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1921 | UNKNOWN |  |  |  |  | 24 | CAST IRON | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 75000 | 76497.994810096725 | 70000 | 71398.12848942361 | 0 | 0 |  | 3.75 | 17498 | 19968.3058823529411764705882352941176471 | 0 | 0 | 162498 | 76317.4983130501844117647058823529411765 | 167864.4291818732761764705882352941176471 | 9 | 0 | 180 | 0 | 0 | 180 | 9 | 45 | 45 | 50 | 192.621 M | 1921-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | COUNTY ROAD | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | BORING | WATER | YES | 2023121501129 |  | NO | FACILITY OWNER | YES | YES | 9 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | JUSTIN MORRIS |  | justin.morris@dteenergy.com | 2484621760 |  |  |  |  | MARINA DARLING |  | 5868724760 | marina.darling@dteenergy.com | BRICCO CONSTUCTION, A CONTRACTOR FOR THE CITY OF MELVINDALE, WAS BORING WATER MAIN. ON PULLBACK, A 24" 50PSIG CAST IRON MAIN WAS HIT, CAUSING A 4" DIAMETER HOLE. THE LINE WAS MARKED BUT THE CONTRACTOR DID NOT VERIFY LOCATION VIA POTHOLES. THIS WAS REPORTED TO THE MICHIGAN PUBLIC SERVICE COMMISSION AT 10:20AM ON 01/12/24 DUE TO THE COST BEING OVER $10K TO REPAIR, THE CLOSURE OF GREENFIELD RD, 189 CUSTOMERS AFFECTED, POTENTIAL MEDIA, AND OVER 1MMCF OF GAS LOSS. THIS WAS ALSO REPORTED TO PHMSA/NRC AT 14:58 ON 01/12/24 UPON GAS LOSS CALCULATION ESTIMATED TO BE OVER 3MMCF. THE GAS WAS SHUT OFF AT 17:10 ON 01/12/24 VIA MAIN LINE VALVES, AND A REPAIR WAS MADE AND GAS WAS RESTABLISHED AT 00:30 ON 01/13/24, AND AT 01:45 THE 189 CUSTOMERS BEGAN TO BE RELIT AND CONTINUED THROUGHOUT THE DAY ON 01/13/24.
2026-06-30 10:38 | NO | YES | NO | 20240009 | 40853 | 2024-02-15 16:31 | SUPPLEMENTAL | 31632 | NORTHWESTERN CORPORATION | 3010 W. 69TH ST. | SIOUX FALLS | SD | 57108 | 2024-01-17 12:50 | MOUNTAIN | YES | 2024 | 1413 S 4TH ST. W | MISSOULA | MISSOULA | MT | 59801 | 46.8657 | -114.0177 | YES | [8 empty] | 2024-01-17 02:19 | 1389218 | 1389458 | NATURAL GAS |  | 16.28 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-17 12:50 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 50 | 2024-01-17 12:50 | YES | OPERATOR | 2024-01-17 12:00 | 2024-01-17 10:35 | 2024-01-17 01:40 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 38 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 3.625 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - LOW FREQUENCY |  | 0.322 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 400000 | 407989.3056538492 | 2500 | 2549.9331603365575 | 10000 | 10199.73264134623 | 0 | 0 |  | 9 | 147 | 167.752941176470588235294117647058823529 | 0 | 0 | 412647 | 170981.7520974703522058823529411764705882 | 420906.7243967084580882352941176470588235 | 4 | 0 | 46 | 0 | 0 | 46 | 4 | 31 | 31 | 35 | 192.619(A)(4) | 1995-01-26 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 3 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROST HEAVE |  | NO | [218 empty] | MELISSA BARUTH | SUPERVISOR DOT | melissa.baruth@northwestern.com | 6053537462 |  |  |  |  | MELISSA BARUTH | DOT SUPERVISOR | 605-353-7462 | melissa.baruth@northwestern.com | A7 - UNABLE TO DETERMINE AS TIME PIPE HAS BEEN LEAKING IS UNKNOWN 21C - NO ADDITIONAL GAS WAS RELEASED BEYOND UNDERGROUND PIPE LEAKING FOR UNKNOWN AMOUNT OF TIME PART C 4.A. - EDUCATED GUESS DUE TO AGE OF PIPE TIMELINE OF EVENTS PRIOR TO EXPLOSION: 10:35 AM: RECEIVED ODOR CALL FOR 1342 S. 5TH ST W 10:52 AM: ARRIVED AT THE SITE OF THE ODOR CALL 1342 S. 5TH ST W WORKED INSIDE, CHECKING APPLIANCES, VENTING, AMBIENT CHECKED OUTSIDE AMBIENT, METER SET, BAR HOLED ALONG SERVICE 11:30 AM: REQUESTED ADDITIONAL HELP WITH LEAK SURVEYING 11:36 AM: GAS SUPERVISOR INFORMING ABOUT ACTIVE LEAK, UNDER INVESTIGATION 11:42 - 11:48 AM: EMERGENCY LOCATES REQUESTED 11:50 AM: ADDITIONAL HELP ARRIVED ONSITE AND BEGAN TO MONITOR AMBIENT, SURVEY SURROUNDINGS, MAPPING 12:00 PM: NOTIFIED MISSOULA FIRE DEPARTMENT (MFD), GAS LEAK, REQUESTED FD TO BE DISPATCHED BEGIN EVACUATING HOMES 12:04 PM: DE-ENERGIZED POWER @ 1410 A/B S. 5TH ST W. MFD ASSISTANCE CHECKING AMBIENT INSIDE HOMES 12:36 PM: DE-ENERGIZED SECONDARY POWER TO 1410 A/B S. 5TH ST W. 12:36 - 12: 48 PM: BEGUN BARHOLING PRIOR 12:48 PM: REQUESTED BACKHOE TO ASSIST WITH BARHOLING 12:50 PM: HOUSE EXPLOSION POST EXPLOSION: 12:50PM: 1413 S. 4TH ST W HOUSE EXPLOSION 12:50 PM: DE-ENERGIZE PRIMARY FOR MULTIPLE BLOCKS FROM RUSSELL & 5TH ' EAST (FOUR BLOCKS EAST) MFD - INCREASED PERIMETER CONTINUED EVACUATIONS, ROAD CLOSURES, FIRE IC DAVE ANY INJURIES RESULTED: HIS RESPONSE NO ONE WAS HOME, NO INJURIES 1:05 PM: DE-ENERGIZED PRIMARY RUSSELL & 5TH ' EAST (FOUR BLOCKS EAST) 1:10 PM: ADDITIONAL SUPPORT ARRIVED ONSITE. INFORMED FIRE IC DAVE ' OF PLAN TO OPERATE ZV # 24, TO ELIMINATE GAS FLOW FROM EAST AND INSTALL PRESSURE CONTROL FITTING (PCF) TO ELIMINATE GAS FLOW FROM WEST 1:39 PM ZONE VALVE # 24 STOPPING FEED FROM THE EAST. 1:40 PM: BEGAN BELLHOLE EXCAVATION AT 1501 S. 4TH ST W ALLEY 2:00 PM: BEGAN SHUTTING OFF ALL LOCKWING VALVES 2:15 PM: MFD SHUT OFF LOCKWING VALVE TO 1413 S. 4TH ST W 4:00 PM: PCF # 1 PILOT BIT BROKE (WEST OF RUSSELL) 4:00 PM: BEGAN PCF # 2 (WEST OF RUSSELL) 5:10 PM: PCF # 2 STOPPERED, FEED FROM WEST WAS SHUT OFF. 5:15 PM: GAS SUCCESSFUL STOPPED.CONFIRMED FEED FROM WEST WAS SHUT OFF BY BREAKING DOWN METER SET AT 1501 S. 4TH ST W. 5:15 PM TO 1 AM: CONTINUED BARHOLING, AMBIENT MONITORING, TURNED OFF ALL THE LOCKWING VALVES EAST OF PRINCE. RESTORATION EFFORTS COMPLETED IN THE FOLLOW DAY. UPDATE 5-7-2025 ON JUNE 3, 2024 DESTRUCTIVE TESTING WAS CONDUCTED AT MATERIAL EVALUATION AND ENGINEERING. ENCLOSED IS THE TESTING PROTOCOL UTILIZED TO DESTRUCTIVELY TEST THE PIPE REMOVED FROM EVENT IN MISSOULA, MT ON JANUARY 17, 2024. THE FOLLOWING TESTS WERE CONDUCTED. 'CHEMISTRY IDENTIFICATION (ASTM E415-2021) ENERGY DISPERSIVE X-RAY SPECTROSCOPY (EDS) KEYENCE MICROHARDNESS ROCKWELL HARNESS SCANNING ELECTRON MICROSCOPY (SEM) XS RESULTS INDICATED A SINGULAR IMMEDIATE (NOT OVER TIME) FACTURE CONSISTENT WITH THE PIPE COMING UP. GIVEN THE DIRECTION OF THE FRACTURE SOMETHING BELOW THE PIPE CAUSED THE SURFACE TO CHANGE/RISE UP TO CREATE THE FRACTURE.
2026-06-30 10:38 | NO | YES | YES | 20240010 | 41258 | 2024-02-15 17:08 | SUPPLEMENTAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2024-01-16 00:46 | CENTRAL | NO | 2024 | 3325 N 53RD ST, LINCOLN NE | LINCOLN | LANCASTER | NE | 68504 | 40.8459 | -96.6474 | [5 empty] | YES |  |  |  | 2024-01-16 04:19 | 1389085 | 1389208 | NATURAL GAS |  | 118.64 | 118.64 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2024-01-16 00:46 | OTHER | FIRE EXTINGUISHED AFTER SERVICE WAS SQUEEZED OFF. | 118.64 | NO | 1 | 2024-01-16 00:58 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2024-01-16 00:58 | 2024-01-16 01:43 | 2024-01-16 03:19 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | THIS IS STILL UNDER INVESTIGATION. | CLASS 3 LOCATION | 1 | 1.019973264134623 | 1700 | 1733.9545490288591 | 1 | 1.019973264134623 | 1 | 1.019973264134623 | ESTIMATES UNKNOWN AT THIS TIME. TOTAL LOSS TO HOME AND VEHICLE AT PROPERTY | 5.43 | 644 | 734.917647058823529411764705882352941176 | 644 | 734.917647058823529411764705882352941176 | 2991 | 1902.413877671852287588235294117647058824 | 3206.849762938910027823529411764705882352 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 8 | 8 | 12 | 192.619(A)(4) | 1952-12-18 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.4 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS LOSS ASSOCIATED WITH THIS INCIDENT WAS NOT LARGE ENOUGH TO HAVE BEEN INDICATED IN THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | EXACT CAUSE OF NATURAL GAS LEAK AND RESULTING EXPLOSION IS DISPUTED. | [45 empty] | BRIAN SISSON |  | brian.sisson@blackhillsenergy.com | 3083407028 |  |  |  |  | BRIAN SISSON |  | 3083407028 | brian.sisson@blackhillsenergy.com | EXPLOSION AT PRIVATE RESIDENCE OF 3325 N 53RD ST IN LINCOLN NE. THIS RESULTED IN DAMAGE TO THE RESIDENCE AND INJURY TO THE SINGLE OCCUPANT. THE GAS METER SERVING THIS RESIDENCE WAS DAMAGED FROM THE STRUCTURE EXPLOSION, RELEASED NATURAL GAS, AND IGNITED. GAS SERVICE TO THE METER WAS SHUT OFF AFTER DIGGING IT UP CLOSE TO THE MAIN AND PINCHING OFF. CAUSE OF EXPLOSION IS UNKNOWN AND STILL UNDER INVESTIGATION. PROPERTY LOSS IS YET UNKNOWN AND UNDER INVESTIGATION. ***UPDATED (8/15/2025)*** EXPLOSION AT PRIVATE RESIDENCE OF 3325 N 53RD ST IN LINCOLN NE. THIS RESULTED IN DAMAGE TO THE RESIDENCE AND INJURY TO THE SINGLE OCCUPANT AND FIRE DAMAGE TO THE NEIGHBORING STRUCTURE LOCATED NORTH OF PRIMARY RESIDENCE. THE GAS METER SERVING THE PRIMARY RESIDENCE WAS DAMAGED FROM THE STRUCTURE EXPLOSION, RELEASED NATURAL GAS, AND IGNITED. GAS SERVICE TO THE METER WAS SHUT OFF AFTER DIGGING IT UP CLOSE TO THE MAIN AND PINCHING OFF. EXACT CAUSE OF NATURAL GAS LEAK AND RESULTING EXPLOSION IS DISPUTED.
2026-06-30 10:38 | NO | YES | NO | 20240011 | 39702 | 2024-02-16 11:45 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2024-01-18 09:40 | EASTERN | NO | 2024 | 1223 MARION BARRY AVE SE | WASHINGTON | WASHINGTON | DC | 20020 | 38.8671 | -76.9879 |  | YES | [7 empty] | 2024-01-18 11:32 | 1389264 | 1389445 | NATURAL GAS |  | 162.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-18 09:55 | OPERATOR/CONTRACTOR |  | 162.7 | YES | 20 | 2024-01-18 09:40 |  |  |  | 2024-01-18 10:16 | 2024-01-18 10:16 | NO | PUBLIC PROPERTY | TRANSITION AREA | SOIL/AIR INTERFACE |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1981 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | OTHER | [8 empty] | MECHANICAL DAMAGE DUE TO IMPACT BY A VEHICLE. | CLASS 4 LOCATION | 500000 | 509986.6320673115 | 79220 | 80802.28198474483406 | 16988 | 17327.305811118975524 | 0 | 0 |  | 2.49 | 405 | 462.176470588235294117647058823529411765 | 0 | 0 | 596613 | 247307.8842818090928649411764705882352941 | 608578.3963337635448781176470588235294118 | 33 | 0 | 3 | 1 | 0 | 3 | 33 | 20 | 20 | 25 | 192.619(A)(2) | 1991-07-23 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS AN ACCIDENTAL HIT BY A VEHICLE TO THE SERVICE RISER. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | LARGE TRUCK | ROADWAY | 13 | NO | [142 empty] | MARK AIESI | SUPERVISOR | mark.aiesi@washgas.com | 5714054623 |  |  |  |  | SHANNON MALONEY | MANAGER | 5712055471 | smaloney@washgas.com | ON JANUARY 18, 2024, AT APPROXIMATELY 0930, A DELIVERY TRUCK STRUCK A METER AND RISER WHICH WAS LOCATED AT 1223 MARION BARRY AVE SE, WASHINGTON D.C.. WASHINGTON GAS WAS NOTIFIED AT 0940 VIA FIREBOARD OF THIS INCIDENT. THE RESULTING DAMAGE, WHICH WAS A BROKEN RISER, CAUSED A BLOWING GAS LEAK. SUBSEQUENTLY, A FLASH FIRE OCCURRED ON THE SECOND FLOOR AT 1225 MARION BARRY AVE SE. MINUTES LATER, AT APPROXIMATELY 1001, AN EXPLOSION OCCURRED AT 1223 MARION BARRY AVE SE. ONE PERSON WAS INJURED AND WAS TAKEN TO THE HOSPITAL WITH MINOR INJURIES. THE FIRST WASHINGTON GAS CREW ARRIVED AT 1016. WASHINGTON GAS STOPPED THE FLOW OF GAS USING VALVES AT 1251, CREATING AN OUTAGE OF 36 CUSTOMERS. CREWS HAVE RESTORED SERVICE TO THE CUSTOMERS THAT WERE AFFECTED.
2026-06-30 10:38 | NO | YES | YES | 20240012 | 39508 | 2024-02-16 15:47 | SUPPLEMENTAL FINAL | 4473 | ATMOS ENERGY CORPORATION - WEST TEXAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2024-01-20 09:47 | CENTRAL | NO | 2024 | 214 ENGLISH RD | AMARILLO | POTTER | TX | 79108 | 35.2352 | -101.7055 |  |  |  | YES | [5 empty] | 2024-01-20 11:07 | 1389461 | 1389595 | NATURAL GAS |  | 43.92 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2024-01-20 09:47 | OPERATOR/CONTRACTOR |  | 43.92 | NO | 0 | 2024-01-20 09:47 |  |  |  | 2024-01-20 10:05 | 2024-01-20 10:35 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1985 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | STRUCK BY VEHICLE | [5 empty] | CLASS 1 LOCATION | 25000 | 25499.331603365575 | 2575 | 2626.431155146654225 | 2006 | 2046.066367854053738 | 0 | 0 | N/A | 4.73 | 208 | 237.364705882352941176470588235294117647 | 0 | 0 | 29789 | 12444.8806729297109884117647058823529412 | 30409.1938322486359041764705882352941176 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 15 | 15 | 60 | 192.619(A)(1) | 1985-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 20 | YES | [5 empty] | YES | ABANDON FACILITIES INCLUDING MAIN STUB AND SERVICE LINE. | [111 empty] | YES | [23 empty] | DUSTIN CROSLEY | MGR. COMPLIANCE | dustin.crosley@atmosenergy.com | 806-290-5751 |  | ANTHONY RAMIREZ | anthony.ramirez@atmosenergy.com | 806-344-7638 | DUSTIN MCKNIGHT | V.P. TECHNICAL SERVICES | 512-591-1302 | dustin.mcknight@atmosenergy.com | UNIT 1 WAS EASTBOUND ON THE 10000 BLOCK OF AMARILLO BLVD EAST. UNIT 1 FAILED TO CONTROL SPEED STRIKING CHAIN LINK FENCE AND NW CORNER OF BUILDING OF 2014 EAGLE LANE LODGING THE VEHICLE ON A METER RISER CAUSING AN IGNITION OF NATURAL GAS.
2026-06-30 10:38 | NO | YES | YES | 20240013 | 41418 | 2024-02-20 14:35 | SUPPLEMENTAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2024-01-20 03:42 | CENTRAL | NO | 2024 | 1811 HIGHLAND DRIVE | CARROLLTON | DALLAS | TX | 75006 | 32.9532 | -96.8928 | [5 empty] | YES |  |  |  | 2024-01-20 05:49 | 1389442 | 1390832 | NATURAL GAS |  | 1 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2024-01-20 03:42 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 8 | 2024-01-20 05:00 |  |  |  | 2024-01-20 04:58 | 2024-01-20 05:00 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1974 | 1974 |  |  |  |  | 3 | ASTM D2513 | NIPAK | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2306 | LEAK |  |  | OTHER | BUTT-FUSION SEPARATION | [5 empty] | CLASS 3 LOCATION | 55000 | 56098.529527404265 | 25971 | 26489.725642840293933 | 25627 | 26138.854839977983621 | 0 | 0 |  | 9.1461 | 9 | 10.27058823529411764705882352941176470588 | 0 | 0 | 106607 | 44158.0592879378906631764705882352941176 | 108737.3805984578366716470588235294117647 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 46 | 46 | 55 | 192.619(A)(2) | 1974-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 8 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | WILLIAM BROOKS | DIRECTOR REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 8067879422 |  | JEFFREY BROWN | jeffery.brown@atmosenergy.com | 214-208-7729 | MARC ROTHBAUER | VP COMPLIANCE AND REGULATORY REPORTING | 469-236-8616 | marc.rothbauer@atmosenergy.com | UPDATE: SEPTEMBER 24, 2025 - THIS EVENT REMAINS UNDER INVESTIGATION. ON JANUARY 20, 2024, AT APPROXIMATELY 4:10 A.M., ATMOS ENERGY RECEIVED NOTIFICATION OF AN EXPLOSION. THE FIRST ATMOS ENERGY TECH ARRIVED ON THE SCENE AT 4:58 A.M. ON JANUARY 20, 2024, AND FOUND THE GAS HAD BEEN SHUT OFF BY THE FIRE DEPARTMENT. AFTER SURVEYING THE SCENE, ATMOS ENERGY PERSONNEL IDENTIFIED GAS ESCAPING FROM A BUTT-FUSION SEPARATION ON A 3 INCH POLYETHYLENE MAIN. A VALUE OF 1 WAS ENTERED IN THE ESTIMATED VOLUME OF GAS CONSUMED BY FIRE, (PART A, 7) AND IN THE VOLUME OF GAS RELEASED (PART A, 21C). THESE ARE INDETERMINATE AMOUNTS. EIGHT (8) HOMES WERE EVACUATED. THE NUMBER OF PEOPLE EVACUATED IS UNKNOWN. A VALUE OF 8 WAS ENTERED INTO A22. TWENTY-FIVE (25) HOMES LOST SERVICE, WHICH INCLUDES THE 8 HOMES THAT WERE EVACUATED.
2026-06-30 10:38 | NO | YES | NO | 20240014 | 39223 | 2024-02-20 16:55 | ORIGINAL FINAL | 30750 | MIDAMERICAN ENERGY COMPANY | 401 DOUGLAS STREET PO BOX 778 | SIOUX CITY | IA | 51101 | 2024-01-22 07:32 | CENTRAL | YES | 2024 | 33 NORTH 12TH STREET | FORT DODGE | WEBSTER | IA | 50501 | 42.5071 | -94.1824 |  | YES | [5 empty] | YES | WELDED 2" CAP ON MAIN AT 100 NORTH 12TH STREET | 2024-01-22 14:53 | 1389637 | 1389832 | NATURAL GAS |  | 18 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-22 07:32 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 18 | YES | 4 | 2024-01-22 07:32 | YES | OPERATOR | 2024-01-22 07:33 | 2024-01-22 07:32 | 2024-01-22 07:32 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | UNKNOWN |  |  |  |  | 2 | API 5L | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 4 LOCATION | 167800 | 171151.5137217897394 | 10000 | 10199.73264134623 | 60000 | 61198.39584807738 | 0 | 0 |  | 2.7 | 49 | 55.91764705882352941176470588235294117647 | 0 | 0 | 237849 | 98535.1692334023024352941176470588235294 | 242605.5598582721729294117647058823529412 | 6 | 0 | 27 | 0 | 0 | 3 | 6 | 32 | 32 | 35 | 192.619(A)(4) | 1989-09-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 4 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | THE SOURCE OF THE NATURAL GAS THAT EXPLODED WAS FROM A LEAK ON AN UNDERGROUND 2" GAS MAIN THAT WAS ABANDONED IN-PLACE UNDER PAVEMENT. THE MIGRATION PATH AND SOURCE OF IGNITION IS NOT KNOWN. | [45 empty] | CHRISTOPHER PAYER | GAS STANDARDS ENGINEER | chris.payer@midamerican.com | 7122777941 | 7122527369 | CHRISTOPHER PAYER | chris.payer@midamerican.com | 7122777941 | BRADLEY LEWIS | VICE PRESIDENT GAS DELIVERY | 7122334840 | bradley.lewis@midamerican.com | MIDAMERICAN ENERGY RESPONDED TO A GAS LEAK CALL AT 15 NORTH 12TH STREET IN FORT DODGE, IOWA AT 16:53 ON JANUARY 21, 2024. INITIAL INVESTIGATION DID NOT FIND THE SOURCE OF THE LEAK AND BARHOLING AND INTERIOR INVESTIGATIONS IN THE AREA CONTINUED FOR THE NEXT 6 HOURS WITH NO PINPOINTED SOURCE. THEY MAIN WAS EXPOSED AND CREWS CONTINUED TO MONITOR AND CHECK GAS LEVELS IN AND AROUND THE BUILDINGS IN THE AREA. THE LOCATION OF THE EXPLOSION DID NOT HAVE A GAS READING THE NIGHT OF THE 21ST. WHILE CONTINUING TO INVESTIGATE FOR THE LEAK ON THE MORNING OF THE 22ND OF JANUARY, NATURAL GAS IN A NEARBY STRIPMALL AT 33 NORTH 12 STREET GAS IGNITED WITH A FLASH FIRE AND THE INTERIOR OF THE MALL WAS DAMAGED BY AN EXPLOSION. THE SOURCE OF THE GAS WAS A LEAK ON A 2" MAIN. THE MAIN WAS WAS ABANDONED IN-PLACE AND A REPLACED BY A BORED IN PLASTIC MAIN. THE GAS THAT EXPLODED IS THOUGHT TO HAVE MIGRATED INTO THE STRIPMALL OVER NIGHT.
2026-06-30 10:38 | NO | NO | NO | 20240015 | 39641 | 2024-02-22 16:13 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2024-01-23 15:54 | CENTRAL | YES | 2024 | 15818 CAMINO DEL SOL | HOUSTON | FORT BEND | TX | 77083 | 29.6932 | -95.6651 | [5 empty] | YES |  |  |  | 2024-01-23 18:04 | 1389745 | 1389887 | NATURAL GAS |  | 39.37 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-23 15:54 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 12 | YES | 10 | 2024-01-23 16:04 |  |  |  | 2024-01-23 16:04 | 2024-01-23 17:18 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1982 | UNKNOWN |  |  |  |  | 1.25 | 2306 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.166 |  | 2306 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 100000 | 101997.3264134623 | 13831 | 14107.250216245970713 | 6547 | 6677.764960289376781 | 0 | 0 |  | 0.6506 | 26 | 29.67058823529411764705882352941176470588 | 0 | 0 | 120404 | 49881.1220071326720831764705882352941176 | 122812.0121782329416116470588235294117647 | 0 | 0 | 38 | 0 | 0 | 38 | 0 | 50 | 50 | 60 | 192.619(A)(1) | 1982-01-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.2 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [7 empty] | YES |  |  | NO | NO | 18” – 36” |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [169 empty] | YES | ELMER SELVERA | SR. COMPLIANCE COORDINATOR | elmer.selvera@centerpointenergy.com | 281-755-2470 | 713-967-7307 | ELMER SELVERA | elmer.selvera@centerpointenergy.com | 281-755-2470 | JAMIE HERDOCIA | DIRECTOR GAS OPERATIONAL STANDARDS | 713-207-4675 | jamie.herdociaaa@centerpointenergy.com | AT 3:54PM CENTERPOINT ENERGY WAS NOTIFIED OF A HOUSEFIRE AT 15818 CAMINO DEL SOL. CENTERPOINT ARRIVED AT 4:04PM. BASED ON SIGNS OF PREVIOUS CONSTRUCTION ACTIVITY IN THE REAR EASEMENT, IT IS BELIEVED THAT IMPROPER CONSTRUCTION PRACTICES BY UNKNOWN/UNIDENTIFIED PARTIES RESULTED IN LOSS OF SUPPORT UNDER THE 1 1/4 INCH POLY MAIN. THIS LOSS OF SUPPORT PLACED STRESS AT A SOCKET FUSION COUPLING ON THE MAIN, ALLOWING GAS TO ESCAPE AND MIGRATE THROUGH THE SOIL INTO STRUCTURE, RESULTING IN FIRE/EXPLOSION BY UNKNOWN/UNDETERMINED IGNITION SOURCE.
2026-06-30 10:38 | NO | YES | NO | 20240016 | 39484 | 2024-02-22 16:38 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2024-01-24 03:19 | CENTRAL | YES | 2024 | 12702 CAMPSITE TRAIL | CYPRESS | HARRIS | TX | 77429 | 29.9598 | -95.6249 |  |  |  | YES | [5 empty] | 2024-01-24 06:40 | 1389765 | 1389940 | NATURAL GAS |  | 57.83 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-24 03:19 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 57.83 | NO | 0 | 2024-01-24 03:19 |  |  |  | 2024-01-24 04:14 | 2024-01-24 05:45 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | 0.113 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 1 |  | CLASS 3 LOCATION | 275000 | 280492.647637021325 | 300 | 305.9919792403869 | 5628 | 5740.409530549658244 | 0 | 0 |  | 0.6506 | 38 | 43.36470588235294117647058823529411764706 | 0 | 0 | 280966 | 116387.2698370407941214117647058823529412 | 286582.4138526937230851764705882352941176 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 50 | 50 | 60 | 192.619(A)(1) | 1974-01-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HEAVY RAIN AND HIGH WINDS, CAUSED LARGE OAK TREE TO UPROOT, CAUSING DAMAGE TO ABOVE GROUND FACILITIES (ELECTRIC AND GAS) THAT RESULTED IN GAS IGNITION. | [119 empty] | YES |  |  | YES |  | YES | [29 empty] | ELMER SELVERA | COMPLIANCE COORDINATOR | elmer.selvera@centerpointenergy.com | 281-755-2470 | 713-967-7307 | ELMER SELVERA | elmer.selvera@centerpointenergy.com | 281-755-2470 | JAMIE HERDOCIA | DIRECTOR GAS OPERATIONAL STANDARDS | 713-207-4675 | jamie.herdocia@centerpointenergy.com | ON THE MORNING OF JANUARY 24, 2024, A WEATHER EVENT WITH HEAVY RAIN AND HIGH WINDS CAUSED LARGE OAK TREE TO UPROOT, FALLING LIMBS DAMAGED RESIDENTIAL ELECTRIC FACILITIES AND ABOVE GROUND METER SET. ESCAPING GAS IGNITED, RESULTING IN HEAVY DAMAGE TO SINGLE FAMILY RESIDENCE.
2026-06-30 10:38 | NO | YES | NO | 20240017 | 39647 | 2024-02-22 16:56 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2024-01-29 19:25 | CENTRAL | YES | 2024 | 502 AVE D | VICTORIA | VICTORIA | TX | 77901 | 28.7962 | -96.9851 | [5 empty] | YES |  |  |  | 2024-01-29 20:49 | 1390282 | 1390441 | NATURAL GAS |  | 93.55 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-29 19:25 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 33.5 | YES | 8 | 2024-01-29 17:09 |  |  |  | 2024-01-29 17:09 | 2024-01-29 19:45 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 82 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2020 | 2020 |  |  |  |  | 2 | ASTM D2513 | DURALINE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 0.5 | [7 empty] | CLASS 3 LOCATION | 175000 | 178495.321223559025 | 7562 | 7713.037823386019126 | 25310 | 25815.52331524730813 | 0 | 0 |  | 0.9446 | 88 | 100.423529411764705882352941176470588235 | 0 | 0 | 207960 | 86176.1362733534502550588235294117647059 | 212124.3058916041169618823529411764705882 | 0 | 0 | 1 | 0 | 2 | 1 | 0 | 50 | 50 | 60 | 192.619(A)(1) | 2020-10-14 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 0.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | YES |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [5 empty] | YES |  |  | NO | NO | MEASURED DEPTH FROM GRADE | 84 | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2451816135 | TEXAS 811 | YES | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | ELMER SELVERA | COMPLIANCE COORDINATOR | elmer.selvera@centerpointenergy.com | 281-755-2470 |  | ELMER SELVERA | elmer.selvera@centerpointenergy.com | 281-755-2470 | JAMIE HERDOCIA | DIRECTOR GAS OPERATIONAL STANDARDS | 713-207-4675 | jamie.herdocia@centerpointenergy.com | ON JANUARY 29, 2024, AROUND 4:40PM G3 UNDERGROUND (SUB OF ONYX CONSULTING WORKING FOR SPARKLIGHT), WAS PULLING BACK FIBER CONDUIT WITH A DIRECTIONAL DRILLING RIG AND DAMAGED 2" POLY MAIN WITH A MAKESHIFT ATTACHMENT THAT EXPANDS THE BORE HOLE THEY ORIGINALLY BORED. THE MAIN THAT WAS DAMAGED, WAS NOT POTHOLED PRIOR TO CONTRACTOR BORING. THE MAIN WAS PROPERLY AND CORRECTLY MARKED AND FLAGGED BY USIC. CENTERPOINT ENERGY'S SERVICE TECHNICIAN ARRIVED AT 5:10PM AND BEGAN COORDINATING WITH OTHER PARTIES ON SITE AND PERFORMING LEAK INVESTIGATION ACTIVITIES. AT APPROXIMATELY 7:25PM, WHILE THE INVESTIGATION ACTIVITIES WERE TAKING PLACE, AN IGNITION OF GAS OCCURRED AT 502 AVE. D DUE TO UNDETECTED GAS MIGRATING FROM THE DAMAGED MAIN.
2026-06-30 10:38 | NO | YES | YES | 20240018 | 39251 | 2024-02-23 18:54 | ORIGINAL | 12582 | ATMOS ENERGY CORPORATION - MISSISSIPPI | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2024-01-24 08:36 | CENTRAL | NO | 2024 | 185 BRISTOL BLVD. | JACKSON | HINDS | MS | 39204 | 32.288 | -90.2444 | [5 empty] | YES |  |  |  | 2024-01-24 11:43 | 1389804 | 1389988 | NATURAL GAS |  | 15 | 0.15 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2024-01-24 08:36 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 15 | NO | 2 | 2024-01-24 11:19 |  |  |  | 2024-01-24 09:06 | 2024-01-24 11:19 | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | NTSB INVESTIGATION ONGOING | 30 | YES | NO | [11 empty] | INVESTOR OWNED |  | OTHER | NTSB INVESTIGATION ONGOING | UNKNOWN | UNKNOWN | [7 empty] | OTHER | NTSB INVESTIGATION ONGOING. | [9 empty] | OTHER | [8 empty] | NTSB INVESTIGATION ONGOING. | CLASS 3 LOCATION | 200000 | 203994.6528269246 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.8657 | 43 | 49.07058823529411764705882352941176470588 | 0 | 0 | 200043 | 82873.9664358501529411764705882352941176 | 204043.7234151598941176470588235294117647 | 0 | 0 | 13 | 1 | 0 | 13 | 0 | 36 | 36 | 40 | 192.619(A)(3) | 1970-12-16 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 12 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | DEAN G MORRIS | MANAGER OF COMPLIANCE | dean.morris@atmosenergy.com | 6018425875 | 6013601489 | DEAN MORRIS | dean.morris@atmosenergy.com | 6018425875 | JAMES MCKENZIE | VICE PRESIDENT - TECHNICAL SERVICES | 6016249408 | james.mckenzie@atmosenergy.com | THE INVESTIGATION, TO WHICH THE MISSISSIPPI PUBLIC SERVICE COMMISSION AND PHMSA ARE PARTIES, IS ONGOING UNDER THE DIRECTION OF THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB). ACCORDINGLY, THE RESPONSES IN THE REPORT WILL BE SUPPLEMENTED WHEN THE INFORMATION IS PERMITTED TO BE RELEASED BY THE NTSB.
2026-06-30 10:38 | NO | YES | NO | 20240019 | 39252 | 2024-02-23 19:16 | ORIGINAL | 12582 | ATMOS ENERGY CORPORATION - MISSISSIPPI | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2024-01-27 04:53 | CENTRAL | NO | 2024 | 1146 SHALIMAR DRIVE | JACKSON | HINDS | MS | 39204 | 32.2793 | -90.2391 | [5 empty] | YES |  |  |  | 2024-01-27 07:45 | 1390069 | 1390197 | NATURAL GAS |  | 60 | 0.035 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-27 04:34 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 60 | YES | 2 | 2024-01-27 07:28 |  |  |  | 2024-01-27 05:35 | 2024-01-27 07:28 | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | NTSB INVESTIGATION ONGOING | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | NTSB INVESTIGATION ONGOING | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | NTSB INVESTIGATION ONGOING. | CLASS 3 LOCATION | 220000 | 224394.11810961706 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.8657 | 172 | 196.282352941176470588235294117647058824 | 0 | 0 | 220172 | 91277.2607264939917647058823529411764706 | 224590.4004625582364705882352941176470588 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 36 | 36 | 40 | 192.619(A)(3) | 1970-12-16 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 6 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | DEAN MORRIS | MANAGER OF COMPLIANCE | dean.morris@atmosenergy.com | 6018425875 | 6013601489 | DEAN MORRIS | dean.morris@atmosenergy.com | 6018425875 | JAMES MCKENZIE | VICE PRESIDENT - TECHNICAL SERVICES | 6016249408 | james.mckenzie@atmosenergy.com | THE INVESTIGATION, TO WHICH THE MISSISSIPPI PUBLIC SERVICE COMMISSION AND PHMSA ARE PARTIES, IS ONGOING UNDER THE DIRECTION OF THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB). ACCORDINGLY, THE RESPONSES IN THIS REPORT WILL BE SUPPLEMENTED WHEN THE INFORMATION IS PERMITTED TO BE RELEASED BY THE NTSB. THE HOUSE INVOLVED WAS VACANT.
2026-06-30 10:38 | NO | YES | NO | 20240020 | 39372 | 2024-03-26 13:28 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2024-02-29 10:08 | EASTERN | NO | 2024 | BRUNSWICK FOREST PARKWAY | LELAND | BRUNSWICK | NC | 28451 | 34.1762 | -78.0392 | [5 empty] | YES |  |  |  | 2024-02-29 11:40 | 1392655 | 1392744 | NATURAL GAS |  | 386.36 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-02-29 10:08 | ALLOWED TO BURN OUT |  | 386.36 | NO | 0 | 2024-02-29 10:08 | YES | OPERATOR | 2024-02-29 10:18 | 2024-02-29 10:08 | 2024-02-29 10:08 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2023 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 189744 | 193533.807029959906512 | 37600 | 38350.9947314618248 | 0 | 0 |  | 3 | 1159 | 1322.623529411764705882352941176470588235 | 0 | 0 | 228503 | 95236.2546817831152630588235294117647059 | 233207.4252908334960178823529411764705882 | 0 | 0 | 436 | 1 | 0 | 436 | 0 | 58 | 60 | 60 | 192.619(A)(1) | 2008-09-14 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AN INCIDENT IN THE FIELD OCCURRED AND WAS CALLED IN BY ONSITE PERSONNEL. | [12 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) |  |  |  |  | YES | YES | YES |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [5 empty] | NO | NO | > 36” |  | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | C240540966 |  | YES | FACILITY OWNER | YES | YES | 22 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | ON FEBRUARY 29, 2024, AT 10:08AM IN LELAND, NC A PIEDMONT NATURAL GAS COMPANY CREW STRUCK A 4 INCH PLASTIC NATURAL GAS MAIN WHEN OPERATING MECHANICAL EXCAVATION EQUIPMENT. THE EQUIPMENT MADE CONTACT WITH A 2" TAPPING TEE ON TOP OF A 4" MAIN, BREAKING THE TEE OFF THE MAIN. THE ESCAPING GAS BUILT UP A STATIC CHARGE ON THE EXPOSED PLASTIC PIPE THAT IMMEDIATELY CAUSED AN IGNITION OF THE GAS. THE EQUIPMENT OPERATOR RECEIVED MINOR BURNS AND WAS TREATED ON SITE AND SUBSEQUENTLY TRANSPORTED TO A MEDICAL FACILITY, BUT NOT ADMITTED. THE EQUIPMENT OPERATOR FAILED TO MAINTAIN ADEQUATE EXCAVATION CLEARANCE FROM THE 4" PLASTIC PIPE WHILE EXCAVATING STRIKING THE PIPE WHILE DIGGING. THE INCIDENT RESULTED IN 436 CUSTOMER OUTAGES ON FEBRUARY 29TH. ALL CUSTOMERS WERE BACK IN SERVICE ON MARCH 1ST.
2026-06-30 10:38 | NO | YES | NO | 20240022 | 39723 | 2024-04-15 12:08 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | 3600 MIDTOWN DR. | TAMPA | FL | 33607 | 2024-03-14 08:25 | EASTERN | YES | 2024 | 6812 INDIANTOWN ROAD | JUPITER | PALM BEACH | FL | 33458 | 26.9337 | -80.1401 | [6 empty] | YES |  |  | 2024-03-14 17:45 | 1393899 | 1393961 | NATURAL GAS |  | 533.2 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-03-14 08:25 |  |  |  | 2024-03-14 09:04 | 2024-03-14 09:04 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 180 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2006 | 2006 |  |  |  |  | 4 | ASTM D2513 | DRIXELPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 219195 | 223573.039631988688485 | 0 | 0 | 25760 | 26274.51128410788848 | SURVEY AND ENVIRONMENTAL PERMITTING OF NEW PIPELINE. | 10 | 5332 | 6084.752941176470588235294117647058823529 | 0 | 0 | 250287 | 106408.6379982330769508823529411764705882 | 255932.3038572730475532352941176470588235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 45 | 60 | 192.619(A)(2) | 2006-08-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 100 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXCAVATION DAMAGE OF PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | INTERSTATE HIGHWAY | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | AUGER | ROAD WORK | YES | 047404343 |  | NO | FACILITY OWNER | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | IYANNA JONES | COMPLIANCE ANALYST | iejones@tecoeenergy.com | 407-420-6617 |  | TRACY YALLEDY | atyalledy@tecoenergy.com | 1-561-741-4704 | RUSSELL HARRIS | MANAGER OF PIPELINE SAFETY COMPLIANCE | 407-466-7137 | rharris@tecoenergy.com | ON MARCH 14, 2024, AT APPROXIMATELY 8:25 AM, A 4-INCH PE HIGH PRIORITY GAS MAIN WAS DAMAGED BY A THIRD-PARTY CONTRACTOR ATTEMPTING TO DRIVE A STEEL PILE INTO THE GROUND, SUBSEQUENTLY STRIKING THE GAS FACILITY. THE DAMAGE WAS MADE SAFE AT APPROXIMATELY 06:27PM ON 03/14/2024 BY CONSTRUCTING A TEMPORARY BYPASS. A PERMANENT REPLACEMENT OF THE DAMAGED PIPELINE WAS COMPLETED ON 03/29/2024 AND THE BYPASS WAS REMOVED COMPLETING THE REPLACEMENT PROJECT. PGS RECEIVED A LOCATE TICKET, PERFORMED A LOCATE WITH MARKS ON THE GROUND AND PROVIDED A POSITIVE RESPONSE ON FEBRUARY 20TH. IN THE RESPONSE, THE CONTRACTOR WAS REQUESTED TO CONTACT PGS PRIOR TO INITIATION OF EXCAVATION, AND NO CONTACT WAS RECEIVED TO COORDINATE AND DISCUSS CONTRACTORS' INSTALLATION.
2026-06-30 10:38 | NO | YES | NO | 20240023 | 39465 | 2024-04-19 12:34 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2024-03-22 16:55 | EASTERN | YES | 2024 | 990 E. WATER ST. | PROSPECT | MARION | OH | 43342 | 40.4527 | -83.1787 | [6 empty] | YES |  |  | 2024-03-22 17:35 | 1394537 | 1394682 | NATURAL GAS |  | 38 | 0.072 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-03-20 15:02 | NO |  |  | 2024-03-20 15:02 | 2024-03-22 16:55 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 38 | NO | YES |  |  | YES | CASED | [7 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | LEAK |  |  | OTHER | UNKNOWN, PIPE NOT EXCAVATED | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 141982 | 144817.843988362042786 | 14972 | 15271.039710623575556 | 0 | 0 |  | 4.35 | 165 | 188.294117647058823529411764705882352941 | 0 | 0 | 157119 | 65158.9924788033009942352941176470588235 | 160277.1778166326771655294117647058823529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 50 | 192.619(A)(4) | 1995-01-27 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VOLUME RELEASED WAS NOT ENOUGH TO TRIGGER ANY ACTION BY CONTROLLERS. PRESSURE CONTROL WAS NOT A FACTOR IN THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | ABANDON PIPE IN PLACE FILLED CARRIER PIPE WITH CONCRETE PER RAIL ROAD | [5 empty] | YES | UNKNOWN |  |  |  |  | YES | UNKOWN | YES | NO |  | NO | NO | [8 empty] | N/A Bare/Ineffectively Coated Pipe | NONE |  | NO | [19 empty] | 2022-03-25 | NO | [227 empty] | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | rrsmith@nisource.com | 1-614-460-5491 |  | ROB R. SMITH | rrsmith@nisource.com | 1-614-460-5491 | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | 1-614-460-5491 | rrsmith@nisource.com | WHILE CONDUCTING A LEAKAGE SURVEY, A GRADE ONE HAZARDOUS LEAK WAS DETECTED. COLUMBIA DISCOVERED A BARE STEEL LINE LEAKING WITHIN THE CONFINES OF A STEEL CASING UNDER A RAILWAY. THE ENDS OF THE STEEL CASING WERE EXCAVATED AND THE LEAK MIGRATION PATH WAS BROKEN AND NO LONGER PRESENTED A HAZARD. COLUMBIA CREWS COORDINATED THE REPAIR WITH THE RAILROAD OPERATOR WHILE CONTINUOUSLY MONITORING THE LEAK UNTIL THE LINE WAS REPLACED. THE COST OF REPAIR TRIGGERED THE REPORTING CRITERIA AS WRITTEN IN 49 CFR PART 191.3. THE PIPE WAS REPLACED SUCCESSFULLY AND THE LEAK WAS MADE SAFE ON 03-29-24 AT 19:15 HOURS. PLEASE CLOSE YOUR FILE ON THIS EVENT.
2026-06-30 10:38 | NO | YES | NO | 20240024 | 41070 | 2024-04-19 15:48 | SUPPLEMENTAL FINAL | 603 | SUMMIT UTILITIES INC. | 10825 E GEDDES AVE SUITE 410 | CENTENNIAL | CO | 80112 | 2024-04-03 16:05 | CENTRAL | YES | 2024 | RE-277 (HIGHWAY 28) | ROVER | YELL | AR | 72860 | 34.9452 | -93.415 |  | YES | [8 empty] | NRC NOTIFICATION REQUIRED BUT NOT MADE | See narrative. Section H | NATURAL GAS |  | 0 | 0.71 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-04-03 09:09 | YES | OPERATOR | 2024-04-03 15:00 | 2024-04-03 08:30 | 2024-04-03 09:30 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | OTHER | SEE NARRATIVE SECTION H | 30 | NO | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | DISTRIBUTION FACILITIES MAINS, SVC LINES, REGS, METERS | UNKNOWN | UNKNOWN | [7 empty] | OTHER | STEEL, PLASTIC | [9 empty] | OTHER | [8 empty] | RELEASE OF DIESEL FUEL DUE TO ENERGY TRANSFER PIGGING OPERATION, INTO(RE)-277 SUMMIT DISTRIBUTION SYSTEM | CLASS 1 LOCATION | 47345 | 48290.634190453725935 | 1670903 | 1704276.386962333974569 | 57807 | 58961.594479830151761 | 91204 | 93025.641582134156092 | UPDATED AS OF 6-24-2025 | 7.97 | 0 | 0 | 6 | 6.84705882352941176470588235294117647059 | 1867265 | 773368.2526520779565951176470588235294118 | 1904561.10427357553776876470588235294118 | 7 | 0 | 22 | 0 | 0 | 24 | 7 | 35 | 35 | 60 | 192.619(A)(2) | 2022-01-10 | PRESSURE DID NOT EXCEED MAOP | WICK |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | SEE NARRATIVE. SECTION H | [47 empty] | RON WOODS | MANAGER OF OPERATIONS-NORTH REGION | rwoods@summitutilities.com | 870-219-8765 |  | RON WOODS | rwoods@summitutilities.com | 870-219-8765 | CARLA RICHARDSON | MANAGER OF PIPELINE SAFETY | 417-527-7719 | crichardson@summitnaturalgas.com | ON 4-03-2024, SUA RECEIVED A LOW-PRESSURE CUSTOMER COMPLAINT FROM A RURAL EXTENSION (RE)-277 NEAR ROVER, ARKANSAS. A TECHNICIAN WAS DISPATCHED IMMEDIATELY, UPON INVESTIGATION FOUND A FOREIGN LIQUID IN THE CUSTOMER'S SERVICE LINE AND HOUSE PIPING. THE SYSTEM HAS 31 TOTAL CUSTOMERS (22 ACTIVE RESIDENTIAL, 7 COMMERCIAL AND 2 INACTIVE RESIDENTIAL). IT WAS DETERMINED THAT ENERGY TRANSFER, THE PIPELINE SUPPLIER TO THE LDC, HAD BEEN PERFORMING AN INLINE INSPECTION OF THE PIPELINE THAT SERVES (RE)-277. PART OF THAT PROCESS INCLUDED INJECTING SEVERAL THOUSAND GALLONS OF DIESEL FUEL BOTH IN FRONT OF AND BEHIND THE INSPECTION TOOL. ENERGY TRANSFER STATED THAT THEY HAD FAILED TO CLOSE OFF A VALVE TO THE LDC STATION AND HAD INADVERTENTLY PUSHED DIESEL FUEL OUT OF THEIR SYSTEM INTO THE SUA DISTRIBUTION SYSTEM. ADDITIONAL DETAILS OF ENERGY TRANSFER'S PROCESS OR GAS HANDLING PLAN ARE NOT AVAILABLE FOR INCLUSION IN THIS REPORT. 6-24-2025 SUPPLEMENTAL REPORT: UPDATED PART D. ALL IMPACTED FACILITIES WERE REPAIRED OR REPLACED PRIOR TO BEING RETURNED TO SERVICE
2026-06-30 10:38 | NO | YES | YES | 20240025 | 41215 | 2024-04-19 18:01 | SUPPLEMENTAL | 12876 | DOMINION ENERGY UTAH/WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2024-03-20 05:52 | MOUNTAIN | YES | 2024 | 67 N 370 E | AMERICAN FORK | UTAH | UT | 84003 | 40.3783 | -111.7891 |  |  |  | YES | [5 empty] | 2024-03-20 07:42 | 1394296 | 1394442 | NATURAL GAS |  | 0 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2024-03-20 05:52 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 3 | 2024-03-20 06:06 |  |  |  | 2024-03-20 06:22 | 2024-03-20 06:22 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | CUSTOMER OWNED FUEL LINE | UNKNOWN | UNKNOWN | [7 empty] | STEEL |  | OTHER | 1/2" BLACK STEEL PIPE | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | UNDER INVESTIGATION | [5 empty] | CLASS 3 LOCATION | 1000000 | 1019973.264134623 | 1500 | 1529.9598962019345 | 10000 | 10199.73264134623 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1011500 | 418932.9637493121485 | 1031702.9566721711645 | 0 | 0 | 2 | 0 | 1 | 4 | 0 | 0.25 | 0.25 | 0.25 | 192.619(A)(2) | 1996-06-11 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BEING ON A RESIDENTIAL CUSTOMER OWNED FUEL LINE. | [12 empty] | YES | 1 | 0 | YES | 1 | 0 | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | STEVE BURSETT | SUPERVISOR GAS OPERATIONS | steve.bursett@dominionenergy.com | 801-548-7520 |  | JUSTIN WITHERS | justin.withers@dominionenergy.com | 801-209-0814 | RYAN JAMISON | MANAGER GAS OPERATIONS | 801-574-0111 | ryan.jamison@dominionenergy.com | AT APPROXIMATELY 6:00 AM, ON MARCH 20, 2024, QUESTAR GAS COMPANY D/B/A DOMINION ENERGY UTAH (DEU) RECEIVED A CALL FROM 911 REPORTING A RESIDENTIAL EXPLOSION AT 67 NORTH 370 EAST, AMERICAN FORK, UTAH. DEU RESPONDED TO THE SCENE AND OBSERVED AN ACTIVE FIRE IN THE DUPLEX STRUCTURE. AMERICAN FORK FIRE DEPARTMENT SHUT OFF THE FLOW OF NATURAL GAS. IT WAS REPORTED THAT THE RESIDENT OF 69 NORTH 370 EAST WAS FOUND DECEASED. THE STRUCTURE AT 67 AND 69 NORTH 370 EAST WERE DESTROYED. THE HOME AT 53 NORTH 370 EAST SUSTAINED STRUCTURAL DAMAGE. ONCE THE SCENE WAS SECURE, DEU PERFORMED PRESSURE TESTS ON THE MAIN AND SERVICE LINES ASSOCIATED WITH 67 AND 69 NORTH 370 EAST. 67 AND 69 NORTH 370 EAST WERE SERVED BY A SINGLE SERVICE LINE AND DUAL METER SETS. DEU TESTED THE MAIN AND SERVICE LINES AT OPERATING PRESSURE OF 45 PSI FOR 15 MINUTES. EACH HELD PRESSURE, INDICATING NO LEAKS ON THE MAIN AND SERVICE LINES. THESE PRESSURE TESTS WERE WITNESSED BY A REPRESENTATIVE OF UTAH PIPELINE SAFETY. DEU ALSO EXECUTED ITS LEAK SCREEN PROCEDURE, SCREENING FOR LEAKS ON THE OTHER MAIN AND SERVICE LINES IN THE NEIGHBORHOOD AND FOUND NO LEAKS. DEU'S CAUSE AND ORIGIN INVESTIGATION IS ONGOING. AT THE FIRE DEPARTMENTS DIRECTION, DEU REMOVED THE METER SETS AND RISER FOR 67 AND 69 NORTH 370 EAST AND SURRENDERED THEM TO THE FIRE DEPARTMENTS CUSTODY ON THE DAY OF THE INCIDENT . TESTING OF OUR DEU EQUIPMENT WAS COMPLETED ON 7/29/2024. INITIAL NRC INCIDENT REPORT #1394296, WAS MADE ON 03/20/2024 AT 7:42AM MT. 48-HOUR UPDATE NRC #1394442, WAS MADE ON 03/21/2024 AT 7:30PM MT.
2026-06-30 10:38 | NO | YES | NO | 20240026 | 39479 | 2024-04-24 14:01 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2024-03-25 12:37 | EASTERN | YES | 2024 | 2661 CAMPBELLTON ROAD SW | ATANTA | FULTON | GA | 30311 | 33.7024 | -84.4761 | [5 empty] | YES |  |  |  | 2024-03-25 13:30 | 1394734 | 1394916 | NATURAL GAS |  | 4352.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-03-25 12:37 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1614 | YES | 20 | 2024-03-25 10:11 |  |  |  | 2024-03-25 10:33 | 2024-03-25 12:37 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 96 | NO | YES |  |  |  |  | YES | UNCASED, BORED/DRILLED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2011 | UNKNOWN |  |  |  |  | 6 | ASTM D2513 | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 4.5 | 4.5 | [7 empty] | CLASS 3 LOCATION | 300000 | 305991.9792403869 | 80079 | 81678.439018636475217 | 108314 | 110477.384131477555622 | 0 | 0 |  | 1.45 | 6311 | 7201.964705882352941176470588235294117647 | 0 | 0 | 494704 | 208143.2506815796422564117647058823529412 | 505349.7670963832837801764705882352941176 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 39 | 39 | 45 | 192.619(A)(2) | 2011-04-16 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 13 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 13 | 0 | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 240112001811 |  | NO | CONTRACT LOCATOR | YES | YES | 13 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | RALPH MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | MANAGER COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A THIRD-PARTY PARTY EXCAVATOR (NEXTIER INFRASTRUCTURE SOLUTIONS) STRUCK AND DAMAGED AN ATLANTA GAS LIGHT COMPANY (AGLC) 6-INCH PLASTIC GAS MAIN WHILE DIRECTIONALLY BORING TO INSTALL TELECOMMUNICATION FIBER MAIN NEAR 2661 CAMPBELLTON ROAD SW, ATLANTA. ESCAPING GAS FROM THE DAMAGE MIGRATED TO A NEARBY STRUCTURE AT 2683 CAMPBELLTON ROAD SW, ATLANTA (PO FREDDIE'S BBQ RESTAURANT) AND WAS IGNITED BY AN UNKNOWN IGNITION SOURCE WHERE A SUBSEQUENT EXPLOSION AND FIRE OCCURRED AT THE RESTAURANT RESULTING IN SIGNIFICANT PROPERTY DAMAGE. AT LEAST ONE VEHICLE WAS DAMAGED BY FALLING DEBRIS FROM THE EXPLOSION. UPON ARRIVAL, AGLC PERSONNEL WORKED WITH EMERGENCY RESPONDERS TO SECURE THE AREA AND MONITOR THE SURROUNDING AREA FOR GAS. GAS WAS SHUT-OFF TO THE DAMAGED AREA AT 14:00 HOURS BY PERFORMING FOUR (4) SQUEEZE-OFF OPERATIONS. A LARGE PROJECT MARKING ' UTILITY FACILITY LOCATING AGREEMENT WAS SIGNED ON MAY 5, 2023, WITH NEXTIER INFRASTRUCTURE SOLUTIONS (EXCAVATOR) TO LOCATE THE AREA AS A LARGE PROJECT EXCAVATION. AS TO THE LOCATION OF THIS INCIDENT, THE LARGE PROJECT MARKING AGREEMENT STATED 'CONTINUE LOCATES EAST ON THE NORTH SIDE OF CAMPBELLTON ROAD SW TO THE NORTHWEST CORNER OF CAMPBELLTON ROAD SW AND DODSON DRIVE SW. LOCATE THIS CORNER 50 FEET IN ALL DIRECTIONS. THEN CONTINUE EAST ON THE NORTH SIDE OF CAMPBELLTON ROAD SW TO THE NORTHWEST CORNER OF WILLIS MILL ROAD AND CAMPBELLTON ROAD SW AND LOCATE IT 50 FEET IN ALL DIRECTIONS'. AGLC FACILITIES WERE LAST MARKED BY STAKE CENTER LOCATING TO SATISFY THIS REQUEST ON MARCH 13, 2024. INVESTIGATION OF THE SITE REVEALED THAT THE LOCATE MARKS WERE ACCURATE AT THE POINT OF DAMAGE, HOWEVER, BECAUSE THE EXCAVATOR DID NOT VERIFY THE LOCATION AND DEPTH OF AGLC FACILITIES BY POT HOLING AND INSTEAD BLINDLY CROSSED THE MARKS ON THE GROUND, THE GAS MAIN WAS DAMAGED. AGLC INITIALLY NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) UNDER NRC REPORT NUMBER 1394734. ADDITIONAL NRC REPORT NUMBER 1394916 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2026-06-30 10:38 | NO | YES | NO | 20240027 | 39503 | 2024-04-30 19:32 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2024-04-15 11:22 | MOUNTAIN | NO | 2024 | 27TH AVE & NORTHERN AVE | PHOENIX | MARICOPA | AZ | 85051 | 33.5533 | -112.1172 | YES | [8 empty] | 2024-04-15 11:40 | 1396485 | 1396605 | NATURAL GAS |  | 11773.13 | 0.29 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 555 | 2024-04-15 10:47 |  |  |  | 2024-04-15 10:47 | 2024-04-15 11:22 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2019 | UNKNOWN | [7 empty] | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.375 | [6 empty] | OTHER | [8 empty] | DISTRICT REGULATOR STATION 2-INCH BYPASS BROKEN WHEN STRUCK BY THIRD-PARTY VEHICLE. | CLASS 3 LOCATION | 20000 | 20399.46528269246 | 250000 | 254993.31603365575 | 21512 | 21941.664858064009976 | 0 | 0 |  | 1.1414 | 13438 | 15335.1294117647058823529411764705882353 | 0 | 0 | 304950 | 133224.9628556495136268235294117647058824 | 312669.5755861769258583529411764705882353 | 0 | 0 | 0 | 3 | 0 | 0 | 4 | 388 | 388 | 400 | 192.619(A)(4) | 1987-05-14 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.2 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | REG STATION WAS HIT BY A 3RD PARTY VEHICLE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | SMALL TRUCK | ROADWAY | 10 | YES | YES | [141 empty] | SHAWN L. BRINK | ADMINISTRATOR DIVISION COMPLIANCE | shawn.brink@swgas.com | 6027230987 | 6024845322 | SHAWN L. BRINK | shawn.brink@swgas.com | 6027230987 | ROBERT MCGEE | DIRECTOR CENTRAL SUPPORT | 6024845367 | robert.mcgee@swgas.com | ACC- PL2024-0058 ON APRIL 15, 2024 AT 10:35 SOUTHWEST GAS (SWG) DISPATCH WAS NOTIFIED BY THE PHOENIX FIRE DEPARTMENT OF A VEHICLE THAT HAD COLLIDED WITH REGULATOR STATION (DR #423886) AT THE NORTHWEST CORNER OF 27TH AVENUE AND NORTHERN AVENUE IN PHOENIX, ARIZONA. CONSTRUCTION CREWS RESPONDED AND DISCOVERED A MULTIPLE-VEHICLE ACCIDENT HAD CAUSED ONE VEHICLE TO COLLIDE WITH THE REGULATOR STATION AND SHEARED OFF THE ABOVE-GROUND 2-INCH BYPASS PIPE FROM THE REGULATOR STATION RESULTING IN A RELEASE OF GAS. GAS FLOW WAS CONTROLLED UTILIZING THREE VALVES TO ISOLATE THE DAMAGED REGULATOR STATION AND GAS OFF AT 12:22. APPROXIMATELY 555 INDIVIDUALS WERE EVACUATED FROM A SCHOOL AS A PRECAUTION BY THE FIRE DEPARTMENT. THREE PEOPLE WERE TRANSPORTED TO THE HOSPITAL DUE TO MINOR INJURIES SUSTAINED IN THE VEHICLE ACCIDENTS. THERE WERE NO OUTAGES, OR FATALITIES DUE TO THE GAS INCIDENT. THE DISTRICT REGULATOR STATION WAS TEMPORARILY TAKEN OUT OF SERVICE FOR REPLACEMENT / RELOCATION AT A LATER DATE. ON APRIL 15, 2024, THE ARIZONA CORPORATION COMMISSION (ACC) WAS TELEPHONICALLY NOTIFIED AT 11:27 OF THE INCIDENT INVOLVING THE EVACUATION OF THE SCHOOL AND THAT ESTIMATED INCIDENT COSTS WOULD EXCEED $139,700. ON APRIL 15, 2024, PHMSA/NRC WAS TELEPHONICALLY NOTIFIED AT 11:40 THAT INCIDENT COSTS WOULD EXCEED $139,700 AND WAS ASSIGNED NRC REPORT #1396485. ON APRIL 16, 2024, A FOLLOW-UP PHMSA/NRC WAS TELEPHONICALLY UPDATED AT 14:11 AND WAS ASSIGNED NRC REPORT #1396605.
2026-06-30 10:38 | NO | YES | NO | 20240028 | 40536 | 2024-05-03 17:04 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | 3600 MIDTOWN DR. | TAMPA | FL | 33607 | 2024-04-05 13:07 | EASTERN | YES | 2024 | 2190 NW NORTH RIVER DRIVE | MIAMI | DADE | FL | 33125 | 25.7896 | -80.2309 | [7 empty] | YES | PRESSURE WAS REDUCED, GAS FLOW WAS NOT INTERRUPTED & SERVICE WAS CONTINUOUSLY PROVIDED TO CUSTOMERS. | 2024-04-05 17:18 | 1395698 | 1395827 | NATURAL GAS |  | 117840 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2024-04-05 13:07 | YES | OPERATOR | 2024-04-05 16:55 | 2024-04-05 13:15 | 2024-04-05 13:15 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 264 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1964 | UNKNOWN |  |  |  |  | 10 | API 5L | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 4063808 | 4144975.510576394024384 | 104000 | 106077.219470000792 | 0 | 0 | 0 | 0.77 | 90737 | 103546.9294117647058823529411764705882353 | 0 | 0 | 4258545 | 1810513.11070498582997082352941176470588 | 4354599.65945815952226635294117647058824 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 65 | 100 | 192.619(A)(2) | 2016-01-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 100 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXCAVATION DAMAGE OF PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [5 empty] | NO | NO | > 36” |  | CONTRACTOR | UNKNOWN/OTHER | SITE DEVELOPMENT | YES | 088406955 |  | NO | FACILITY OWNER | NO | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | IYANNA JONES | COMPLIANCE ANALYST | iejones@tecoenergy.com | [5 empty] | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | 407-466-7137 | rharris@tecoenergy.com | ON APRIL 5, 2024, AT APPROXIMATELY 13:07 PM, A 10-INCH STEEL HIGH PRIORITY GAS MAIN WAS DAMAGED BY A THIRD-PARTY CONTRACTOR ATTEMPTING TO DRIVE A STEEL SHEET PILE INTO THE GROUND, SUBSEQUENTLY STRIKING THE GAS FACILITY. A LOCATE TICKET FROM THE PRIMARY CONTRACTOR RECEIVED A POSITIVE RESPONSE FROM PGS ON APRIL 2ND - SUNSHINE 811 POSITIVE RESPONSE CODE 3M. WE UNDERSTAND THAT THE PRIMARY CONTRACTOR WHO CONTACTED THE ONE-CALL CENTER, MEMORIALIZED IN TICKET NUMBER 088406955, WAS NOT THE EXCAVATOR WHO PERFORMED THE WORK. ANY SUB-CONTRACTORS PERFORMING WORK SHOULD HAVE CALLED IN THEIR OWN LOCATE REQUEST, OF WHICH NONE WERE FOUND FOR THIS EXCAVATION WORK. PRELIMINARY INVESTIGATION DID NOT FIND WHERE THE PRIMARY CONTRACTOR CONTACTED PGS PRIOR TO EXCAVATION. ADDITIONALLY, A VERTICAL PIPELINE MARKER WAS PRESENT AND VISIBLE TO THE EXCAVATOR AT THE TIME OF THE INCIDENT AT THE EXCAVATION SITE. THE DAMAGE WAS MADE SAFE AT APPROXIMATELY 04:24AM ON 04/15/2024 BY CONSTRUCTING A PERMANENT OFFSET. ALL PERMANENT REPAIRS AND RESTORATION ACTIVITIES HAVE BEEN COMPLETED. FINAL ESTIMATED COSTS HAVE BEEN UPDATED IN THIS FINAL REPORT.
2026-06-30 10:38 | NO | YES | NO | 20240029 | 39524 | 2024-05-05 11:08 | SUPPLEMENTAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2024-03-30 01:19 | EASTERN | YES | 2024 | 114 CLIFF STREET | PATERSON | PASSAIC | NJ | 07501 | 40.9258 | -74.1789 | [5 empty] | YES |  |  |  | 2024-04-09 10:59 | 1395960 | 1396116 | NATURAL GAS |  | 55 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-03-30 01:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 49 | NO | 10 | 2024-03-30 01:19 |  |  |  | 2024-03-30 01:36 | 2024-04-09 10:15 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2005 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | OTHER | [8 empty] | VEHICLE STRUCK THE METER SET CAUSING IT AND THE VALVE TO BE COMPLETELY TORN OFF THE SWEEP. | CLASS 4 LOCATION | 150000 | 152995.98962019345 | 89 | 90.777620507981447 | 1385 | 1412.662970826452855 | 0 | 0 |  | 18.588 | 1022 | 1166.282352941176470588235294117647058824 | 0 | 0 | 152496 | 63685.8467137551244507058823529411764706 | 155665.7125644690607725882352941176470588 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 15 | 15 | 15 | 192.619(A)(2) | 2005-08-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | NO | UNKNOWN | PASSENGER CAR | ROADWAY | 25 | NO | [118 empty] | YES | [23 empty] | HENRY VARUM | PRINCIPAL REGULATORY SPECIALIST | henry.varum@pseg.com | 7323433421 |  | HENRY VARUM | henry.varum@pseg.com | 7323433421 | CHRIS LAROSSA | DISTRICT MANAGER REGULATORY POLICY PROCEDURE | 9738967617 | christopher.larossa@pseg.com | ON SATURDAY, 3/30/3024 AT 01:19 HRS, PSE&G WAS INITIALLY NOTIFIED OF AN SUV THAT STRUCK A METER-SET COMPLETELY SEPARATING IT FROM THE SERVICE SWEEP AT 106 CLIFF ST, PATERSON, WHICH HAS SINCE BEEN UPDATED TO 114 CLIFF STREET. THE DAMAGE TO THE METER-SET, WHICH IS FED BY A 1.25" 15# SERVICE CREATED THE CONDITION OF UNCONTROLLED GAS THAT FED A FIRE ON THE PREMISES. A PSE&G FIRST RESPONDER ARRIVED ON SITE AT 01:36 HRS AND CONFIRMED THE GAS FED FIRE. A PSE&G CREW REPORTED TO THE SCENE AND ONCE THE FIRE DEPARTMENT WAS EXTINGUISHED THE FIRE, RETIRED THE SERVICE TO 114 CLIFF STREET AT THE MAIN AND SHUT GAS OFF AT THE CURB TO 112 AND 106 CLIFF STREET. THE BUILDING THAT WAS STRUCK WAS EVACUATED AND RESIDENTS OF 106 CLIFF STREET THAT WERE INITIALLY EVACUATED WERE ALLOWED BACK INTO THEIR HOMES AT 4:15 AM. THERE WERE NO INJURIES TO BE REPORTED, BUT THE DRIVE AND ONE PASSENGER OF THE SUV WERE TRANSPORTED TO THE HOSPITAL FOR OBSERVATIONS.
2026-06-30 10:38 | NO | NO | NO | 20240031 | 39530 | 2024-05-08 16:11 | ORIGINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2024-04-29 14:42 | MOUNTAIN | YES | 2024 | CHARLES ST AND COLLEGE DR | CHEYENNE | LARAMIE | WY | 82001 | 41.1493 | -104.7611 | [6 empty] | YES |  |  | 2024-05-06 14:30 | 1398244 |  | NATURAL GAS |  | 4782 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-04-29 15:11 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2024-04-29 14:42 | 2024-04-29 15:11 | 2024-05-06 10:56 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2010 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 4 | 12.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 130 | 150 | 192.619(A)(1) | 2010-02-09 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE. CONTROLLER NOT INVOLVED IN RELEASE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | [7 empty] | YES |  |  | NO | NO | 18” – 36” |  | CONTRACTOR | BORING | ELECTRIC | YES | 20241701720 |  | Unknown | FACILITY OWNER | NO | NO |  | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | JACOB KILMURRAY | PIPELINE SAFETY PROFESSIONAL | jake.kilmurray@blackhillscorp.com | 3072865179 |  | MELINDA BARRETT | melinda.barrett@blackhillscorp.com | 6055800515 | JAKE KILMURRAY | PIPELINE SAFETY PROFESSIONAL | 3072865179 | jake.kilmurray@blackhillscorp.com | ON 4/29/24, AN ELECTRIC CONTRACTOR BORED INTO 4 INCH 130 PSI DISTRIBUTION MAIN CAUSING 4 INCH HOLE IN THE PIPE. GAS WAS RELEASED FOR 90 MINUTES BEFORE FLOW OF GAS WAS STOPPED. 2 FEET OF 4 INCH PIPE WAS REPLACED AND MAIN WAS RETURNED TO SERVICE. GAS LOSS CALCULATIONS WERE COMPLETED ON 5/6/24 AND IT WAS DETERMINED THE GAS LOSS EXCEEDED THE REPORTABLE THRESHOLD.
2026-06-30 10:38 | NO | YES | YES | 20240032 | 40252 | 2024-05-10 14:17 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2024-04-15 21:37 | EASTERN | YES | 2024 | 2175 SAVANNAH HIGHWAY | JESUP | WAYNE | GA | 31545 | 31.6309 | -81.8651 | [5 empty] | YES |  |  |  | 2024-04-15 22:23 | 1396518 | 1396669 | NATURAL GAS |  | 51 | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-04-15 17:24 |  |  |  | 2024-04-15 18:15 | 2024-04-15 18:15 | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 34 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 300 | 305.9919792403869 | 629 | 641.563183140677867 | 0 | 0 |  | 1.285 | 66 | 75.31764705882352941176470588235294117647 | 0 | 0 | 995 | 446.105114506288666294117647058823529412 | 1022.872809439888296411764705882352941176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 60 | 192.619(A)(4) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 10 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | PLEASE SEE NARRATIVE IN PART H |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [44 empty] | YES |  |  |  | YES | RALPH MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | 4045843733 | (404) 584-4710 |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND PRM | (630) 388-2316 | lquezad@southernco.com | ON APRIL 15, 2024, AN AGL EMPLOYEE WAS DISPATCHED IN RESPONSE TO AN OUTSIDE ODOR COMPLAINT AT 2175 SAVANNAH HIGHWAY, JESUP, GA ('PREMISE'). ACCORDING TO THE HOMEOWNER, THE EMPLOYEE DETERMINED THAT THE 3/4' PLUG ON THE OUTLET OF THE SERVICE RISER VALVE WAS LEAKING ABOVE GROUND. UPON INFORMATION AND BELIEF, BECAUSE THERE WAS NO METER AT THIS PREMISE, THE EMPLOYEE PLANNED TO ELIMINATE THE ABOVE-GROUND LEAK BY SQUEEZING, CUTTING AND CAPPING THE RISER PIPING BELOW GROUND. AT APPROXIMATELY 17:05-17:10 HOURS, THE HOMEOWNER FOUND THE EMPLOYEE UNRESPONSIVE AND CALLED 911. ACCORDING TO THE CITY OF JESUP FIRE DEPARTMENT, THE EMPLOYEE WAS FOUND LYING ON THE GROUND WITH HIS UPPER BODY IN THE EXCAVATION HOLE THAT HE HAD PRESUMEDLY DUG AND GAS BLOWING IN THE HOLE. WAYNE COUNTY EMS TRANSPORTED THE EMPLOYEE TO WAYNE MEMORIAL HOSPITAL, WHERE THE EMPLOYEE WAS PRONOUNCED DECEASED. AN AUTOPSY LATER DETERMINED THAT DEATH WAS ACCIDENTAL, AND THE CAUSE OF DEATH WAS 'VITIATED ATMOSPHERE OF NATURAL GAS'. AGL WAS CONTACTED BY 911 AT 17:23 HOURS AND DISPATCHED ADDITIONAL AGL PERSONNEL TO THE PREMISES. UPON THEIR ARRIVAL, AGL PERSONNEL FOUND THAT THE EMPLOYEE HAD BEEN TAKEN TO THE HOSPITAL AND A HOLE MEASURING APPROXIMATELY 3 FEET DEEP AND 14 INCHES BY 16 INCHES IN DIAMETER AND GAS BLOWING FROM A CUT TO THE BELOW-GROUND POLYETHYLENE (PE) PORTION (PIGTAIL) OF THE RISER. AGL PERSONNEL EXCAVATED APPROXIMATELY 20 FEET FROM THE BLOWING GAS AND SQUEEZED OFF THE SERVICE LINE TO STOP THE LEAK. THE COMPANY DOES NOT KNOW EXACTLY WHAT OCCURRED AFTER THE EMPLOYEE SQUEEZED AND CUT THE POLYETHYLENE (PE) PORTION (PIGTAIL) OF THE RISER THAT LED TO HIS DEATH, BUT AT SOME POINT, THE SQUEEZERS CAME OFF THE POLYETHYLENE (PE) PIPING (THE EMPLOYEE'S SQUEEZERS WERE FOUND AT THE BOTTOM OF THE EXCAVATION), RESULTING IN BLOWING GAS. IT IS POSSIBLE THAT THE SQUEEZERS ACCIDENTALLY CAME OFF, THOUGH THE COMPANY HAS NO INDICATION THAT THE SQUEEZERS FAILED. IT IS ALSO POSSIBLE THAT THE EMPLOYEE LOOSENED THE SQUEEZERS TO ADJUST THEIR LOCATION. POST-INCIDENT, THE COMPANY DETERMINED THAT THE AMOUNT OF POLYETHYLENE (PE) PIPING BETWEEN THE SQUEEZE POINT AND THE CUT WAS INSUFFICIENT TO INSTALL A STAB FITTING. THE COMPANY DOES NOT KNOW WHETHER THE EMPLOYEE WAS IN THE HOLE WHEN THE GAS STARTED BLOWING OR IF HE CHOSE TO ENTER THE HOLE KNOWING THERE WAS BLOWING GAS. THE SERVICE LINE WAS OPERATING AT A PRESSURE OF 55 PSIG. AGL INITIALLY NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) UNDER NRC REPORT NUMBER 1396518. ADDITIONAL NRC REPORT NUMBER 1396669 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2026-06-30 10:38 | YES | NO | NO | 20240033 | 39661 | 2024-06-07 18:24 | ORIGINAL FINAL | 12876 | ENBRIDGE GAS UTAH/ WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2024-05-05 03:05 | MOUNTAIN | YES | 2024 | 2144 JORDAN WAY | EAGLE MOUNTAIN | UTAH | UT | 84005 | 40.3155 | -112.0028 | [5 empty] | YES |  |  |  | 2024-05-08 15:02 | 1398411 | 1398501 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-05-05 03:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | NO | 6 | 2024-05-05 03:05 |  |  |  | 2024-05-05 04:19 | 2024-05-05 04:19 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2017 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ALUMINUM METER/REGULATOR | [9 empty] | OTHER | [8 empty] | FIRE FIRST EVENT. | CLASS 3 LOCATION | 500000 | 509986.6320673115 | 1950 | 1988.94786506251485 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 501950 | 207892.63584178668605 | 511975.57993237401485 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 43 | 43 | 60 | 192.619(A)(2) | 2017-01-09 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | STEVE BURSETT | SUPERVISOR GAS OPERATIONS | steve.bursett@dominionenergy.com | 801-548-7520 |  | STEVE BURSETT | steve.bursett@dominionenergy.com | 801-548-7520 | RYAN JAMISON | MANAGER GAS OPERATIONS | 801-574-0111 | ryan.jamison@dominionenergy.com | ON MAY 5, 2024 DOMINION ENERGY UTAH (DEU) WAS NOTIFIED OF A HOUSE FIRE AT 2144 JORDAN WAY, EAGLE MOUNTAIN, UTAH. UPON ARRIVAL THE TECHNICIAN NOTED THAT THE METER WAS DAMAGED AND MELTED DUE TO THE EXTREME HEAT OF THE FIRE. DEU CREW PROCEEDED TO EXCAVATE TWO REMOTE BELL HOLES UTILIZING SQUEEZE BARS ON THE 2" PLASTIC MAIN TO ISOLATE THE 3/4" PLASTIC SERVICE FEEDING THE STRUCTURE. AFTER REPAIRS WERE MADE AND FIRE EXTINGUISHED, THE FIRE DEPARTMENT DECLARED THAT STRUCTURE LOCATED AT 2144 JORDAN WAY (ORIGIN OF THE FIRE) ALONG WITH A SECONDARY STRUCTURE LOCATED AT 2150 JORDAN WAY (IGNITED DUE TO PROXIMITY) WERE BOTH COMPLETE LOSSES. AN ADDITIONAL STRUCTURE LOCATED AT 2158 JORDAN WAY WAS SHUT OFF AND EVACUATED AS PRECAUTIONARY. ACCESS TO THE SITE WAS RESTRICTED AT THIS POINT IN ORDER FOR THE FIRE DEPARTMENT TO PERFORM ITS INVESTIGATION. DEU CREW RETIRED ROUGHLY 50' OF 2" PLASTIC MAIN AND PERFORMED A LEAK SCREENING OF THE SURROUNDING AREA WITH NO LEAKS DETECTED. CALCULATION OF GAS LOSS WAS NOT COMPLETED DUE TO NOT HAVING COMPLETE INFORMATION. AN INVESTIGATION IS CURRENTLY ONGOING AND THIS IS BELIEVED TO BE A FIRE FIRST EVENT.
2026-06-30 10:38 | NO | YES | YES | 20240034 | 41576 | 2024-06-21 11:34 | SUPPLEMENTAL FINAL | 4060 | ENBRIDGE GAS OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2024-05-28 14:44 | EASTERN | YES | 2024 | 47 E FEDERAL STREET | YOUNGSTOWN | MAHONING | OH | 44503 | 41.0997 | -80.649 | YES | [8 empty] | 2024-05-28 15:25 | 1400174 | 1400285 | NATURAL GAS |  | 37.1 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 9 | 9 | YES | 2024-05-28 14:44 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 4.2 | YES | 200 | 2024-05-28 14:51 |  |  |  | 2024-05-28 14:58 | 2024-05-28 14:59 | NO | PUBLIC PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | UNKNOWN | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | YES | 1 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | MECHANICAL CUT TO THE SERVICE LINE CAUSED BY POWER TOOL. DIMENSIONS OF THE CUT ARE NOT YET AVAILABLE FOR RELEASE THROUGH THE NTSB PARTY INVESTIGATION. | CLASS 4 LOCATION | 2000000 | 2039946.528269246 | 5000 | 5099.866320673115 | 50000 | 50998.66320673115 | 0 | 0 |  | 1.814 | 67 | 76.45882352941176470588235294117647058824 | 0 | 0 | 2055067 | 851181.6383636544391176470588235294117647 | 2096121.51662017967676470588235294117647 | 1 | 0 | 23 | 0 | 0 | 1 | 1 | 38.21 | 40 | 60 | 192.619(A)(3) | 1983-10-18 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.4 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THIRD PARTY CONTRACTOR WORKING IN VAULT CUT INTO FACILITY WITH SAWZALL. | [154 empty] | DANIEL EVANS | MANAGER COMPLIANCE | daniel.evans@enbridge.com | [5 empty] | DANIEL EVANS | MANAGER COMPLIANCE | 3305715796 | daniel.evans@enbridge.com | ON MAY 28TH, 2024 AT APPROXIMATELY 2:44PM, AN EXPLOSION OCCURRED AT THE REALTY BUILDING LOCATED AT 47 E FEDERAL STREET, YOUNGSTOWN, OH. THE EXPLOSION DESTROYED THE FIRST FLOOR OF THE BUILDING, AND SEVERELY DAMAGED THE BASEMENT AND FLOORS ABOVE IT. THE FIRST FLOOR OF THE 13 STORY BUILDING WAS OCCUPIED BY A BRANCH OF CHASE BANK, WHILE THE STORIES ABOVE CONTAINED OFFICES AND 23 APARTMENT UNITS. THE EXPLOSION RESULTED IN A ONE FATALITY AND 9 INJURIES REQUIRING HOSPITALIZATION. AFTER THE EXPLOSION, AN INITIAL INVESTIGATION CONDUCTED BY ENBRIDGE GAS OHIO THE NIGHT OF MAY 28TH AND CONTINUING INTO THE MORNING OF MAY 29TH DETERMINED THAT AN INACTIVE SERVICE LINE TO AN UNDERGROUND VAULT CONNECTED TO THE BUILDING HAD BEEN CUT, WHICH RESULTED IN A RELEASE OF NATURAL GAS. IT WAS DISCOVERED THAT A THIRD-PARTY CONTRACTOR HAD BEEN HIRED TO CLEAR OUT OLD UTILITIES IN THE BASEMENT OF THE BUILDING, AND THAT CONTRACTOR MADE THE CUT TO THE INACTIVE SERVICE LINE. A NTSB INVESTIGATION INTO THE INCIDENT WAS ANNOUNCED THE AFTERNOON OF MAY 29TH, AND IS ON-GOING. AS ADDITIONAL INFORMATION IS PUBLICLY RELEASED DURING THE COURSE OF THE NTSB INVESTIGATION, FUTURE SUPPLEMENTAL REPORTS WILL BE UPDATED TO REFLECT THOSE FACTS. THE TOTAL DAMAGES FROM THE INCIDENT ARE STILL BEING DETERMINED. THE FIGURES USED IN THIS REPORT WERE BASED ON PUBLICLY AVAILABLE VALUATION DATA FROM THE MAHONING COUNTY AUDITOR WEBSITE AND ARE ONLY A PRELIMINARY ESTIMATE. 11/13/2025 SUPPLEMENTAL/FINAL UPDATE: THE NATIONAL TRANSPORTATION SAFETY BOARD DETERMINED THAT THE PROBABLE CAUSE OF THE EXPLOSION AND SUBSEQUENT FATALITY WAS A CUT BY A SCRAP-REMOVAL CREW INTO AN ACTIVE CUSTOMER OWNED SERVICE LINE, WHICH WAS INCORRECTLY DOCUMENTED AS HAVING BEEN ABANDONED YEARS EARLIER BY THE PIPELINE OWNER AT THE TIME, DOMINION ENERGY INC., AND WHICH ALLOWED NATURAL GAS TO LEAK INTO THE REALTY BUILDING WHERE IT WAS IGNITED BY AN UNKNOWN SOURCE. CONTRIBUTING TO THE SEVERITY OF THE ACCIDENT WERE CHASE BANK’S EMERGENCY PROCEDURES THAT DID NOT REQUIRE EMPLOYEES TO IMMEDIATELY EVACUATE UPON BEING ALERTED TO A NATURAL GAS LEAK. AS DISCUSSED IN THE NTSB REPORT, ENBRIDGE HAS TAKEN ADDITIONAL STEPS TO INVESTIGATE OTHER PIPELINES THAT WERE DOCUMENTED AS ABANDONED BY PREVIOUS OWNERS. PLEASE REFERENCE NTSB DOCKET PLD24MR005 AND PIPELINE INVESTIGATION REPORT (PIR-25-03) FOR FURTHER INFORMATION.
2026-06-30 10:38 | NO | YES | YES | 20240036 | 39735 | 2024-06-28 18:50 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2023-02-24 | PACIFIC | NO | 2023 | 591 GOLF COURSE RD | LAKE ARROWHEAD | SAN BERNARDINO | CA | 92352 | 34.2606 | -117.2169 |  |  |  | YES | [5 empty] | 2024-05-31 18:54 | 1400498 | 1400502 | NATURAL GAS |  | 416 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 2023-02-24 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 416 | YES | 2 | 2023-02-24 | YES | OPERATOR | 2023-03-01 09:51 | 2023-03-01 15:05 | 2023-03-01 15:05 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1963 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | DAMAGE BY SNOW | [5 empty] | CLASS 3 LOCATION | 2706500 | 2816140.8230386658245 | 1840 | 1914.53874538745432 | 1000 | 1040.510187710573 | 0 | 0 |  | 6 | 2496 | 2177.266187050359712230215827338129496403 | 0 | 0 | 2711836 | 1146494.38132151126678604316546762589928 | 2821273.1381588142115322302158273381295 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 45 | 45 | 60 | 192.619(A)(1) | 1963-10-01 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | DAMAGE FROM SNOW/ICE | [56 empty] | SNOW/ICE IMPACT OR ACCUMULATION | [5 empty] | YES |  |  |  | YES | SNOWSTORM | [213 empty] | CARLOS CHAVEZ | PIPELINE SAFETY AND COMPLIANCE ADVISOR | cchavez@socalgas.com | 213-264-6814 |  | CARLOS CHAVEZ | cchavez@socalgas.com | (213)264-6814 | CARLOS CHAVEZ | PIPELINE SAFETY AND COMPLIANCE ADVISOR | (213)264-6814 | cchavez@socalgas.com | 06-28-2024: THE SAN GABRIEL MOUNTAINS SUFFERED AN UNPRECEDENTED SNOWSTORM EVENT IN FEBRUARY AND MARCH OF 2023, CAUSING MAJOR SNOW LEVELS WITH WIDE RANGING IMPACT, INCLUDING SIGNIFICANTLY LIMITING ACCESS TO THE AFFECTED AREA. IT WAS RECENTLY DISCOVERED THAT THERE WAS A RELEASE OF NATURAL GAS, CAUSED BY EXCESSIVE SNOW ACCUMULATION, WHICH LED TO PIPELINE DAMAGE THAT POTENTIALLY RESULTED IN PROPERTY DAMAGES OVER $129,300 AT THESE LOCATIONS: 591 GOLF COURSE RD, LAKE ARROWHEAD ON 24 FEB 2023, 910 CREST FERN DRIVE, UNIT A, LAKE ARROWHEAD, CA 92352 ON 1 MARCH 2023, 772 SIERRA VISTA DRIVE, TWIN PEAKS, CA 92391 ON 3 MARCH 2023, 26520 AUGUSTA DRIVE, LAKE ARROWHEAD, CA 92352 ON 4 MARCH 2023, AND 30683 FERNDALE DRIVE, RUNNING SPRINGS, CA 92382 ON 4 MARCH 2023. CPUC SED WAS AWARE OF THE EXTREME WEATHER EVENT AND SOCALGAS DID PROVIDE A COURTESY CALL TO THE CPUC ON 03/02/2023 WITH UP-TO-DATE INFORMATION AT THAT TIME. DURING THE SNOWSTORM EVENT, SOCALGAS, WHICH HAD LIMITED ACCESS TO THE IMPACTED AREA, WAS UNAWARE THAT REPORTING CRITERIA HAD BEEN MET. GAS LOSS CALCULATIONS AND DAMAGE COSTS WITHIN THIS FORM ARE BEST EFFORT ESTIMATIONS AND ARE TOTALS OF ALL FIVE (5) ADDRESSES COMBINED. RESPONSES IN A10E, A16, AND A17 ARE ASSOCIATED WITH THE SECOND LOCATION OF 910 CREST FERN DRIVE, AS SOCALGAS DID NOT BECOME AWARE OF THE EVENTS AT 591GOLF COURSE RD UNTIL LATER.
2026-06-30 10:38 | NO | YES | NO | 20240037 | 41498 | 2024-07-08 17:47 | SUPPLEMENTAL FINAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2024-06-08 01:23 | CENTRAL | YES | 2024 | 4405 APPLETREE CT | ST. JOSEPH | BUCHANAN | MO | 64506 | 39.7829 | -94.7893 |  |  |  | YES | [5 empty] | 2024-06-08 09:58 | 1401249 | 1401394 | NATURAL GAS |  | 28.16 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-06-08 01:23 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 28.16 | NO | 0 | 2024-06-08 01:43 |  |  |  | 2024-06-08 02:15 | 2024-06-08 01:46 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1989 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | UNKNOWN | [10 empty] | OTHER | [8 empty] | SERVICE RISER STRUCK BY LIGHTNING AND BROKE RISER WHICH ALLOWED GAS TO BE RELEASED. | CLASS 3 LOCATION | 210000 | 214194.38546827083 | 1869 | 1906.330030667610387 | 500 | 509.9866320673115 | 0 | 0 |  | 9.38 | 264 | 301.270588235294117647058823529411764706 | 0 | 0 | 212633 | 88202.2352728400115321764705882352941176 | 216911.9727192410460046470588235294117647 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 44.5 | 44.3 | 58 | 192.619(A)(2) | 1989-02-10 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF GAS RELEASED WAS NOT DETECTABLE BY THE SCADA SYSTEM AND THE CONTROLLER(S) TOOK NO ACTIONS THAT WOULD HAVE CONTRIBUTED TO OR CAUSED THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [218 empty] | ERIN MILKERT | MANAGER DISTRIBUTION INTEGRITY | erin.milkert@spireenergy.com | 314-349-2932 |  | ERIN MILKERT | erin.milkert@spireenergy.com | 314-349-2932 | CRAIG HOEFERLIN | VP OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A THUNDERSTORM EVENT CAUSED LIGHTNING TO STRIKE RESIDENTIAL HOME AND THEN HIT THE COMPANY'S NATURAL GAS METER LOCATED OUTSIDE OF 4405 APPLETREE COURT ST. JOSEPH MO. THE ESCAPING NATURAL GAS CAUGHT FIRE WHICH RESULTED IN ADDITIONAL DAMAGE TO THE HOME. A 48-HOUR UPDATE TO THE NRC WAS MADE ON JUNE 10, 2024 AT 8:40 AM - REPORT NUMBER 1401394. SUPPLEMENTAL REPORT HAS BEEN UPDATED TO REFLECT THE CORRECT EVENT TIMES.
2026-06-30 10:38 | NO | YES | NO | 20240038 | 39784 | 2024-07-17 17:24 | ORIGINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2024-06-18 14:47 | CENTRAL | YES | 2024 | 225 WILLINGTON WAY | OSWEGO | KENDALL | IL | 60543 | 41.6871 | -88.3244 | [7 empty] | YES | CUT AND CAP | 2024-06-18 16:27 | 1402289 | 1402449 | NATURAL GAS |  | 12.6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-06-18 14:47 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 11.8 | NO | 2 | 2024-06-18 14:58 |  |  |  | 2024-06-18 15:14 | 2024-06-18 15:14 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2005 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ALUMINUM / STEEL | [9 empty] | LEAK |  |  | OTHER | MULCH FIRE MELTED METER SET. | [5 empty] | CLASS 3 LOCATION | 550000 | 560985.29527404265 | 200 | 203.9946528269246 | 2938 | 2996.681450027522374 | 0 | 0 |  | 3.4 | 43 | 49.07058823529411764705882352941176470588 | 0 | 0 | 553181 | 229133.1349504369977231764705882352941176 | 564235.0419651323910916470588235294117647 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 56 | 57 | 60 | 192.619(A)(2) | 2004-07-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | MULCH FIRE DAMAGED METER SET CAUSING NATURAL GAS RELEASE. | [154 empty] | PAMELA L. REID | MANAGER - COMPLIANCE AND QA | preid@southernco.com | (630) 417-0867 |  | PAMELA L. REID | preid@southernco.com | (630) 417-0867 | PAMELA L. REID | MANAGER - COMPLIANCE AND QA | (630) 417-0867 | preid@southernco.com | NICOR GAS RESPONDED TO A RESIDENTIAL FIRE REPORTED BY THE LOCAL FIRE DEPARTMENT. THE NICOR GAS FIELD SERVICE REPRESENTATIVE REPORTED THAT THE METER SET, REGULATOR, AND ABOVE-GROUND SERVICE WERE COMPLETELY MELTED. THE GAS WAS STOPPED BY A FIELD OPERATIONS DISTRIBUTION CREW AT 4:10 P.M. THE FIRE DEPARTMENT INVESTIGATOR IDENTIFIED THE CAUSE OF THE INCIDENT AS A MULCH FIRE. THE GAS SERVICE TO THE HOUSE WAS ABANDONED IN PLACE AND CAPPED.
2026-06-30 10:38 | NO | YES | NO | 20240039 | 40424 | 2024-07-26 14:21 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | 3600 MIDTOWN DR. | TAMPA | FL | 33607 | 2024-06-26 17:30 | EASTERN | YES | 2024 | 7133 SOUTHSIDE BLVD | JACKSONVILLE | DUVAL COUNTY | FL | 32256 | 30.2439 | -81.5514 |  | YES |  |  |  | YES |  |  |  | 2024-07-03 15:11 | 1403702 | 1403857 | NATURAL GAS |  | 3903.9 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-06-26 18:19 |  |  |  | 2024-06-26 18:39 | 2024-06-26 18:39 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 144 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1997 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 1 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 180000 | 183595.18754423214 | 0 | 0 | 0 | 0 | 0 | 10 | 39039 | 44550.3882352941176470588235294117647059 | 0 | 0 | 219039 | 110833.9074393239611764705882352941176471 | 228145.5757795262576470588235294117647059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 220 | 250 | 192.619(A)(4) | 1999-10-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD-PARTY DAMAGE, DIRECTIONAL DRILLING, WAS IDENTIFIED WITH NO IMPACT TO ALARMS WITHIN THE SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | SEWER (SANITARY/STORM) | YES | 169402076 |  | Unknown | FACILITY OWNER | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | IYANNA JONES | COMPLIANCE ANALYST | iejones@tecoenergy.com | (407)-420-6617 |  | JAMES WHITE JR. | jtwhitejr@tecoenergy.com | (904)-219-5163 | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | 407-420-6667 | rharris@tecoenergy.com | PGS RECEIVED A LEAK REPORT ON JUNE 26, 2024, AT APPROXIMATELY 18:19 THAT A THIRD-PARTY CONTRACTOR HIT A 6-INCH STEEL GAS MAIN ATTEMPTING TO DIRECTIONAL DRILL INTO THE GROUND, SUBSEQUENTLY STRIKING THE GAS FACILITY. THE DAMAGE PIPE WAS MADE SAFE AT APPROXIMATELY 1:30 ON 06/27/2024 BY TURNING OFF TWO VALVES AND SQUEEZING THE DAMAGED AREA OF THE PIPE. THE DAMAGE SECTION OF 6" STEEL PIPE WAS REPAIRED ON 07/06/2024 AT 16:00 AND THE DAMAGED SECTION OF PIPE WAS REMOVED AND REPLACED BY WELDING IN NEW PRETESTED PIPE AND FITTINGS. THE EXCAVATED AREA WAS BACK FILLED, AND THE SURFACE RESTORED TO ITS ORIGINAL STATE. THE ENTIRE SECTION OF THE REPLACEMENT MAIN WAS TESTED AND CHARTED AFTER FINAL REPAIRS WERE MADE.
2026-06-30 10:38 | NO | YES | NO | 20240040 | 39849 | 2024-08-01 10:50 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2024-07-02 11:45 | CENTRAL | YES | 2024 | 15602 FOUR SEASON DR | HOUSTON | HARRIS | TX | 77084 | 29.852 | -95.6308 | [5 empty] | YES |  |  |  | 2024-07-02 15:15 | 1403630 | 1403858 | NATURAL GAS |  | 11.75 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-07-02 11:45 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 11.75 | NO | 0 | 2024-07-02 12:11 |  |  |  | 2024-07-02 12:11 | 2024-07-02 14:50 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1983 | 1983 | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.5 | MDPE 2306 | DUPONT | PLASTIC |  |  |  |  | OTHER | ALDYL A | 11 |  |  |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 0.5 | 0.5 |  | CLASS 3 LOCATION | 200000 | 203994.6528269246 | 113 | 115.256978847212399 | 3247 | 3311.853188645120881 | 0 | 0 |  | 5.99 | 70 | 79.88235294117647058823529411764705882353 | 0 | 0 | 203430 | 84290.6717825606708047058823529411764706 | 207501.6453473581097505882352941176470588 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 45 | 45 | 60 | 192.619(A)(1) | 1983-12-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE DID NOT EXCEED DETECTION THRESHOLD OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | YES | YES |  | NO |  |  |  |  | YES |  |  | YES | PRIVATE LANDOWNER | [6 empty] | NO | NO | < 18” |  | CONTRACTOR | HAND TOOLS | UNKNOWN/OTHER | YES | 246768597 | 811 | NO | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | ELMER SELVERA | OPERATIONS SPECIALIST | elmer.selvera@centerpointenergy.com | 281-755-2470 |  | ELMER SELVERA | elmer.selvera@centerpointenergy.com | 281-755-2470 | PHILLIP GREEN | MANAGER GAS COMPLIANCE SOUTH | 713-378-9845 | phillip.green@centerpointenergy.com | ON JULY 2, 2024, RAM JACK FOUNDATION SOLUTIONS WERE PERFORMING FOUNDATION REPAIRS AT 15602 FOUR SEASONS. WHILE EXCAVATING WITH HAND TOOLS, THE PROPERLY MARKED GAS SERVICE LINE AT THIS LOCATION WAS STRUCK. THE ESCAPING GAS IGNITED, RESULTING IN FIRE DAMAGE TO THE SINGLE-STORY STRUCTURE. THE FIRE DEPARTMENT RESPONDED AND NOTIFIED CENTERPOINT ENERGY AT 11:45AM. SERVICE TECHNICIAN ARRIVED AT 12:11PM, GAS WAS SHUT OFF AT 1:45PM, LINE WAS SQUEEZED OFF AT THE SERVICE TAP LOCATION BY THE FIRE DEPARTMENT ON SITE AND CENTERPOINT ENERGY PERSONNEL. ADDITIONALLY, THIS SAME SERVICE LINE WAS STRUCK ON JULY 1, 2024, BY THE SAME 3RD PARTY EXCAVATOR, RAM JACK FOUNDATION SOLUTIONS. CENTERPOINT ENERGY RESPONDED AND MADE REPAIRS ON JULY 1,2024.
2026-06-30 10:38 | NO | YES | YES | 20240041 | 40608 | 2024-08-06 11:28 | SUPPLEMENTAL FINAL | 4060 | ENBRIDGE GAS OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2024-07-07 01:50 | EASTERN | YES | 2024 | 1210 INDEPENDENCE AVENUE | AKRON | SUMMIT | OH | 44310 | 41.1107 | -81.4712 |  | YES | [7 empty] | 2024-07-08 13:46 | 1404092 | 1404282 | NATURAL GAS |  | 933 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2024-07-07 02:16 | ALLOWED TO BURN OUT |  | 900 | NO | 0 | 2024-07-07 02:10 |  |  |  | 2024-07-07 02:47 | 2024-07-08 13:00 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2006 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | YES |  |  |  | OTHER | ABOVE GROUND SERVICE RISER AND METER SET | [9 empty] | OTHER | [8 empty] | VEHICLE DROVE THROUGH BOLLARDS AND METER SET BEFORE IMPACTING BUILDING. | CLASS 3 LOCATION | 0 | 0 | 5000 | 5099.866320673115 | 5000 | 5099.866320673115 | 0 | 0 | INCIDENT WAS SECONDARY IGNITION | 2.828 | 2639 | 3011.564705882352941176470588235294117647 | 0 | 0 | 12639 | 6594.417733557213529411764705882352941176 | 13211.2973472285829411764705882352941176 | 1 | 0 | 182 | 0 | 0 | 182 | 1 | 46 | 46 | 60 | 192.619(C) | 1967-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.5 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  |  | YES |  |  | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 200 | YES | YES | [141 empty] | DANIEL EVANS | SUPERVISOR PIPELINE COMPLIANCE | daniel.a.evans@dominionenergy.com | 3305715796 |  | GABE VIGORITO | gabriele.vigorito@dominionenergy.com | 3305907504 | DANIEL EVANS | SUPERVISOR PIPELINE COMPLIANCE | 3305715796 | daniel.a.evans@dominionenergy.com | AT APPROXIMATELY 01:50 LOCAL TIME, A LARGE SUV DRIVEN BY A MEMBER OF THE GENERAL PUBLIC LEFT THE ROADWAY TRAVELING SOUTH NEAR THE INTERSECTION OF BUCHHOLZER AVE AND INDEPENDENCE AVE IN AKRON, OH. THE VEHICLE TRAVELED APPROXIMATELY 200' THROUGH A PARKING AREA BEFORE STRIKING, IN ORDER; PROTECTIVE BOLLARDS, AN OUTDOOR METER SET, AND FINALLY THE OUTSIDE BUILDING WALL OF ADDRESS 1210 INDEPENDENCE AVENUE IN AKRON, OHIO. THE ADDRESS WAS A REGAL CINEMA MOVIE THEATER, UNOCCUPIED AT THE TIME. THE FORCE OF THE VEHICLE IMPACT FOLDED THE PROTECTIVE BOLLARDS OVER AND SHEARED THE METER/MANIFOLD ASSEMBLY OFF FROM THE 2" SERVICE RISER AT GROUND LEVEL. JURISDICTIONAL GAS BEGAN TO RELEASE, AND THE VEHICLE CAUGHT FIRE. AKRON POLICE AND FIRE RESPONDED TO THE CRASH AND CONTACTED ENBRIDGE GAS OHIO'S DISPATCH CENTER AT 02:10. ENBRIDGE DISPATCHED A QUALIFIED PERSON TO THE SCENE. AT APPROXIMATELY 02:16, AKRON FIRE DEPARTMENT CALLED ENBRIDGE PERSONNEL TO REPORT THAT NATURAL GAS WAS ALSO ON FIRE. ENBRIDGE DISPATCHED FURTHER PERSONNEL TO ASSIST AT THE SCENE. ENBRIDGE PERSONNEL FIRST ARRIVED AT THE SCENE AT 02:47 TO FIND THE AKRON FIRE DEPARTMENT MONITORING THE FIRE AND WERE ASKED TO SHUT OFF FLOW OF GAS TO THE BUILDING. THE EXTERIOR OF THE BUILDING AROUND THE METER WAS BRICK, AND NOT BELIEVED TO BE LIKELY TO ALLOW THE FIRE TO SPREAD THROUGHOUT THE STRUCTURE. ENBRIDGE PERSONNEL AT THE SCENE WERE UNABLE TO LOCATE A CURB BOX TO ISOLATE THE SERVICE LINE AFTER SEARCHING THE AREA AND REQUESTING EMERGENCY LOCATE SERVICES FROM THE OHIO UTILITY PROTECTION SERVICE. ENBRIDGE PERSONNEL IDENTIFIED THREE MAIN LINE VALVES THAT COULD BE CLOSED TO ISOLATE GAS TO THE BUILDING, WHICH ALSO CAUSE AN OUTAGE OF 182 RESIDENTIAL CUSTOMERS. ENBRIDGE PERSONNEL PROCEEDED WITH CLOSING THESE VALVES AT APPROXIMATELY 05:40. AT 06:00, GAS FLOW TO THE BUILDING HAD STOPPED AND THE FIRE BURNED OUT. ENBRIDGE PROCEEDED WITH TRACING OUT THE SERVICE LINE AND WERE ABLE TO LOCATE A CURB BOX IN A DIFFERENT LOCATION THAT WAS ORIGINALLY SEARCHED. ENBRIDGE CUT THE SERVICE LINE TO THE BUILDING WHILE BEGINNING THE PROCESS OF TURNING OFF IMPACTED CUSTOMERS TO BEGIN THE RELIGHT PROCESS. ENBRIDGE RELIT ALL BUT 35 OF THE IMPACTED CUSTOMERS BY 21:55 ON 7/7/2024 DUE TO NO ACCESS TO THE PREMISE. THE OWNER OF THE VEHICLE WAS NOT PRESENT AT THE SCENE OF THE ACCIDENT, SO THE IDENTITY AND SCOPE OF HIS INJURIES WERE NOT INITIALLY CLEAR. LATER, AKRON POLICE WERE ABLE TO LOCATE THE OWNER AT A LOCAL HOSPITAL. HE HAD BEEN PICKED UP AND TRANSPORTED THERE BY A GOOD SAMARITAN WHO FOUND HIM WALKING ALONG THE ROAD. THE FULL SCOPE OF INJURIES TO THE OWNER IS CURRENTLY UNKNOWN, BUT PER THE AKRON POLICE REPORT HE DID SUSTAIN SOME BURNS. THE OWNER WAS FOUND TO BE UNDER THE INFLUENCE OF ALCOHOL BUT DENIED BEING THE DRIVER OF THE VEHICLE. HE CLAIMED A SECOND INDIVIDUAL WAS DRIVING BUT DID NOT KNOW HIS IDENTITY. THE ACCIDENT IS STILL UNDER INVESTIGATION BY THE AKRON POLICE DEPARTMENT. THE EXACT SEQUENCE OF VEHICLE IMPACT, VEHICLE FIRE, AND GAS IGNITION THAT OCCURRED AFTER THE IMPACT IS CURRENTLY UNKNOWN. GIVEN THE RELEASE AND IGNITION OF JURISDICTIONAL GAS, AND REPORTED BURN INJURIES SUSTAINED BY THE VEHICLE OWNER, ENBRIDGE AT THIS TIME BELIEVES IT IS PROBABLE THAT JURISDICTIONAL GAS CONTRIBUTED TO THE OVERNIGHT HOSPITALIZATION OF THE DRIVER. 3/11/25 SUPPLEMENTAL/FINAL UPDATE: AKRON POLICE REPORT CONFIRMS THAT DRIVER OF THE INVOLVED MOTOR VEHICLE WAS TREATED FOR BURNS SUSTAINED DURING THE ACCIDENT AT AKRON CHILDREN'S HOSPITAL. GIVEN THAT A RELEASE OF JURISDICTIONAL GAS WAS INVOLVED IN THE FIRE AND LIKELY CONTRIBUTED TO THE DRIVER'S INJURIES, EGO IS FINALIZING THIS AS A REPORTABLE EVENT UNDER THE CRITERIA OF §191.3
2026-06-30 10:38 | NO | YES | YES | 20240042 | 42160 | 2024-08-13 10:42 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2024-07-10 16:08 | CENTRAL | YES | 2024 | 917 NORTHLAKE DRIVE | RICHARDSON | DALLAS | TX | 75080 | 32.9586 | -96.7542 | [6 empty] | YES |  |  | 2024-07-10 17:06 | 1404326 | 1404510 | NATURAL GAS |  | 1.25 | 0 | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES | 2024-07-10 16:08 | OPERATOR/CONTRACTOR |  | 1.25 | NO | 0 | 2024-07-10 15:30 | NO |  |  | 2024-07-10 15:30 | 2024-07-10 18:30 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 33 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | SEE NARRATIVE FOR DETAILS | CLASS 3 LOCATION | 0 | 0 | 3360 | 3427.11016749233328 | 0 | 0 | 0 | 0 |  | 8.503 | 11 | 12.55294117647058823529411764705882352941 | 0 | 0 | 3371 | 1401.834758475223745882352941176470588235 | 3439.663108668803868235294117647058823529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 28 | 55 | 192.619(A)(3) | 2010-12-07 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 10 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | YES | 3 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | SEE NARRATIVE |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | BILL BROOKS | DIRECTOR OF REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 806-787-9422 |  |  |  |  | MARC ROTHBAUER | V.P. COMPLIANCE AND REGULATORY REPORTING | 469-236-8616 | marc.rothbauer@atmosenergy.com | ON JULY 10, 2024, A SECOND-PARTY CONTRACTOR WAS DISPATCHED TO REPAIR A LEAK ON A SERVICE TAPPING TEE IN THE ALLEY OF NORTHLAKE DRIVE IN RICHARDSON, TEXAS. BOTH THE MAIN AND TAPPING TEE WERE STEEL. TO RETIRE THE TAPPING TEE, THE CAP WAS REMOVED. AFTER THE CONTRACTOR ONSITE MADE MULTIPLE ATTEMPTS TO UTILIZE A TAPERED PLUG IN THE REPAIR, THERE WAS A QUANTITY OF NATURAL GAS RELEASED. AT APPROXIMATELY 3:30 P.M. A FLASH FIRE OCCURRED. THE SOURCE OF THE IGNITION IS UNKNOWN. AN EMPLOYEE ONSITE TO OBSERVE THE REPAIR NOTIFIED ATMOS ENERGY OF THE FLASH FIRE. CONTRACTOR PERSONNEL EXTINGUISHED THE FIRE. THE INJURED CONTRACTOR SUFFERED BURNS TO HIS HANDS, WAS TRANSPORTED TO THE HOSPITAL, AND WAS ADMITTED AT APPROXIMATELY 6:30 P.M. THE HOSPITALIZATION IS CONFIRMED DISCOVERY TIME FOR THIS EVENT. THE CONTRACTOR DID NOT FOLLOW THE APPROPRIATE AOC’S. AFTER THE EVENT, CONTRACT EMPLOYEES INVOLVED WERE SUSPENDED FROM WORK, RETRAINED, AND COMPLETED ASSESSMENTS IN MULTIPLE OQ TASKS. ADDITIONALLY, AN ALL-PIPELINE CONSTRUCTION CONTRACTOR STAND-DOWN WAS CONDUCTED ON JULY 12, 2024, TO DISCUSS THIS EVENT AND COMMUNICATE PROCEDURES AND LESSONS LEARNED. ALL CONSTRUCTION CONTRACTORS REVIEWED AND IMPLEMENTED THE USE OF SAFE T STOPPERS AS THE APPROPRIATE TOOL TO ADDRESS GAS RELEASES AT THE CAP ON A SERVICE TEE AND THE DISCONTINUANCE OF EXPANSION PLUGS, TAPERED PLUGS, AND PUNCHES. THE LEAK REPAIR WAS COMPLETED AT 1:17 A.M. ON JULY 11, 2024.
2026-06-30 10:38 | NO | YES | NO | 20240043 | 40969 | 2024-08-15 17:26 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2024-07-16 11:30 | CENTRAL | YES | 2024 | 1605 H ST | FLORESVILLE | WILSON | TX | 78114 | 29.1335 | -98.1476 | [5 empty] | YES |  |  |  | 2024-07-16 15:31 | 1404974 | 1405079 | NATURAL GAS |  | 51.51 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-07-16 14:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 51.51 | YES | 5 | 2024-07-16 11:45 | YES | OPERATOR | 2024-07-16 14:15 | 2024-07-16 11:45 | 2024-07-16 14:05 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 42 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2021 | 2021 |  |  |  |  | 2 | ASTM 2406/2708 | DURALINE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 500000 | 509986.6320673115 | 16335 | 16661.263269639066705 | 180 | 183.59518754423214 | 0 | 0 |  | 9.73 | 501 | 571.729411764705882352941176470588235294 | 0 | 0 | 517016 | 214390.6573118892381438235294117647058824 | 527403.2199362595047273529411764705882353 | 0 | 0 | 2 | 0 | 0 | 3 | 0 | 30 | 30 | 60 | 192.619(A)(1) | 2021-06-29 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 0.5 |  | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FAILURE DID NOT EXCEED THE DETECTION THRESHOLD OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [5 empty] | YES |  |  | NO | NO | > 36” |  | UTILITY | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2469288723 | TEXAS 811 | NO | CONTRACT LOCATOR | YES | UNKNOWN/OTHER |  | LOCATING ISSUE | FACILITY MARKED INACCURATELY DUE TO LOCATOR ERROR | [170 empty] | ELMER SELVERA | OPERATIONS SPECIALIST | elmer.selvera@centerpointenergy.com | 281-755-2470 |  | ELMER SELVERA | operations specialist | 281-755-2470 | PHILLIP GREEN | MANAGER GAS COMPLIANCE | 713-378-9845 | phillip.green@centerpointenergy.com | ON JULY 16TH, 2024, C4 UNLIMITED WAS PERFORMING BORING EXCAVATION ACTIVITIES TO INSTALL TELECOMMUNICATIONS CONDUIT FOR RISE BROADBAND IN THE 1600 BLOCK OF H ST. IN FLORESVILLE, TEXAS. AT 11:30AM, CENTERPOINT ENERGY RESPONDED TO A LEAK ODOR CALL AT 1705 10TH ST. NO GAS LEAK ON THE PROPERTY WAS DETECTED BY THE TECHNICIAN; HOWEVER, ODOR WAS DETECTED. THE CENTERPOINT ENERGY TECHNICIAN BEGAN INVESTIGATING THE VICINITY FOR LEAKS. AT 11:45AM, THE CENTERPOINT ENERGY TECH WAS FLAGGED DOWN BY CONTRACT LOCATOR REPRESENTATIVE AND NOTIFIED OF POSSIBLE DAMAGE TO CENTERPOINT ENERGY'S GAS LINE IN THE 1600 BLOCK OF H ST. BY C4 UNLIMITED. C4 UNLIMITED DID NOT REPORT THE POSSIBLE DAMAGE TO CENTERPOINT ENERGY. THE CENTERPOINT ENERGY TECHNICIAN DETECTED GAS VENTING OUT OF THE GROUND AT MULTIPLE LOCATIONS ALONG H ST. THE TECHNICIAN THEN BEGAN TO CHECK THE SEWER LATERAL AT 1601 H ST. AND IDENTIFIED GAS BLOWING. THIS PROMPTED THE TECHNICIAN TO DETERMINE WHETHER EVACUATIONS WERE NECESSARY AT THIS LOCATION AND EAST OF 1601 H ST., IN THE DIRECTION OF THE POSSIBLE BORE PATH, AS WELL AS REQUEST ADDITIONAL RESOURCES FROM CENTERPOINT ENERGY. AT 12:00PM ADDITIONAL CENTERPOINT ENERGY RESOURCES ARRIVED TO ASSIST WITH IDENTIFYING THE EXTENT OF THE GAS LEAK, OPENING SEWER LATERAL CLEAN OUTS TO VENT OUT GAS FROM SEWER SYSTEM, AS WELL AS ENSURING EVACUATIONS FROM THE 1600 BLOCK OF H ST. IT WAS LATER DETERMINED THAT THE STRUCTURES WERE PREVIOUSLY EVACUATED BY THE FLORESVILLE FIRE DEPARTMENT. AFTER EVACUATIONS WERE CONFIRMED, THE CENTERPOINT ENERGY CONSTRUCTION CREW ESTABLISHED THE DAMAGE LOCATION AREA AND REMOTE ISOLATION POINT. AT 2:00PM, WHILE THE CONSTRUCTION CREW WAS EXCAVATING AT THE ISOLATION POINT, THE MAIN STRUCTURE AT 1605 H ST. EXPLODED. THE CREW CONTINUED EXCAVATING THE GAS LINE AND SQUEEZED OFF THE 2" PLASTIC MAIN AT 2:05PM. AFTER THE INCIDENT, IT WAS DETERMINED THAT THE CONTRACT LOCATOR INCORRECTLY LOCATED AND MARKED THE 2" PLASTIC MAIN, WHICH THE EXCAVATOR C4 UNLIMITED HAD DAMAGED IN SEVERAL LOCATIONS.
2026-06-30 10:38 | NO | NO | NO | 20240044 | 39911 | 2024-08-16 16:37 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2024-07-18 15:06 | EASTERN | YES | 2024 | NEAR INTERSECTION LEE JACKSON MEM. HWY & STRINGFELLOW RD. | CHANTILLY | FAIRFAX COUNTY | VA | 20151 | 38.8843 | -77.4065 | [5 empty] | YES |  |  |  | 2024-07-18 20:29 | 1405223 | 1405316 | NATURAL GAS |  | 2304 | 256 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-07-18 15:03 | YES | OPERATOR | 2024-07-18 15:31 | 2024-07-18 15:31 | 2024-07-18 20:29 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 60 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1997 | 1996 |  |  |  |  | 12 | ASTM D2513 | ALDYL-A | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 4 | 2 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 2000 | 2039.946528269246 | 36500 | 37229.0241409137395 | 54405 | 55491.645435244164315 | CONTRACTOR: LABOR, TRAFFIC CONTROL, SHORING, LIGHTING, BACKFILL MATERIAL, PAVING | 2.1838 | 5031 | 5741.258823529411764705882352941176470588 | 559 | 637.917647058823529411764705882352941176 | 98495 | 43673.8764183191746479411764705882352941 | 101139.7925750153851091176470588235294118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1997-06-13 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA DOES NOT HAVE ANY CONTROL OVER THIS PORTION OF THE SYSTEM. IT WAS MONITORING ONLY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [8 empty] | NO | NO | MEASURED DEPTH FROM GRADE | 60 | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | A418001634 |  | Unknown | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY MARKED INACCURATELY DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | RICHARD FITZPATRICK | SUPERVISOR DOT PIPELINE SAFETY | richardfitzpatrick@washgas.com | 7036397825 |  | RICHARD FITZPATRICK | richardfitzpatrick@washgas.com | 7036397825 | SHANNON MALONEY | MANAGER DOT PIPELINE SAFETY AND COMPLIANCE | 7037505558 | smaloney@washgas.com | ON 7/18/24 AT 1506 HRS, WASHINGTON GAS RECEIVED A REPORT OF A BROKEN NATURAL GAS LINE NEAR THE INTERSECTION OF LEE JACKSON MEM. HWY & STRINGFELLOW RD. CHANTILLY, VA. 20151 FROM A COMPANY WORKING ON FIBER. ON ARRIVAL, WG PERSONNEL WORKED WITH FAIRFAX COUNTY FIRE AND POLICE TO SECURE THE SCENE. WASHINGTON GAS GAINED ACCESS ON EACH SIDE OF THE DAMAGED FACILITY TO PERFORM A DOUBLE SQUEEZE-OFF OPERATION. THIS PORTION OF THE SYSTEM WAS A TWO-WAY FEED. WASHINGTON GAS STOPPED THE GAS FLOW 0109 HRS ON 7/19/24 AND THE ROADWAY WAS OPENED JUST AFTER. ON 7/19/24 AT 1310 HRS GAS WAS RESTORED TO NORMAL OPERATION. WASHINGTON GAS DOES NOT VIEW THIS EVENT AS 'SIGNIFICANT' PURSUANT TO THE DEFINITION OF 'INCIDENT' IN 49 C.F.R §191.3 (3) (IN ADDITION TO THE EVENT NOT MEETING THE CRITERIA FOR 'INCIDENT' PURSUANT TO 49 C.F.R §§191.3 (1) AND(2)), BUT IS FILING THIS REPORT BECAUSE THE EVENT IS AN OPEN MATTER AT THE VIRGINIA STATE CORPORATION COMMISSION.
2026-06-30 10:38 | NO | YES | NO | 20240047 | 40354 | 2024-08-30 14:41 | SUPPLEMENTAL FINAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY | CANONSBURG | PA | 15317 | 2024-08-02 13:40 | EASTERN | YES | 2024 | VIRIGINIA AVENUE AT CLEVELAND STREET | ROCHESTER | BEAVER | PA | 15074 | 40.7131 | -80.284 | [5 empty] | YES |  |  |  | 2024-08-02 21:52 | 1406738 | 1406850 | NATURAL GAS |  | 578.4 | 41.88 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-08-02 14:12 | YES | OPERATOR | 2024-08-02 14:22 | 2024-08-02 14:22 | 2024-08-02 14:22 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 90 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.203 | [6 empty] | MECHANICAL PUNCTURE | 0.9 | 0.4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 130593 | 133201.368483132821439 | 30000 | 30599.19792403869 | 0 | 0 |  | 4.88 | 2823 | 3221.541176470588235294117647058823529412 | 204 | 232.8 | 163620 | 69326.1336108683004093529411764705882353 | 167254.9075836420996742941176470588235294 | 8 | 3 | 1 | 0 | 0 | 1 | 11 | 92 | 92 | 100 | 192.619(A)(1) | 1988-04-29 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NATURE OF THE EVENT (EXCAVATION DAMAGE). | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | MEASURED DEPTH FROM GRADE | 90 | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 20241790152 |  | Unknown | CONTRACT LOCATOR | NO | YES | 30 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | MATTHEW MICELI | MANAGER - OPERATIONS COMPLIANCE AND RISK MANAGMENT | mmiceli@nisource.com | 724-812-2844 |  | MATTHEW MICELI | mmiceli@nisource.com | 724-812-2844 | BRIAN MCCAUL | VICE PRESIDENT GAS OPERATIONS | 4129926929 | bmccaul@nisource.com | SECOND PARTY CONTRACTOR DAMAGED 12'' STEEL HIGH PRESSURE DISTRIBUTION GAS MAIN. THE CONTRACTOR WAS USING AN EXCAVATOR TO DRIVE THE SHEET PILING INTO THE GROUND TO SUPPORT A SHORING BOX. THE SHEET PILING PUNCTURED THE GAS MAIN RESULTING IN A RELEASE OF GAS. THE EMERGENCY RESPONSE, REPAIR, AND RESTORATION RESULTED IN COSTS IN EXCESS OF $145,400.
2026-06-30 10:38 | NO | NO | NO | 20240048 | 39970 | 2024-09-04 14:37 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2024-08-05 13:10 | EASTERN | YES | 2024 | WELCOME ALL ROAD AT FAIRBURN ROAD | ATLANTA | GA | GA | 30331 | 33.6641 | -84.5226 | [7 empty] | YES | REPAIR MADE ON LIVE MAIN | 2024-08-05 13:44 | 1406960 | 1407043 | NATURAL GAS |  | 4709 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-08-05 10:48 |  |  |  | 2024-08-05 12:14 | 2024-08-05 12:14 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 42 | NO | YES |  |  |  |  | YES | UNCASED, BORED/DRILLED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1964 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 792 | 807.818825194621416 | 20995 | 21414.338680506409885 | 3675 | 3748.401745694739525 | PAVING RESTORATION | 1.905 | 8971 | 10237.4941176470588235294117647058823529 | 0 | 0 | 34433 | 18883.3497014186712062352941176470588235 | 36208.0533690428296495294117647058823529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 38 | 45 | 192.619(A)(2) | 1964-03-10 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 17 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 231114005671 |  | NO | CONTRACT LOCATOR | NO | NO |  | NOTIFICATION ISSUE | EXCAVATOR PROVIDED INCORRECT NOTIFICATION INFORMATION | [170 empty] | RALPH T MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | 4045843733 | (404) 584-4710 |  |  |  | RICK SLAGLE | MANAGER COMPLIANCE AND QA | 4045844910 | rslagle@southernco.com | A THIRD-PARTY PARTY EXCAVATOR (FOREVER PACHECO UNDERGROUND, LLC) STRUCK AND DAMAGED AN ATLANTA GAS LIGHT COMPANY (AGLC) 6-INCH STEEL GAS MAIN WHILE DIRECTIONALLY BORING TO INSTALL TELECOMMUNICATION FIBER MAIN NEAR THE INTERSECTION OF WELCOME ALL ROAD AT FAIRBURN ROAD SW, ATLANTA. THE DAMAGE OCCURRED WITHIN CLOSE PROXIMITY OF A CSX RAILROAD RIGHT-OF-WAY, AND THE RAILROAD COMPANY WAS CONTACTED TO STOP ANY TRAINS SCHEDULED TO COME THROUGH AT 12:10 HOURS. AT 13:10 HOURS, IT WAS IDENTIFIED THAT A COMPANY-ESTABLISHED THRESHOLD FOR A SIGNIFICANT EVENT HAD BEEN MET BECAUSE THE RAILROAD HAD BEEN CLOSED FOR ONE HOUR. UPON ARRIVAL, AGLC PERSONNEL WORKED WITH EMERGENCY RESPONDERS TO SECURE THE AREA AND MONITOR THE SURROUNDING AREA FOR GAS. GAS WAS SHUT-OFF TO THE DAMAGED AREA BY INSTALLING A REPAIR SLEEVE AND WELD-OVER. A LARGE PROJECT MARKING ' UTILITY FACILITY LOCATING AGREEMENT ('LARGE PROJECT AGREEMENT') WAS SIGNED ON NOVEMBER 14, 2023, WITH NEXTIER INFRASTRUCTURE SOLUTIONS TO LOCATE THE AREA AS A LARGE PROJECT EXCAVATION. AGL'S CONTRACT LOCATOR MARKED AGL'S FACILITIES LOCATED WITHIN THIS SPECIFIC WORK SITE ON MARCH 1, 2024, AS SET FORTH IN THE LARGE PROJECT AGREEMENT. AS TO THE DATE AND LOCATION OF THIS INCIDENT, THE SUBCONTRACTOR FOR NEXTIER WHO WAS PERFORMING THE EXCAVATION ACTIVITIES DID NOT NOTIFY AGL'S CONTRACT LOCATOR PRIOR TO COMMENCING EXCAVATION ACTIVITIES TO ENSURE THE SPECIFIC WORK SITE WAS MARKED OR RE-MARKED AS WAS REQUIRED BY THE LARGE PROJECT AGREEMENT. AGLC INITIALLY NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) UNDER NRC REPORT NUMBER 1406960. ADDITIONAL NRC REPORT NUMBER 1407043 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2026-06-30 10:38 | NO | YES | NO | 20240049 | 39975 | 2024-09-06 16:52 | ORIGINAL FINAL | 17570 | ROCHESTER GAS & ELECTRIC CORP | 180 SOUTH CLINTON AVENUE | ROCHESTER | NY | 14604 | 2024-08-08 03:22 | EASTERN | YES | 2024 | 154 THOMPSON RD. | HENRIETTA | MONROE | NY | 14467 | 43.0704 | -77.6035 |  |  | YES | [6 empty] | 2024-08-08 10:56 | 1407285 | 1409131 | NATURAL GAS |  | 27.63 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-08-08 03:24 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 27.63 | NO | 7 | 2024-08-08 03:40 |  |  |  | 2024-08-08 03:40 | 2024-08-08 03:40 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | 1960 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | OTHER | METER SET | [9 empty] | OTHER | [8 empty] | RESIDENT REMOVED SERVICE REGULATOR WHICH RESULTED IN RELEASE OF GAS. | CLASS 3 LOCATION | 276300 | 281818.6128803963349 | 2500 | 2549.9331603365575 | 5000 | 5099.866320673115 | 0 | 0 | COST OF METER SET AND EMERGENCY RESPONSE IS ESTIMATED FROM SIMILAR INCIDENTS. | 7.176 | 198 | 225.952941176470588235294117647058823529 | 0 | 0 | 283998 | 117725.4719842360729058823529411764705882 | 289694.3653025824779882352941176470588235 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 41 | 41 | 42 | 192.619(A)(2) | 1959-12-31 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2.6 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT BEING CAUSED BY OCCUPANT VANDALISM OF COMPANY PROPERTY. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [156 empty] | DANIEL C BLANCE | ENGINEER | dcblance@nyseg.com | 607-759-6453 |  |  |  |  | BARRY KACHMARYK | SENIOR MANAGER GAS ENGINEERING | 585-315-1227 | barry_kachmaryk@rge.com | THE ROCHESTER GAS &ELECTRIC (RG&E) CONTROL ROOM WAS NOTIFIED BY 911 OF A FIRE AT 154 THOMPSON RD. IN HENRIETTA, NY AT 03:40 ON 08/08/2024. THE RG&E CONTROL ROOM DISPATCHED EMERGENCY RESPONSE PERSONNEL IN ACCORDANCE WITH COMPANY PROCEDURES. THE RG&E CONTROL ROOM NOTIFIED THE NRC ON 08/08/2024 AT 10:56 (REPORT #1407285) AND PROVIDED THE REQUIRED 24-HOUR UPDATE TO THE NRC (REPORT #1409131). THERE ARE NO REPORTS OF INJURIES RELATED TO THE INCIDENT AND THE STRUCTURE WAS EXTENSIVELY DAMAGED BY FIRE. RG&E PERFORMED A LEAK SURVEY IN PROXIMITY TO THE INCIDENT IN ACCORDANCE WITH COMPANY O&M PROCEDURES AND NO UNDERGROUND LEAKS WERE IDENTIFIED. AS REPORTED TO A LOCAL NEWS STATION BY THE MONROE COUNTY SHERIFF'S OFFICE, "WHEN THE DEPUTIES ARRIVED, THEY LOCATED A PERSON STANDING IN THE FRONT YARD OF THE RESIDENCE. THE DEPUTIES STARTED TALKING WITH THAT PERSON. IT THEN BECAME VERY CLEAR THAT THE PERSON WAS SUFFERING A MENTAL HEALTH CRISIS. THE DEPUTIES WERE ABLE TO DETAIN HIM AND HE HAS SINCE BEEN TRANSPORTED UP TO ONE OF OUR LOCAL HOSPITALS FOR TREATMENT." FIRE/POLICE INVESTIGATORS DETERMINED THAT THE RG&E SERVICE REGULATOR WAS INTENTIONALLY DAMAGED BY THE RESIDENT AND, IN ADDITION, THE GAS METER WAS NOT LOCATED IN AN INITIAL SEARCH OF THE STRUCTURE.
2026-06-30 10:38 | NO | NO | NO | 20240050 | 40473 | 2024-09-11 13:36 | SUPPLEMENTAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2024-08-13 10:30 | CENTRAL | YES | 2024 | 6750 DANIEL BURNHAM DRIVE | PORTAGE | PORTER | IN | 46368 | 41.6021 | -87.1516 |  | YES |  |  |  | YES |  |  |  | 2024-08-14 09:30 | 1407900 | 1408121 | NATURAL GAS |  | 5541.69 | 2.32 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-08-13 10:36 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2024-08-13 10:45 | 2024-08-13 12:30 | 2024-08-14 09:17 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2002 | UNKNOWN |  |  |  |  | 8 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | UNKNOWN | OTHER | [8 empty] | MECHANICAL PUNCTURE BUT TWO PUNCTURES 4" X 5" AND 5" X 5" | CLASS 3 LOCATION | 17649 | 18001.508138711961327 | 14561 | 14851.830699064245503 | 23924 | 24401.840371156720652 | 500 | 509.9866320673115 | ADMIN FEE & POLICE REPORT | 2.34 | 12968 | 14798.7764705882352941176470588235294118 | 5 | 5.70588235294117647058823529411764705882 | 69607 | 35513.3630934043936907058823529411764706 | 72569.6481939414154525882352941176470589 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 50 | 50 | 60 | 192.619(A)(3) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS EVENT WAS DUE TO A THIRD-PARTY EXCAVATION DAMAGE AND DID NOT INVOLVE ANY PRESSURE REGULATING. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | OTHER | [5 empty] | YES |  |  | YES | YES | > 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2408055498 | INDIANA 811 | NO | CONTRACT LOCATOR | NO | YES | 12 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | JOHNESE MCKINNEY | MGR OPERATIONS COMPLIANCE AND RISK MANAGEMENT | johnesemckinney@nisource.com | 2197131771 |  | JOHNESE MCKINNEY | johnesemckinney@nisource.com | 2197131771 | JOHNESE MCKINNEY | MGR OPERATIONS COMPLIANCE AND RISK MANAGEMENT | 2197131771 | johnesemckinney@nisource.com | ON 8/13/2024 AT APPROXIMATELY 10:30 AM CENTRAL TIME, A THIRD-PARTY CONSTRUCTION CONTRACTOR WAS DIRECTIONAL BORING AND MADE CONTACT WITH AN UNMARKED 8" PLASTIC DISTRIBUTION MAIN IN AN EASEMENT ALONG A MAJOR HIGHWAY. NIPSCO CREWS RESPONDED AND STOPPED THE FLOW OF GAS BY CLOSING A MAIN VALVE AT ONE POINT AND SQUEEZING OFF THE MAIN AT ANOTHER POINT. THIS RESULTED IN AN OUTAGE OF (5) RESIDENTIAL CUSTOMERS. REPAIRS WERE MADE TO THE SECTION OF PIPE BY CUTTING OUT AND REPLACING WITH A NEW SECTION. ALL CUSTOMERS WERE RESTORED. THE DAMAGE OCCURRED DUE TO A CONTRACTOR LOCATOR MISREADING THE FACILITY PRINTS, WHICH RESULTED IN NOT LOCATING AND MARKING A SECTION OF PIPELINE. THIS CONTRACT LOCATE EMPLOYEE WILL NO LONGER BE PERFORMING WORK FOR NIPSCO AS THE REMEDIAL ACTION.
2026-06-30 10:38 | NO | YES | YES | 20240051 | 39988 | 2024-09-11 14:09 | ORIGINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2024-08-11 06:48 | EASTERN | YES | 2024 | 2300 ARTHURS WOODS DR | BEL AIR | HARFORD | MD | 21015 | 39.4862 | -76.3337 | [5 empty] | YES |  |  |  | 2024-08-11 08:50 | 1407546 | 1407800 | NATURAL GAS |  | 15.2 | 0 | YES | 0 | 1 | 0 | 0 | 1 | 2 | NO | [5 empty] | 0 | YES | 2024-08-11 06:48 | OPERATOR/CONTRACTOR |  | 2.53 | YES | 0 | 2024-08-11 06:35 | YES | OPERATOR | 2024-08-11 06:39 | 2024-08-11 07:12 | 2024-08-11 07:12 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 | YES | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2006 | 2004 | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.5 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 4710 | LEAK |  |  | OTHER | UNDER INVESTIGATION BY NTSB | [5 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TOTAL COSTS UNDER INVESTIGATION | 1.34 | 20 | 22.82352941176470588235294117647058823529 | 0 | 0 | 20 | 18.58823529411764705882352941176470588235 | 22.82352941176470588235294117647058823529 | 0 | 0 | 2 | 0 | 1 | 12 | 0 | 89 | 89 | 99 | 192.619(A)(2) | 2006-02-07 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT IS UNDER INVESTIGATION BY THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB). | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | JEFFREY WEATHERHOLTZ |  | jeffrey.weatherholtz@bge.com | [5 empty] | ROBERT REX |  | 302-593-3732 | robert.rex@bge.com | THIS INCIDENT IS UNDER INVESTIGATION BY THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB).
2026-06-30 10:38 | NO | NO | NO | 20240052 | 41203 | 2024-09-30 10:01 | SUPPLEMENTAL FINAL | 14330 | ORANGE & ROCKLAND UTILITY INC | ONE BLUE HILL PLAZA | PEARL RIVER | NY | 10965 | 2024-09-03 15:49 | EASTERN | YES | 2024 | 282 AVALON GARDEN | NANUET | ROCKLAND | NY | 10954 | 41.106 | -74.0209 |  |  | YES | [6 empty] | 2024-09-03 19:36 | 1409845 | 1410018 | NATURAL GAS |  | 18.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-09-03 15:35 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 14 | NO | 2 | 2024-09-03 15:59 | YES | OPERATOR | 2024-09-03 15:50 | 2024-09-03 15:59 | 2024-09-03 15:59 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1998 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES | 0.75 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | MECHANICAL PUNCTURE | 1.2 | 0.2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 5000 | 5099.866320673115 | 35000 | 35699.064244711805 | 0 | 0 | ESTIMATED OTHER COSTS ARE UNKNOWN | 1.68 | 31 | 35.37647058823529411764705882352941176471 | 0 | 0 | 40031 | 16595.6121106994423529411764705882352941 | 40834.3070359731552941176470588235294118 | 0 | 0 | 16 | 0 | 0 | 2 | 0 | 55 | 55 | 80 | 192.619(A)(2) | 1998-04-09 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [6 empty] | NO | YES | 18” – 36” |  | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 0826400219100 | UDIG | NO | CONTRACT LOCATOR | YES | YES | 5 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | PATRICK WALSH | MANAGER | walshp@oru.com | 8455773731 |  |  |  |  | PATRICK WALSH | MANAGER | 8455773731 | walshp@oru.com | ON SEPTEMBER 3, 2024, AT 1549 HRS., ORANGE AND ROCKLAND'S (O&R) GAS EMERGENCY RESPONSE CENTER (GERC) RECEIVED A REPORT OF A POSSIBLE DAMAGE TO A NATURAL GAS LINE AND A STRUCTURE FIRE AT 282 AVALON GARDENS DRIVE, LOCATED IN NANUET, NEW YORK, AN EIGHT-CONDOMINIUM BUILDING. AT 1549 HRS., THE GERC BEGAN DISPATCHING MULTIPLE O&R GAS CREWS TO THE LOCATION. AT 1547 HRS., TO MITIGATE POTENTIAL IGNITION SOURCES, O&R ELECTRIC CREWS DE-ENERGIZED ELECTRIC SERVICE TO 1,515 CUSTOMERS. AT 1559 HRS., O&R GAS CREWS BEGAN TO ARRIVE AT THE SCENE OF AN ACTIVE BUILDING FIRE AT 282 AVALON GARDENS DRIVE (BUILDING #28) AND BEGAN TO ASSESS THE SITUATION. UPON CONFIRMATION A GAS SERVICE HAD BEEN DAMAGED, AT 1647 HRS. O&R GAS CREWS CLOSED TWO CURB VALVES TO 282 AVALON GARDENS DRIVE (BUILDING #28) AND, AS A PRECAUTION, THE ADJACENT BUILDING #25, ISOLATING THE TWO GAS SERVICES THEREBY INTERRUPTING GAS SERVICE TO A TOTAL OF 16 GAS METERS. O&R'S INITIAL INVESTIGATION DETERMINED BORTECH COMPANY INC., A CONTRACTOR HIRED BY VERIZON, HIRED E&J PRO COMMUNICATION LLC (E&J) TO INSTALL A FIBER OPTIC CABLE CONDUIT. E&J WAS USING A PNEUMATIC TRENCHLESS TOOL KNOWN AS A "BULLET" (THE BULLET), WHICH DAMAGED A 3/4 INCH PLASTIC GAS SERVICE TO 282 AVALON GARDENS DRIVE. THE 3/4-INCH PLASTIC GAS SERVICE TO 282 AVALON GARDENS DRIVE (BUILDING 28) WAS LOCATED AND MARKED CORRECTLY. THE E&J EMPLOYEE ADMITTED THAT E&J DID NOT EXPOSE THE GAS OR ELECTRIC BY HAND TO VERIFY THE MARKED LOCATION PRIOR TO THE USE OF THE BULLET IN BOTH DIRECTIONS. THE BULLET WAS SHOT WITHIN THE TOLERANCE ZONE OF THE GAS SERVICE AS WELL AS THE GAS MAIN AND ELECTRIC PRIMARY. THIS IS A DIRECT VIOLATION OF NYS CODE RULE 753-3.6 - VERIFICATION OF UNDERGROUND FACILITIES. ADDITIONALLY E&J ARE IN VIOLATION OF NYS CODE RULE 753-3.10 - REQUIREMENTS CONCERNING CONTACT AND DAMAGE TO UNDERGROUND FACILITIES. E&J, WHILE OPERATING THE BULLET BELOW GRADE, STRUCK A HIGH-PRESSURE PLASTIC GAS SERVICE LINE OPERATING AT APPROXIMATELY 55 (PSIG). E&J REMOVED THE BULLET AND REALIZED THE BULLET HAD STRUCK THE SERVICE. THE E&J EMPLOYEE THAT WAS OPERATING THE BULLET STATED WITHIN 1-2 MINUTES THE ESCAPING GAS FROM THE SERVICE IGNITED. THE FIRE SEVERELY DAMAGED ALL EIGHT CONDOMINIUM UNITS IN BUILDING #28. THERE WERE NO FATALITIES AND NO INJURIES. AT APPROXIMATELY 2000 HRS., O&R CREWS CUT AND CAPPED THE REMAINING ONE GAS SERVICES (EIGHT GAS METERS) TO THE FIRE DAMAGED BUILDING (#28) AND AT APPROXIMATELY 2130 HRS. O&R GAS CREWS, AS A PRECAUTION, COMPLETED A PRESSURE TEST FOR 282 AVALON GARDENS DRIVE RULING OUT ANY PRE-EXISTING LEAKS. BY 2200 HRS., O&R GAS CREWS RESTORED THE EIGHT GAS METERS (ONE GAS SERVICE) TO BUILDING #25 AND BY 2208 HRS., O&R HAD RESTORED ELECTRIC SERVICE TO ALL CUSTOMERS (1,507), EXCEPT FOR THE EIGHT DAMAGED UNITS. THE FOLLOWING DAY (9/4/2024), O&R GAS CREWS PERFORMED A LEAK SURVEY YIELDING NO LEAKS FOUND. THE FIRE WAS INVESTIGATED BY THE TOWN OF CLARKSTOWN (POLICE DEPARTMENT ARSON UNIT AND FIRE INSPECTION UNIT) LOCATED IN NEW CITY, NEW YORK. NOTES: 1. AT THIS TIME, THE ESTIMATED COST OF PUBLIC AND NON-OPERATOR PRIVATE PROPERTY DAMAGE PAID/REIMBURSED BY THE OPERATOR AND THE ESTIMATED OTHER COSTS IS UNKNOWN. 2. RE: Q21A. ESTIMATED TIME BASED UPON WHEN 44-CONTROL (ROCKLAND COUNTY EMERGENCY DISPATCH) WAS NOTIFIED A GAS LINE WAS STRUCK AND THE BUILDING WAS ON FIRE.
2026-06-30 10:38 | NO | YES | NO | 20240053 | 40064 | 2024-10-03 15:32 | ORIGINAL | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | NY | 12601 | 2024-09-03 13:12 | EASTERN | YES | 2024 | 6 CREST CT | HOPEWELL JUNCTION | DUTCHESS COUNTY | NY | 12533 | 41.5728 | -73.8362 | YES | [6 empty] | YES | VALVES ON TRANSMISSION PIPELINE INSPECTED WITH PART 192.745 | 2024-09-03 16:04 | 1409823 | 1410110 | NATURAL GAS |  | 3078 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-09-03 13:12 | ALLOWED TO BURN OUT |  | 3078 | YES | 14 | 2024-09-03 13:12 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2024-09-03 13:12 | 2024-09-03 13:12 | 2024-09-03 13:12 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2002 | 2002 | [7 empty] | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.28 | [6 empty] | OTHER | [8 empty] | RELIEF VALVE AT REGULATOR STATION OPERATED. | CLASS 3 LOCATION | 10680 | 10893.31446095777364 | 752810 | 767846.07297318554063 | 549013 | 559978.581662341777099 | 0 | 0 |  | 3.7693 | 11602 | 13239.9294117647058823529411764705882353 | 0 | 0 | 1324105 | 554382.4141570572840758235294117647058824 | 1351957.89850824979725135294117647058824 | 37 | 0 | 454 | 1 | 0 | 37 | 454 | 122.67 | 114 | 120 | 192.619(A)(2) | 2002-09-25 | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE COMPANY PERSONNEL ON SITE THAT WERE AWARE OF WHAT HAPPENED AND THE CONTROL ROOM WAS NOT THE CAUSE OR CONTRIBUTING FACTOR. | [12 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [222 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED |  |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | JERRY R AMATO | DIRECTOR OF GAS COMPLIANCE | jamato@cenhud.com | 8454163887 |  | JERRY R AMATO | jamato@cenhud.com | 8454163887 | ERIC KISZKIEL | VICE PRESIDENT OF GAS ENGINEERING AND OPERATIONS | 845-486-5472 | ekiszkiel@cenhud.com | ON TUESDAY SEPTEMBER 3, 2024, TWO CENTRAL HUDSON GAS MECHANICS WERE PERFORMING A MONTHLY REGULATOR STATION INSPECTION AT THE HOPEWELL GAS REGULATOR STATION NEAR 6 CREST CT. HOPEWELL JUNCTION NY. THE REGULATOR STATION IS CONSTRUCTED WITH TWO REGULATOR RUNS IN PARALLEL WITH ONE RELIEF VALVE SERVING AS THE OVERPRESSURE PROTECTION DEVICE. THE REGULATOR STATION REDUCES PRESSURE FROM THE MP TRANSMISSION PIPELINE (MAOP 750 PSIG) TO 120 PSIG TO SERVE THE HH GAS DISTRIBUTION SYSTEM. THE TRANSMISSION PIPELINE WAS OPERATING AT APPROXIMATELY 425 PSIG AND THE DISTRIBUTION SYSTEM AT APPROXIMATELY 114 PSIG AT THE TIME OF THE INCIDENT. THE REGULATOR STATION IS LOCATED IN CLOSE PROXIMITY TO OVERHEAD TRANSMISSION ELECTRIC LINES. DURING THE MONTHLY INSPECTION, A LEAK ON A FITTING AT THE VORTEX HEATER WAS DISCOVERED. THE GAS MECHANIC DECIDED TO ISOLATE THE VORTEX HEATER TO MAKE THE NECESSARY REPAIRS. DURING THE ATTEMPT TO ISOLATE THE HEATER, THE GAS MECHANIC CLOSED A SERIES OF VALVES ON THE PILOT SUPPLY LINE OF THE REGULATOR WHICH CAUSED THE REGULATOR TO GO WIDE OPEN. AS A RESULT, THE PRESSURE DOWNSTREAM OF THE REGULATOR INCREASED AND EXCEEDED THE SET PRESSURE OF THE RELIEF VALVE. THE RELIEF VALVE OPERATED AND BEGAN TO VENT NATURAL GAS TO ATMOSPHERE. SHORTLY AFTER THE GAS STARTED VENTING, THE RELEASED GAS FROM RELIEF VALVE STACK IGNITED. THE INTENSITY OF THE PRESSURE AND HEAT FROM THE FLAME POSED AN IMMEDIATE DANGER TO BOTH GAS MECHANICS ON SITE. THE EMPLOYEES WERE ABLE TO SAFELY EXIT THE STATION AND ALERT SURROUNDING RESIDENCES AND EMERGENCY SERVICES, AND EVACUATE PEOPLE FROM THEIR HOMES. ONE GAS MECHANIC WENT TO THE HOSPITAL FOR EVALUATION AS A PRECAUTION. THE NUMBER OF EVACUATIONS PROVIDED IN THIS REPORT IS ESTIMATED AND IS BASED ON THE NUMBER OF BUILDINGS ON CREST CT. SHORTLY AFTER THE NATURAL GAS IGNITION, THE OVERHEAD ELECTRIC BURNT AND FELL TO THE GROUND ADJACENT TO THE REGULATOR STATION. THE ELECTRIC DEPARTMENT WAS CONTACTED AND RESPONDED TO REMEDIATE THE HAZARD. TO EXTINGUISH THE FIRE, THE REGULATOR STATION WAS ISOLATED FROM ALL SOURCES OF GAS BY CLOSING TRANSMISSION LINE VALVES ON THE MP PIPELINE AND CLOSING A DISTRIBUTION LINE VALVE ON THE HH LINE. THE FIRE EXTINGUISHED ITSELF ONCE THE GAS SUPPLY RAN OUT. NATURAL GAS CUSTOMERS SERVED FROM THE HH PIPELINE WERE NOT INTERRUPTED AS THIS PIPELINE IS SERVED BY ADDITIONAL NATURAL GAS REGULATOR STATIONS. THE 491 CUSTOMERS THAT WERE INTERRUPTED WERE FED FROM DIFFERENT REGULATOR STATIONS FED FROM THE MP LINE WITHIN THE ISOLATION ZONE THAT WAS BLOWN DOWN. THE MAJORITY WERE RESTORED THE NEXT DAY.
2026-06-30 10:38 | NO | YES | NO | 20240054 | 40566 | 2024-10-12 09:25 | SUPPLEMENTAL FINAL | 13635 | NORTHEAST OHIO NATURAL GAS CORP | 5640 LANCASTER NEWARK RD NE | PLEASANTVILLE | OH | 43148 | 2024-09-11 10:26 | EASTERN | YES | 2024 | SOUTHWEST CORNER OF INTERSECTION - SAINT CLAIR AND LOST NATION RD | WILLOUGHBY | LAKE | OH | 44060 | 41.653 | -81.4043 | [6 empty] | YES |  |  | 2024-09-13 08:49 | 1410698 | 1410979 | NATURAL GAS |  | 5194.77 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-09-11 21:30 | YES | OPERATOR | 2024-09-11 10:31 | 2024-09-11 10:50 | 2024-09-11 21:30 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 84 | YES | YES |  |  |  |  | YES | CASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.237 | [6 empty] | LEAK |  |  | OTHER | HOLE IN PIPE | [5 empty] | CLASS 2 LOCATION | 50000 | 50998.66320673115 | 100000 | 101997.3264134623 | 250000 | 254993.31603365575 | 0 | 0 |  | 4.3252 | 22468 | 25639.9529411764705882352941176470588235 | 0 | 0 | 422468 | 186550.0269893473647058823529411764705882 | 433629.2585950256705882352941176470588235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 500 | 192.621 M | 2019-12-04 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [136 empty] | YES | [10 empty] | YES | [20 empty] | JOSHUA SMITH | STRATEGIC ADVISOR COMPLIANCE | joshua.d.smith@neogas.com | 304-533-1865 |  | MARK LOWER | mlower@neogas.com | 740-400-9559 | SCOTT WALLACE | DIRECTOR PIPELINE SAFETY AND COMPLIANCE | 304-844-1256 | scott.a.wallace@hopegas.com | ODOR CALL RECEIVED AND DISPATCHED TO TECHNICIAN ON 9/11/2024. INVESTIGATION INTO LEAK RESULTED IN NATURAL FORCE DAMAGE. A STORM BLEW A POWER LINE DOWN OVER CROSSING OF CASING. POWER TRAVELED THROUGH GROUND TO CASING, WHERE PIPE EXITED CASING, IT ARCED A HOLE IN PIPE. CREWS SECURED SITE AND MONITORED LEAK CONTINUOUSLY UNTIL REPAIRS WERE MADE ON 9/20/2024 WITH PIPELINE REPLACEMENT. PIPELINE REPLACEMENT WAS PRESSURE TESTED PER 192.619 TO ESTABLISH MAOP.
2026-06-30 10:38 | NO | YES | NO | 20240055 | 40602 | 2024-10-23 20:21 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2024-09-22 09:47 | EASTERN | NO | 2024 | INTERSECTION OF BEDFORD PARK BLVD AND WEBSTER AVENUE | NEW YORK | BRONX | NY | 10458 | 40.868 | -73.8843 |  | YES | [7 empty] | 2024-09-22 15:35 | 1411748 | 141585 | NATURAL GAS |  | 16985 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-09-22 09:47 |  |  |  | 2024-09-22 09:57 | 2024-09-22 10:00 | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1977 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 738648 | 753401.211606511009704 | 37148 | 37889.966816072975204 | 0 | 0 |  | 1.55 | 26327 | 30043.7529411764705882352941176470588235 | 0 | 0 | 802123 | 345780.0595599222615498823529411764705882 | 821334.9313637604554962352941176470588235 | 0 | 0 | 31 | 0 | 3 | 31 | 0 | 64 | 64 | 89 | 192.619(A)(1) | 2015-03-26 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NON-RESTRAINING COUPLING LEAKED CAUSING A BLOWING GAS CONDITION | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | [197 empty] | NON-THREADED CONNECTION FAILURE | [14 empty] | OTHER | NON-RESTRAINING COUPLING | [67 empty] | RYAN BOULA | DEPARTMENT MANAGER | boular@coned.com | 646-941-0423 |  | RYAN BOULA | boular@coned.com | 6469410423 | RYAN BOULA |  | 6469410423 | boular@coned.com | ON 9/22/24 AT 09:47, THE FIRE DEPARTMENT OF THE CITY OF NEW YORK (FDNY) CALLED CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) AND REPORTED THAT THEY WERE ON LOCATION WITH A RUPTURED GAS MAIN AT THE INTERSECTION OF BEDFORD PARK BOULEVARD AND WEBSTER AVENUE IN THE BRONX. CON EDISON'S GERC IMMEDIATELY INITIATED A MULTIPLE RESOURCE RESPONSE EVENT (CODE MURRE) AND DISPATCHED MULTIPLE PERSONNEL TO THE LOCATION FROM SEVERAL DEPARTMENTS, INCLUDING GAS DISTRIBUTION SERVICES (GDS), GAS EMERGENCY RESPONSE FORCE (ERF) CONSTRUCTION, LEAK SURVEY, AND ITS GAS EMERGENCY RESPONSE GROUP (ERG). AT 09:47, CON EDISON'S GAS CONTROL GROUP REPORTED RECEIVING A LOW-PRESSURE ALARM AT GAS REGULATOR STATION GR-110, WHICH SUPPLIES THE SAME AREA. CON EDISON GDS PERSONNEL ARRIVED ON LOCATION AT 09:57 AND BEGAN INVESTIGATING. THE FDNY WAS ALREADY ON LOCATION. AT 10:00, GDS PERSONNEL REPORTED A BLOWING GAS CONDITION FROM UNDER A STEEL PLATE AT THE INTERSECTION OF BEDFORD PARK BOULEVARD AND WEBSTER AVENUE. AT 10:07, CON EDISON'S GERC IDENTIFIED HIGH-PRESSURE MAIN VALVES (7707, 7708 AND 8740) FOR ISOLATING THE HIGH-PRESSURE STEEL GAS SUPPLY MAIN AT THAT LOCATION (12-INCH STEEL, INSTALLED IN 1977). AT 12:00, GDS CLOSED THE MAIN VALVES, THEREBY ISOLATING THE AFFECTED SUPPLY MAIN AND ELIMINATING THE BLOWING GAS CONDITION. THE INCIDENT RESULTED IN 31 SERVICE LINE INTERRUPTIONS AFFECTING 767 CUSTOMERS WITH NO OTHER SYSTEM IMPACT. CON EDISON RECEIVED A TOTAL OF NINETY-FOUR (94) RELATED GAS ODOR COMPLAINTS. CON EDISON INVESTIGATED EACH COMPLAINT AND FOUND ALL TO BE ASSOCIATED WITH THE INCIDENT. CON EDISON'S GAS ENGINEERING GROUP DETERMINED THAT APPROXIMATELY SEVENTEEN MILLION CUBIC FEET OF NATURAL GAS WAS LOST DURING THE INCIDENT. THREE MEMBERS OF THE PUBLIC WERE TRANSPORTED TO AN UNKNOWN HOSPITAL WITH ILLNESSES POTENTIALLY RELATED TO THE INCIDENT. REPAIRS WERE MADE AND CUSTOMERS WERE FULLY RESTORED AT 17:25 ON 9/24/2024. CON EDISON NOTIFIED THE DEPARTMENT OF PUBLIC SERVICE STAFF (DPS STAFF), THE NEW YORK CITY DEPARTMENT OF ENVIRONMENTAL PROTECTION (NYCDEP), AND THE U.S. DEPARTMENT OF TRANSPORTATION (USDOT). MULTIPLE MEDIA OUTLETS WERE ON LOCATION DURING THE INCIDENT.
2026-06-30 10:38 | NO | NO | NO | 20240056 | 40167 | 2024-10-29 15:21 | SUPPLEMENTAL FINAL | 4473 | ATMOS ENERGY CORPORATION - WEST TEXAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2024-09-30 08:00 | CENTRAL | NO | 2024 | 6012 77TH ST | LUBBOCK | LUBBOCK | TX | 79424 | 33.5244 | -101.9456 | [5 empty] | YES |  |  |  | 2024-09-30 10:14 | 1412353 |  | NATURAL GAS |  | 108 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-09-30 08:00 | ALLOWED TO BURN OUT |  | 108 | NO | 1 | 2024-09-30 08:33 |  |  |  | 2024-09-30 08:55 | 2024-09-30 09:33 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1991 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | OTHER | THREADED CONNECTION | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | STRUCK BY VEHICLE | [5 empty] | CLASS 1 LOCATION | 20000 | 20399.46528269246 | 200 | 203.9946528269246 | 14500 | 14789.6123299520335 | 80000 | 81597.86113076984 | CEMENT TRUCK | 1.49 | 161 | 183.729411764705882352941176470588235294 | 0 | 0 | 114861 | 47654.9352862541803588235294117647058824 | 117174.6628080059639823529411764705882353 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 40 | 40 | 44 | 192.619(A)(1) | 1991-09-05 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | NO | UNKNOWN | LARGE TRUCK | ROADWAY | 3 | NO | [118 empty] | YES | [23 empty] | DUSTIN CROSLEY |  | dustin.crosley@atmosenergy.com | 8062905751 |  | EJAY NAVARRETTE | ejay.navarrette@atmosenergy.com | 806-702-4806 | DUSTIN CROSLEY |  | 8062905751 | dustin.crosley@atmosenergy.com | AT 9:33 AM ATMOS ENERGY WEST TEXAS CONFIRMED DISCOVERY. A THIRD-PARTY VEHICLE OPERATOR WAS OUTSIDE OF THE VEHICLE WHEN CLEANING WHILE PARKED IN AN ALLEY. THE VEHICLE WAS NOT SECURELY PARKED RESULTING IN THE VEHICLE ACCELERATING FORWARD INTO A RESIDENTIAL GAS METER AND CAUSING AN IGNITION OF GAS.
2026-06-30 10:38 | NO | YES | NO | 20240057 | 41427 | 2024-11-07 14:49 | SUPPLEMENTAL FINAL | 13535 | NORTH ALABAMA GAS DISTRICT | 602 DEARBORN AVENUE | MUSCLE SHOALS | AL | 35661 | 2024-10-15 09:42 | CENTRAL | NO | 2024 | 136 BELMONT PLACE | MADISON | LIMESTONE | AL | 35756 | 34.7215 | -86.7895 |  | YES | [7 empty] | 2024-11-01 15:13 | 1415342 |  | NATURAL GAS |  | 6.5 | 3 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-10-15 09:47 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 6 | NO | 3 | 2024-10-15 09:47 |  |  |  | 2024-10-15 09:57 | 2024-10-30 14:27 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 2005 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | ASTM D2513 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 0.2 | 1 | [7 empty] | CLASS 4 LOCATION | 200000 | 203994.6528269246 | 92 | 93.837540300385316 | 6085 | 6206.537312259180955 | 0 | 0 |  | 4.46 | 29 | 33.09411764705882352941176470588235294118 | 13 | 14.83529411764705882352941176470588235294 | 206219 | 85431.3651675155025618235294117647058823 | 210342.9570912488721533529411764705882353 | 0 | 0 | 128 | 0 | 0 | 128 | 0 | 45 | 45 | 60 | 192.619(A)(2) | 2005-03-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES |  |  | YES | PRIVATE LANDOWNER | [6 empty] | NO | NO | MEASURED DEPTH FROM GRADE | 18 | CONTRACTOR | AUGER | UNKNOWN/OTHER | NO |  |  |  | FACILITY OWNER | NO | YES | 2 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | ERIC SMITH | TECHNICAL SERVICES DIRECTOR | esmith@nagd.com | 2563491473 |  | DAVID MCCARLEY | dmccarley@nagd.com | 256-509-3309 | ERIC SMITH | TECHNICAL SERVICES DIRECTOR | 2563491473 | esmith@nagd.com | TERMITE CONTRACTOR WAS SETTING TERMITE TEST STATIONS WITH HANDHELD POWER AUGER. CONTRACTOR FAILED TO CALL IN LOCATES PRIOR TO DIGGING. DAMAGED 3/4" SERVICE LINE IN CLOSE PROXIMITY TO HOUSE, SPECIFICALLY THE ELECTRIC METER. AFTER A SHORT TIME BLOWING GAS IGNITED, SPREADING TO THE HOUSE, MAINLY THE ATTIC AREA. REIGNITION OCCURRED AFTER ATTEMPTING TO EXTINGUISH THE FIRE SO NORTH ALABAMA GAS PERSONNEL CLOSED A MAIN LINE VALVE FEEDING THE SUBDIVISION. SERVICE LINE WAS EVENTUALLY CAPPED UPSTREAM OF THE DAMAGE AND SERVICE WAS RESTORED TO THE SUBDIVISION AT 11:13 A.M. ON 10/15/24.
2026-06-30 10:38 | NO | YES | NO | 20240058 | 40217 | 2024-11-14 08:43 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2024-10-15 17:36 | EASTERN | YES | 2024 | 5992 COLBY HUNT COURT | HAYMARKET | PRINCE WILLIAM | VA | 20169 | 38.8284 | -77.6241 | [5 empty] | YES |  |  |  | 2024-10-15 18:21 | 1413814 | 1413954 | NATURAL GAS |  | 84.25 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-10-15 17:36 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 84.25 | YES | 20 | 2024-10-15 16:32 |  |  |  | 2024-10-15 17:14 | 2024-10-15 17:36 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 46 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2000 | UNKNOWN |  |  |  |  | 2 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 0.4 | 2.2 | [7 empty] | CLASS 3 LOCATION | 800000 | 815978.6113076984 | 542 | 552.825509160965666 | 12092 | 12333.516709915861316 | 0 | 0 |  | 3.24 | 273 | 311.541176470588235294117647058823529412 | 0 | 0 | 812907 | 336822.3602209179718083529411764705882353 | 829176.4947032458152172941176470588235294 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 55 | 55 | 60 | 192.619(A)(1) | 2000-06-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.6 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MECHANICAL DAMAGE DUE TO THIRD PARTY DIRECTIONAL DRILL. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [6 empty] | NO | NO | > 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | WATER | YES | A428900415 |  | Unknown | CONTRACT LOCATOR | YES | YES | 25 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | MARK AIESI | SUPERVISOR | mark.aiesi@washgas.com | 5714054623 |  |  |  |  | STACEY FORD | VP EHS- UTILITIES | 5716517504 | stacey.ford@washgas.com | ON OCTOBER 15, 2024, AT APPROXIMATELY 1617, BLANKENSHIP UTILITIES, A CONTRACTOR DIRECTIONALLY DRILLING A WATER LINE, STRUCK A 2" MAIN LOCATED AT 5992 COLBY HUNT COURT, HAYMARKET VIRGINIA. WASHINGTON GAS WAS NOTIFIED AT 1632 VIA FIREBOARD OF THE THIRD PARTY DAMAGE. THE RESULTING DAMAGE, WHICH WAS A MECHANICAL PUNCTURE OF THE MAIN, CAUSED A GAS LEAK. THE FIRST WASHINGTON GAS CREW ARRIVED AT 1714. SUBSEQUENTLY, GAS MIGRATED INTO THE HOUSE LOCATED AT 5992 COLBY HUNT COURT, FOUND AN UNKNOWN IGNITION SOURCE, AND AT APPROXIMATELY 1736 AN EXPLOSION OCCURRED AT 5992 COLBY HUNT COURT. WASHINGTON GAS STOPPED THE FLOW OF GAS BY SQUEEZING OFF THE MAIN AT 1847, CREATING AN OUTAGE OF 8 CUSTOMERS. CREWS HAVE RESTORED GAS SERVICE TO THE AREA. THERE WERE NO INJURIES FROM THIS INCIDENT.
2026-06-30 10:38 | NO | YES | NO | 20240059 | 40495 | 2024-11-15 15:25 | SUPPLEMENTAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2024-10-18 10:27 | CENTRAL | YES | 2024 | 6701 N. FM 620 | AUSTIN | TRAVIS | TX | 78732 | 30.3984 | -97.8566 | [6 empty] | YES |  |  | 2024-10-18 15:29 | 1414094 | 1414235 | NATURAL GAS |  | 26258 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-10-18 11:06 |  |  |  | 2024-10-18 11:06 | 2024-10-18 14:45 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 50 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2006 | UNKNOWN |  |  |  |  | 8.625 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 3.5 | 2.5 | [7 empty] | CLASS 3 LOCATION | 25714 | 26227.592513957695822 | 108146 | 110306.028623102938958 | 90909 | 92724.749469214442307 | 82137 | 83777.543996225529351 | ADMINISTRATIVE COSTS. | 4.58 | 120262 | 137240.1647058823529411764705882352941176 | 0 | 0 | 427168 | 238884.1783217463116634117647058823529412 | 450276.0793083829593791764705882352941176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 238 | 265 | 192.621 M | 2006-11-14 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSE WAS RELATED TO THIRD PARTY DAMAGE OF THE PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [8 empty] | NO | YES | MEASURED DEPTH FROM GRADE | 50 | CONTRACTOR | DIRECTIONAL DRILLING | PUBLIC TRANSIT AUTHORITY | NO |  |  |  | FACILITY OWNER | NO | NO |  | NOTIFICATION ISSUE | EXCAVATOR DUG OUTSIDE AREA DESCRIBED ON TICKET | [143 empty] | YES | [26 empty] | BRYAN WEEKS | DIRECTOR OF ENGINEERING | bryan.weeks@onegas.com | 5124071529 | 5124651133 |  |  |  | BRYAN WEEKS | DIRECTOR OF ENGINEERING | (512) 407-1529 | bryan.weeks@onegas.com | THIRD-PARTY CONTRACTOR WORKING ON BEHALF OF THE STATE HIGHWAY AUTHORITY INSTALLING CABLING FOR TRAFFIC CAMERAS DAMAGED TEXAS GAS SERVICE (TGS) 8-INCH HIGH-PRESSURE STEEL DISTRIBUTION MAIN WHILE HORIZONTAL DIRECTIONAL DRILLING (BORING). THE TGS PIPELINE WAS LOCATED OUTSIDE OF THE HORIZONTAL LIMITS OF THE CONTRACTOR'S ONE-CALL TICKET AND WAS THEREFORE NOT LOCATED.
2026-06-30 10:38 | NO | YES | YES | 20240060 | 40245 | 2024-11-21 17:30 | ORIGINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2024-10-23 10:30 | CENTRAL | YES | 2024 | 133 W. 147TH STREET | HARVEY | COOK | IL | 60426 | 41.6231 | -87.6639 | [5 empty] | YES |  |  |  | 2024-10-23 14:56 | 1414507 | 1414770 | NATURAL GAS |  | 28 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 4 | 4 | YES | 2024-10-23 10:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 28 | NO | 0 | 2024-10-23 10:56 |  |  |  | 2024-10-23 11:23 | 2024-10-23 11:23 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1981 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | OTHER | ALUMINUM / STEEL | [9 empty] | OTHER | [8 empty] | VEHICLE DROVE INTO AND OVER THE TOP OF A METER SET, CAUSING AN UNCONTROLLED RELEASE OF GAS. | CLASS 3 LOCATION | 133000 | 135656.444129904859 | 200 | 203.9946528269246 | 2374 | 2421.416529055595002 | 0 | 0 |  | 2.8 | 78 | 89.01176470588235294117647058823529411765 | 0 | 0 | 135652 | 56223.1788703403314095294117647058823529 | 138370.8670764932609549411764705882352941 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 24 | 25 | 28 | 192.619(A)(2) | 1998-07-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | YES | UNKNOWN | PASSENGER CAR | ROADWAY | 150 | NO | [142 empty] | PAMELA L. REID | MANAGER - COMPLIANCE AND QA | preid@southernco.com | 2244570663 |  | PAMELA L. REID, ASQ CMQ/OE | preid@southernco.com | 2244570663 | PAMELA L. REID | MANAGER - COMPLIANCE AND QA | 2244570663 | preid@southernco.com | TWO PASSENGER VEHICLES WERE REPORTEDLY STREET RACING EASTBOUND ON W. 147TH STREET IN HARVEY WHEN ONE OF THE DRIVERS LOST CONTROL OF THEIR VEHICLE. THE VEHICLE CROSSED OVER THE CENTERLINE DIVIDER, THE ONCOMING LANE(S) OF TRAFFIC, AND ONTO PRIVATE PROPERTY. THE VEHICLE STRUCK THE GAS METER OUTSIDE OF THE UNIVERSAL KINGDOM OF GOD HOUSE OF ISRAEL TEMPLE. THE MAJORITY OF DAMAGE WAS NOT CAUSED BY FIRE (BRICK) BUT BY STRUCTURAL DAMAGE FROM THE COLLISION; THE BUILDING WAS LATER DEMOLISHED. THE VEHICLE AND METER SET BOTH IGNITED, RESULTING IN INJURIES TO FOUR PASSENGERS. ONE OF THE PASSENGERS WAS TRANSPORTED TO THE LOYOLA BURN CENTER IN MAYWOOD. THE OTHER THREE WERE TRANSPORTED TO AREA HOSPITALS. DUE TO THE FEDERAL HIPAA LAW THAT PROTECTS THE PRIVACY AND SECURITY OF HEALTH INFORMATION, NICOR GAS WAS UNABLE TO GATHER ANY ADDITIONAL INFORMATION ON THOSE INJURED, NOR DO WE KNOW FOR CERTAIN ALL FOUR PASSENGERS REQUIRED OVERNIGHT HOSPITALIZATION.
2026-06-30 10:38 | NO | YES | NO | 20240061 | 40587 | 2024-11-22 08:42 | SUPPLEMENTAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2024-10-24 08:44 | CENTRAL | YES | 2024 | 6174 OLD US HWY 27 | PLEASANT LAKE | STEUBEN | IN | 46779 | 41.5536 | -85.0053 | [6 empty] | YES |  |  | 2024-10-25 16:33 | 1414774 | 1414894 | NATURAL GAS |  | 3312 | 0.84 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2024-10-24 09:36 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2024-10-24 09:36 | 2024-10-24 09:36 | 2024-10-25 16:00 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | 0.28 | [6 empty] | MECHANICAL PUNCTURE | 2.5 | 0.1 | [7 empty] | CLASS 1 LOCATION | 98429 | 100394.948415506807267 | 194215 | 198094.107493905805945 | 42112 | 42953.114099237243776 | 3413 | 3481.168750491468299 | ADMINISTRATIVE FEE & TAXES | 2.126 | 7041 | 8035.023529411764705882352941176470588235 | 2 | 2.28235294117647058823529411764705882353 | 345212 | 146605.3047139309342027647058823529411765 | 352960.644641494266463470588235294117647 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 194 | 195 | 250 | 192.621 M | 1969-06-15 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY EXCAVATOR DAMAGE AND DURING THE INCIDENT PRESSURE DID NOT BREECH ALARM LIMITS | [12 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [5 empty] | YES |  |  | NO | NO | MEASURED DEPTH FROM GRADE | 48 | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 2410214968 |  | NO | CONTRACT LOCATOR | YES | YES | 17 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | JOHNESE MCKINNEY | MGR OPERATIONS COMPLIANCE AND RISK MANAGEMENT | johnesemckinney@nisource.com | 2197131771 |  | JOHNESE MCKINNEY | johnesemckinney@nisource.com | 2197131771 | JOHNESE MCKINNEY | MGR OPERATIONS COMPLIANCE AND RISK MANAGEMENT | 2197131771 | johnesemckinney@nisource.com | ON OCTOBER 24TH AT APPROXIMATELY 9:36AM, NIPSCO DISPATCH WAS NOTIFIED BY THE SECOND PARTY EXCAVATOR, THAT THE EXCAVATOR HAD STRUCK A 6" HP DISTRIBUTION STEEL LINE THAT RESULTED IN A RELEASE OF GAS. NIPSCO CREWS RESPONDED AND STOPPED THE FLOW OF GAS USING STOPPLE FITTINGS. TWO RESIDENCES WERE EVACUATED AND THE SAME TWO HOMES WERE WITHOUT GAS UPON STOPPING. THE EXCAVATOR FAILED TO MAINTAIN PROPER DIG CLEARANCE WHILE USING BACKHOE EQUIPMENT. THIS 2ND PARTY OPERATOR WILL NO LONGER BE PERFORMING WORK FOR NIPSCO AS THE REMEDIAL ACTION.
2026-06-30 10:38 | NO | YES | NO | 20240062 | 40271 | 2024-11-29 14:59 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2024-10-31 16:31 | EASTERN | NO | 2024 | BEHIND 93 JOY AVE. | DELAWARE | DELAWARE | OH | 43015 | 40.3075 | -83.0533 | [6 empty] | YES |  |  | 2024-11-01 09:07 | 1415283 | 1415407 | NATURAL GAS |  | 29616 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 44 | 2024-10-31 16:31 | YES | OPERATOR | 2024-10-31 17:02 | 2024-10-31 17:02 | 2024-11-01 08:41 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1968 | UNKNOWN |  |  |  |  | 10 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.31 | [6 empty] | MECHANICAL PUNCTURE | 8 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 10001 | 10200.752614610364623 | 108696 | 110867.013918376981608 | 0 | 0 |  | 5.04 | 149265 | 170337.7058823529411764705882352941176471 | 0 | 0 | 267962 | 187889.3845755334691947647058823529411765 | 291405.4724153402874074705882352941176471 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 225 | 225 | 240 | 192.619(A)(3) | 1990-04-16 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLED IDENTIFIED THE ISSUE WHEN THEY OBSERVED A LOW ALARM AND SENT FIELD RESOURCES TO IMMEDIATELY TO INVESTIGATE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [6 empty] | NO | NO | < 18” |  | DEVELOPER | BULLDOZER | GRADING | YES | A42990246900 | OHIO 811 | NO | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | rrsmith@nisource.com | 1-614-460-5491 |  | ROB R. SMITH | rrsmith@nisource.com | 1-614-460-5491 | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | 1-614-460-5491 | rrsmith@nisource.com | ON OCTOBER 31, 2024, A THIRD-PARTY EXCAVATOR OPERATING A BULLDOZER DAMAGED A PROPERLY LOCATED AND MARKED 10-INCH STEEL MAIN LINE. COLUMBIA GAS OF OHIO, INC. ("COLUMBIA") TOOK IMMEDIATE ACTION TO REPAIR THE LEAK AND SET UP A PERIMETER AND BEGAN MONITORING THE LEAK. COLUMBIA MONITORED THE LEAK AS IT REMAINED NON-HAZARDOUS AND WELDED TWO 10-INCH STOPPLE FITTINGS ON THE MAIN LINE TO BYPASS THE DAMAGE FOR PERMANENT REPAIRS. THE PERMANENT REPAIRS WERE MADE, AND THE BYPASSED SECTION WAS PLACED BACK IN SERVICE ON NOVEMBER 1, 2024. PLEASE CONSIDER THIS A FINAL REPORT.
2026-06-30 10:38 | NO | YES | YES | 20240063 | 40599 | 2024-12-06 08:15 | SUPPLEMENTAL | 12876 | ENBRIDGE GAS UTAH/ WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2024-11-06 15:13 | MOUNTAIN | NO | 2024 | 10593 S 3210 W | SOUTH JORDAN | SALT LAKE | UT | 84095 | 40.5587 | -111.9678 |  |  |  | YES | YES | YES |  |  |  | 2024-11-06 18:44 | 1415759 | 1415924 | NATURAL GAS |  | 108 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2024-11-06 15:13 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 2 | 2024-11-06 15:40 |  |  |  | 2024-11-06 15:40 | 2024-11-06 16:25 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNDER INVESTIGATION WITH THE NTSB | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNDER INVESTIGATION WITH THE NTSB | CLASS 3 LOCATION | 1000000 | 1019973.264134623 | 0 | 0 | 30000 | 30599.19792403869 | 0 | 0 |  | 4.1 | 443 | 505.541176470588235294117647058823529412 | 0 | 0 | 1030443 | 427006.8383210988758823529411764705882353 | 1051078.00323513227823529411764705882353 | 0 | 0 | 2 | 0 | 0 | 4 | 0 | 43 | 43 | 60 | 192.619(A)(2) | 2013-06-25 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 5.8 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | STEVE BURSETT | SUPERVISOR GAS OPERATIONS | steve.bursett@dominionenergy.com | 801-548-7520 |  | STEVE BURSETT | steve.bursett@dominionenergy.com | 801-548-7520 | RYAN JAMISON | MANAGER GAS OPERATIONS | 801-574-0111 | ryan.jamision@dominionenergy.com | ON NOVEMBER 6, 2024, AT APPROXIMATELY 3:13 P.M., A NATURAL GAS-FUELED EXPLOSION FATALLY INJURED ONE PERSON AND DESTROYED A HOME LOCATED AT 10593 S 3210 W, SOUTH JORDAN, UTAH. THERE WERE NO OTHER INJURIES REPORTED. THIS INCIDENT IS CURRENTLY UNDER INVESTIGATION BY THE NTSB. SEE NTSB PRELIMINARY REPORT FOR ADDITIONAL DETAILS (PLD25FR001). ENBRIDGE GAS UTAH (EGU) WAS ABLE TO DISCOVER AND ISOLATE A NEARBY LEAK ROUGHLY 150 FEET NORTHEAST OF THE HOME ON A 4-INCH DIAMETER ALDYL-A NATURAL GAS MAIN AT 12:16 P.M. ON NOVEMBER 7. THE ALDYL-A MAIN WAS MANUFACTURED AND INSTALLED IN 1976 AND OPERATED AT A PRESSURE OF ABOUT 45 PSIG, BELOW THE MAXIMUM ALLOWABLE OPERATING PRESSURE OF 60 PSIG. EGU OPERATIONS DETECTED SUBSURFACE GAS BETWEEN THE MAIN AND TWO NEIGHBORING RESIDENCES, INCLUDING THE ACCIDENT HOME AND THE HOME IMMEDIATELY TO THE NORTH. THE SUBSURFACE GAS EXTENDED FROM THE MAIN TO THE BACKYARD AND FRONT YARD OF EACH HOME, REACHING ABOUT 250 FEET FROM THE ORIGIN OF THE LEAK. INITIAL NRC INCIDENT REPORT #1415759, WAS MADE ON 11/6/2024 AT 6:42 PM MT. 48-HOUR UPDATE NRC #1415924, WAS MADE ON 11/8/2024 AT 2:19 PM MT. UPDATE 3/7/2025: REVISED ESTIMATED VOLUME OF GAS RELEASED UNINTENTIONALLY BASED ON ADDITIONAL INFORMATION.
2026-06-30 10:38 | NO | YES | NO | 20240064 | 40921 | 2024-12-06 10:31 | SUPPLEMENTAL FINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2024-11-06 20:24 | EASTERN | YES | 2024 | 1702 WOODHOME DR | BEL AIR | HARFORD | MD | 21015 | 39.5109 | -76.3182 | [5 empty] | YES |  |  |  | 2024-11-06 22:57 | 1415765 | 1415883 | NATURAL GAS |  | 34.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-11-06 20:24 | OPERATOR/CONTRACTOR |  | 34.7 | NO | 2 | 2024-11-06 20:24 |  |  |  | 2024-11-06 20:38 | 2024-11-06 20:38 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1995 | 1995 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | OTHER | FITTING | 0.154 | [6 empty] | LEAK |  |  | OTHER | VEHICLE STRIKE ON METER SET | [5 empty] | CLASS 4 LOCATION | 650000 | 662982.62168750495 | 326 | 332.511284107887098 | 1806 | 1842.071715027129138 | 0 | 0 |  | 1.39 | 48 | 54.77647058823529411764705882352941176471 | 0 | 0 | 652180 | 270138.1278455426891009411764705882352941 | 665211.9811572282015301176470588235294118 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 91.5 | 91.5 | 99 | 192.619(A)(2) | 1995-10-23 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL AMOUNT OF RELEASE AT EVENT LOCATION. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  | YES |  | YES | FAILURE TO CONTROL SPEED, NEGLIGENT DRIVING | UNKNOWN | UNKNOWN | SMALL TRUCK | ROADWAY | 60 | NO | [142 empty] | JEFFREY WEATHERHOLTZ | MANAGER GAS ENGINEERING | jeffrey.weatherholtz@bge.com | [5 empty] | ROBERT REX |  | 3025933732 | robert.rex@bge.com | ON 11/6/2024 AT 20:24, BGE GAS DISPATCH RECEIVED A CALL FROM HARFORD COUNTY FIRE DEPARTMENT REGARDING A VEHICLE INTO A SINGLE-FAMILY RESIDENTIAL STRUCTURE AT 1702 WOODHOME DR. BEL AIR, MD 21015. A GAS TECHNICIAN ARRIVED ON SITE AT 20:58 AND FOUND THAT THE VEHICLE HAD STRUCK THE GAS METER AND REGULATOR SET AND IGNITED. THE TECHNICIAN CANVASSED A TOTAL OF 7 NEARBY HOMES AND FOUND NO OTHER GAS READINGS. THE GAS METER AND REGULATOR SET WAS APPROXIMATELY 60' FROM THE NEAREST ROADWAY. GAS CREWS WERE ABLE TO EXCAVATE AND SQUEEZE-OFF THE 1/2" PLASTIC GAS SERVICE AT 22:30, WHICH EXTINGUISHED THE FIRE. THE DRIVER FLED THE SCENE AND WAS LATER APPREHENDED AND CHARGED WITH SEVERAL RELATED OFFENSES.
2026-06-30 10:38 | YES | NO | NO | 20240065 | 40300 | 2024-12-06 18:42 | ORIGINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2024-11-06 22:30 | PACIFIC | YES | 2024 | OLD COACH DR AND VALLEY VISTA DR | CAMARILLO | VENTURA | CA | 93010 | 34.2474 | -119.0615 |  |  |  | YES | [5 empty] | 2024-11-07 10:40 | 1415771 | 1415884 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-11-06 13:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | NO | 14000 | 2024-11-06 22:30 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2024-11-06 12:00 | 2024-11-06 13:00 | 2024-11-06 13:00 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | UNKNOWN | [10 empty] | LEAK |  |  | OTHER | MIGRATING FIRE | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMOUNT UNKNOWN AT THIS TIME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 45 | 50 | 192.619(A)(1) | 1965-01-01 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | OTHER | NEWS MEDIA |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [143 empty] | YES | [24 empty] | CARLOS CHAVEZ | PIPELINE SAFETY AND COMPLIANCE ADVISOR | cchavez@socalgas.com | 213-264-6814 |  |  |  |  | CARLOS CHAVEZ |  | 213-264-6814 | cchavez@socalgas.com | ON NOVEMBER 6, 2024, SOCALGAS CREWS RESPONDED TO THE VENTURA MOUNTAIN FIRE WITH AN UNKNOWN CAUSE. THE FIRE SPREAD TO VARIOUS SOCALGAS FACILITIES, RESULTING IN A RELEASE OF NATURAL GAS THAT WAS SECONDARY TO THE FIRE. CREWS WORKED TO CONTROL THE RELEASE OF NATURAL GAS AS THE AREA BECAME SAFE. NO INJURIES OR FATALITIES RESULTED FROM THIS INCIDENT RELATED TO THE RELEASE OF NATURAL GAS. THE INCIDENT WAS INITIALLY REPORTED TO THE DOT AND CPUC DUE TO THE RELEASE OF NATURAL GAS WITH MEDIA COVERAGE AND COSTS ASSOCIATED WITH THE INCIDENT POTENTIALLY EXCEEDING $145,400. OUT OF THE 141 IMPACTED DISTRIBUTION SERVICES, 62 REQUIRED RESTORES. THE QUANTITY OF NATURAL GAS ESCAPE IS CURRENTLY UNKNOWN.
2026-06-30 10:38 | NO | YES | NO | 20240066 | 40349 | 2024-12-07 23:51 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2024-11-06 10:10 | EASTERN | NO | 2024 | 201 PIEDMONT AVENUE SE | ATLANTA | FULTON | GA | 30303 | 33.7497 | -84.3873 | [5 empty] | YES |  |  |  | 2024-11-06 10:10 | 1415700 | 1415878 | NATURAL GAS |  | 5261 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 170 | 2024-11-06 10:55 |  |  |  | 2024-11-06 09:03 | 2024-11-06 09:03 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 84 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1977 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 19440 | 19828.28025477707112 | 8200 | 8363.7807659039086 | 157560 | 160706.98749705119988 | PAVING RESTORATION | 1.74 | 9154 | 10446.3294117647058823529411764705882353 | 0 | 0 | 194354 | 85212.1208960678298588235294117647058824 | 199345.3779294968854823529411764705882353 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 40 | 45 | 192.619(A)(2) | 1977-06-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 17 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES |  |  |  |  | YES |  |  | YES |  |  | NO | NO | > 36” |  | CONTRACTOR | DRILLING | BUILDING CONSTRUCTION | YES | 240814001016 |  | NO | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY MARKED INACCURATELY DUE TO LOCATOR ERROR | [170 empty] | RALPH MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | 4045843733 | (404) 584-4710 |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND PRM | (630) 388-2316 | lquezad@southernco.com | A THIRD-PARTY PARTY EXCAVATOR (BALFOUR BEATTY CONSTRUCTION) STRUCK AND DAMAGED AN ATLANTA GAS LIGHT COMPANY (AGLC) 6-INCH STEEL GAS MAIN WHILE VERTICALLY DRILLING FOR A NEW BUILDING FOUNDATION NEAR THE INTERSECTION OF PIEDMONT AVENUE SE AT MLK JR DRIVE SW, ATLANTA. THE DAMAGE OCCURRED WITHIN CLOSE PROXIMITY OF A CSX RAILROAD RIGHT-OF-WAY AND A MARTA COMMUTER TRAIN RIGHT-OF-WAY WHERE BOTH RAIL COMPANIES WERE CONTACTED AT 10:40 HOURS TO STOP ANY TRAINS SCHEDULED TO COME THROUGH. BOTH RAIL COMPANIES RESUMED OPERATION AT 16:10 HOURS. IN ADDITION, DUE TO THE DURATION OF THE LEAK, APPROXIMATELY 5,261,061 SCF OF NATURAL GAS WAS EMITTED TO THE ATMOSPHERE WHICH EXCEEDED THE THREE MILLION CUBIC FEET OR MORE FOR REPORTING. DUE TO THE INCIDENT BEING NEAR THE GEORGIA STATE CAPITOL AND OCCURRING THE MORNING AFTER A FEDERAL ELECTION, IT WAS DECIDED TO NOTIFY THE NRC AT 10:10 HOURS OUT OF THE ABUNDANCE OF CAUTION ALTHOUGH NO TRIGGERS FOR REPORTING WERE PRESENT AT THAT TIME. THE NRC WAS LATER UPDATED OF THESE EVENTS DURING THE 48 HOUR UPDATE. UPON ARRIVAL, AGLC PERSONNEL WORKED WITH EMERGENCY RESPONDERS TO SECURE THE AREA AND MONITOR THE SURROUNDING AREA FOR GAS. GAS WAS SHUT-OFF TO THE DAMAGED AREA BY PERFORMING THREE SQUEEZE-OFF OPERATIONS. A LARGE PROJECT MARKING ' UTILITY FACILITY LOCATING AGREEMENT ('LARGE PROJECT AGREEMENT') WAS SIGNED ON AUGUST 13, 2024, WITH BALFOUR BEATTY CONSTRUCTION TO LOCATE THE AREA AS A LARGE PROJECT EXCAVATION. AGL'S CONTRACT LOCATOR LAST MARKED AGL'S FACILITIES LOCATED WITHIN THIS SPECIFIC WORK SITE ON SEPTEMBER 16, 2024, AS SET FORTH IN THE LARGE PROJECT AGREEMENT. AS TO THE DATE AND LOCATION OF THIS INCIDENT, THE EXCAVATOR WHO WAS PERFORMING THE EXCAVATION ACTIVITIES DID NOT NOTIFY AGL'S CONTRACT LOCATOR PRIOR TO COMMENCING EXCAVATION ACTIVITIES AS REQUIRED BY THE LARGE PROJECT AGREEMENT TO ENSURE THE SPECIFIC WORK SITE WAS MARKED OR RE-MARKED AS NECESSARY. POTHOLING ACTIVITIES CONDUCTED BY THE EXCAVATOR WITH A HYDRO-VAC TRUCK EXCAVATING APPROXIMATELY 8 FEET DEEP DID NOT REVEAL THE LOCATION OF THE GAS MAIN ALONG THE MARKS PROVIDED. UPON FURTHER REVIEW, IT WAS DETERMINED THAT THE GAS MAIN WAS MISMARKED BY APPROXIMATELY 20 FEET FROM WHERE THE DAMAGE OCCURRED. AGLC INITIALLY NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) UNDER NRC REPORT NUMBER 1415700. ADDITIONAL NRC REPORT NUMBER 1415878 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2026-06-30 10:38 | NO | YES | YES | 20240067 | 41533 | 2024-12-11 19:17 | SUPPLEMENTAL FINAL | 17570 | ROCHESTER GAS & ELECTRIC CORP | 180 SOUTH CLINTON AVENUE | ROCHESTER | NY | 14604 | 2024-11-11 05:20 | EASTERN | NO | 2024 | 843 STONE ROAD | ROCHESTER | MONROE | NY | 14616 | 43.2196 | -77.6477 |  |  | YES | [6 empty] | 2024-11-11 07:52 | 1416052 | 1416249 | NATURAL GAS |  | 2.37 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES | 2024-11-11 05:20 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 2.37 | YES | 7 | 2024-11-11 05:33 |  |  |  | 2024-11-11 05:33 | 2024-11-11 05:33 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | 1982 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | OTHER | METER SET | [9 empty] | OTHER | [8 empty] | IT APPEARS THE METER WAS TAMPERED WITH, WHICH RESULTED IN A RELEASE OF GAS. | CLASS 3 LOCATION | 342900 | 349748.8322717622267 | 5000 | 5099.866320673115 | 5000 | 5099.866320673115 | 0 | 0 | COST OF METER SET AND EMERGENCY RESPONSE IS ESTIMATED FROM SIMILAR INCIDENTS | 15.5907 | 37 | 42.22352941176470588235294117647058823529 | 0 | 0 | 352937 | 146194.9842878223007470588235294117647059 | 359990.7884425202214058823529411764705882 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 13 | 13 | 14 | 192.619(A)(2) | 1982-07-27 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2.2 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT APPEARS TO HAVE BEEN CAUSED BY OCCUPANT VANDALISM OF COMPANY PROPERTY. THE BODY OF THE METER WAS OBSERVED TO BE DISASSEMBLED, ALL SCREWS INTENDED TO SECURE THE FRONT COVER WERE FOUND REMOVED. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | OTHER | DAMAGE APPEARS TO BE INTENTIONAL. THE BODY OF THE METER WAS OBSERVED TO BE DISASSEMBLED, AND ALL SCREWS INTENDED TO SECURE THE FRONT COVER WERE FOUND REMOVED. | [155 empty] | DANIEL C BLANCE | ENGINEER | dcblance@nyseg.com | 607-240-3821 |  |  |  |  | TOM EICHE | MANAGER GAS ENGINEERING | 607-743-5733 | teiche@nyseg.com | THE ROCHESTER GAS AND ELECTRIC (RG&E) CONTROL ROOM WAS NOTIFIED BY 911 OF AN EXPLOSION AT 843 STONE RD., IN ROCHESTER, NY AT 05:20 ON 11/11/2024. THE RG&E CONTROL ROOM DISPATCHED EMERGENCY RESPONSE PERSONNEL IN ACCORDANCE WITH COMPANY PROCEDURES. THE RG&E CONTROL ROOM NOTIFIED THE NRC ON 11/11/2024 AT 07:52 (REPORT #1416052) AND PROVIDED THE REQUIRED 24-HOUR UPDATE TO THE NRC (REPORT #1416249). THREE PEOPLE WERE REPORTED INJURED BECAUSE OF THE INCIDENT AND THE STRUCTURE WAS EXTENSIVELY DAMAGED BY FIRE. THE COMPANY IS NOT AWARE OF OCCUPANT HOSPITALIZATION AND IS PRECLUDED FROM OBTAINING INFORMATION BY THE HIPPA PRIVACY LAW. RG&E ISOLATED THE SERVICE TO STOP THE FLOW OF GAS USING THE CURB VALVE AT 06:54 ON 11/11/2024. RG&E PERFORMED A LEAK SURVEY IN PROXIMITY TO THE INCIDENT IN ACCORDANCE WITH COMPANY O&M PROCEDURES AND NO UNDERGROUND LEAKS WERE IDENTIFIED. THE INITIAL INVESTIGATION FOUND THAT THE METER APPEARED TO HAVE BEEN TAMPERED WITH, LEADING TO THE RELEASE OF NATURAL GAS. THE FINAL REPORT NUMBERED MCSO CR 24-200968 FROM THE MONROE COUNTY, NY FIRE BUREAU # 24-0325 SUPPORTED THE INITIAL FINDINGS THAT THERE WERE NO DEFICIENCIES IN THE COMPANY’S FACILITIES AND THAT THE CAUSE OF THE FIRE WAS THAT EIGHT (8) PHILLIP'S HEAD RETAINING BOLTS HOLDING THE GAS METER’S FACE PLATE IN PLACE HAD BEEN REMOVED PRIOR TO THE INCIDENT.
2026-06-30 10:38 | NO | NO | NO | 20240068 | 40625 | 2024-12-12 12:56 | SUPPLEMENTAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2024-11-12 12:37 | CENTRAL | NO | 2024 | 709 W POLK AVENUE | PHARR | HIDALGO | TX | 78577 | 26.206 | -98.1931 | YES | [8 empty] | 2024-11-12 16:54 | 1416414 | 1416222 | NATURAL GAS |  | 4570 | 30 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-11-12 12:40 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2024-11-12 13:07 | 2024-11-12 13:07 | 2024-11-12 16:17 | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 78 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 12.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.22 | [6 empty] | MECHANICAL PUNCTURE | 4 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 10902 | 11119.748525595659946 | 12739 | 12993.439411810962397 | 12896 | 13153.575214280098208 | ADMINISTRATIVE COST | 3 | 13710 | 15645.5294117647058823529411764705882353 | 90 | 102.705882352941176470588235294117647059 | 50337 | 27958.4119589803440135882352941176470589 | 53014.9984458043676098235294117647058824 | 2 | 0 | 7 | 0 | 0 | 7 | 2 | 173 | 175 | 188 | 192.619(A)(2) | 2010-08-31 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSED BY THIRD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [8 empty] | NO | NO | MEASURED DEPTH FROM GRADE | 78 | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | NO |  |  |  | CONTRACT LOCATOR | NO | YES | 19 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | BRYAN WEEKS |  | bryan.weeks@onegas.com | [5 empty] | BRYAN WEEKS | DIRECTOR OF ENGINEERING | 5124071529 | bryan.weeks@onegas.com | THIRD PARTY CONTRACTOR STRUCK A BURIED 12" HIGH-PRESSURE DISTRIBUTION MAIN WHILE EXCAVATING FOR STORMWATER MANAGEMENT FACILITIES. TEXAS GAS SERVICE SHUT DOWN THE IMPACTED MAIN SEGMENT WITH EMERGENCY ISOLATION VALVES AND REPAIRED THE DAMAGE WITH A STEEL SLEEVE.
2026-06-30 10:38 | NO | YES | YES | 20240069 | 40348 | 2024-12-12 18:04 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2024-11-13 09:00 | EASTERN | NO | 2024 | 1711 ATHENS HIGHWAY | GRAYSON | GWINNETT | GA | 30017 | 33.858 | -83.9847 | [7 empty] | YES | SEE PART H - NARRATIVE | 2024-11-13 09:10 | 1416254 | 1416456 | NATURAL GAS |  | 0.01 | 0 | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES | 2024-11-12 12:21 | OTHER | SEE PART H - NARRATIVE | 0.01 | NO | 0 | 2024-11-12 12:21 | YES | OPERATOR | 2024-11-12 12:23 | 2024-11-12 12:21 | 2024-11-13 09:00 | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1974 | UNKNOWN |  |  |  |  | 4 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.156 | [6 empty] | OTHER | [8 empty] | SEE PART H - NARRATIVE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 1653 | 1686.015805614531819 | 0 | 0 |  | 1.37 | 0 | 0 | 0 | 0 | 1653 | 684.623024298183867 | 1686.015805614531819 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 192.619(A)(2) | 1974-03-08 | PRESSURE DID NOT EXCEED MAOP | OTHER | SEE PART H - NARRATIVE |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 10 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | SEE PART H - NARRATIVE |  |  | YES |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | RALPH MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | 4045843733 | (404) 584-4710 |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND PRM | (630) 388-2316 | lquezad@southernco.com | ON NOVEMBER 12, 2024, AGL CONTRACTOR EMPLOYEES (SEC) WERE WORKING TO ISOLATE AND RETIRE APPROXIMATELY 1,340 FEET OF 4-INCH STEEL MAIN ALONG HIGHWAY 78, FROM N CRESTVIEW DRIVE SW TO SUMMIT CHASE DRIVE SW NEAR GRAYSON, GA IN GWINNETT COUNTY. THE OPERATION INVOLVED A CROSS-COMPRESSION ACTIVITY TO REMOVE THE NATURAL GAS FROM THE ISOLATED SECTION OF THE MAIN AND INJECT IT BACK INTO THE ACTIVE SYSTEM. AFTER COMPLETING THIS CROSS-COMPRESSION ACTIVITY, A VENTURI WAS SET UP TO REMOVE ANY REMAINING RESIDUAL GAS FROM THE RETIRED SECTION OF THE MAIN BEFORE SEALING AND CAPPING THE ENDS. AN INVESTIGATION REVEALED A MISCOMMUNICATION AMONG THE CONTRACTOR EMPLOYEES REGARDING THE COMPLETION AND CONFIRMATION OF THE REMOVAL OF THE RESIDUAL GAS. THIS MISCOMMUNICATION OCCURRED BEFORE THE WELDER AND HIS HELPER ENTERED THE EXCAVATION TO PERFORM WELDING OPERATIONS. APPROXIMATELY FIVE MINUTES INTO THE WELDING PROCESS OF INSTALLING A WELD-OVER ON THE CONTROL FITTING USED TO ISOLATE THE MAIN, A FLASH FIRE IGNITED DUE TO THE REMAINING RESIDUAL GAS IN THE RETIRED SECTION OF THE MAIN. BOTH CONTRACTOR EMPLOYEES WERE WEARING THEIR PERSONAL PROTECTIVE EQUIPMENT (PPE); HOWEVER, THE HELPER HAD REMOVED HIS GLOVES AND HELMET TO DRINK SOME WATER WHEN THE FLASH FIRE OCCURRED, RESULTING IN BURNS TO HIS FACE AND HANDS. BOTH CONTRACTOR EMPLOYEES WERE TAKEN TO SEPARATE HOSPITALS. ONE CONTRACTOR EMPLOYEE WAS TREATED AND RELEASED, WHILE THE OTHER WAS ADMITTED TO THE HOSPITAL THE FOLLOWING MORNING. AT THAT POINT, AGL NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) UNDER NRC REPORT NUMBER 1416254. AN ADDITIONAL NRC REPORT NUMBER 1416456 WAS CREATED FOR THE SAME EVENT FOLLOWING A SUPPLEMENTAL CALL TO THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2026-06-30 10:38 | NO | YES | YES | 20240070 | 41004 | 2024-12-13 11:23 | SUPPLEMENTAL FINAL | 31588 | COSERV GAS, LTD | 7701 SOUTH STEMMONS | CORINTH | TX | 76210 | 2024-11-15 17:50 | CENTRAL | YES | 2024 | CROSS TIMBERS RD | FLOWER MOUND | DENTON | TX | 75022 | 33.0469 | -97.1329 |  |  |  | YES |  |  |  | YES | FLOW SHUTOFF WAS NOT NECESSARY, NO LOSS OF GAS AT TIME OF INCIDENT. | 2024-11-15 18:56 | 1416529 | 1416586 | OTHER GAS | NO GAS RELEASE | 0 | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-11-15 17:50 | YES | OPERATOR | 2024-11-15 17:51 | 2024-11-15 17:50 | 2024-11-15 17:50 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | HOT TAP MACHINE | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | NO RELEASE OF GAS AT TIME OF INCIDENT. | CLASS 1 LOCATION | 0 | 0 | 60000 | 61198.39584807738 | 25820 | 26335.70967995596586 | 0 | 0 | 2.B OPERATORS HOT TAP TOOLING IS DAMAGED; REPAIR COSTS ARE ESTIMATED AT 60,000 | 0 | 0 | 0 | 0 | 0 | 85820 | 35544.07014232918298 | 87534.10552803334586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429.2 | 429.2 | 740 | 192.619(A)(1) | 2023-04-11 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ACCIDENT HAD NOTHING TO DO WITH CONTROL ROOM. | [12 empty] | YES | 9 | 0 | YES | 1 | 0 | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | [197 empty] | OTHER EQUIPMENT FAILURE | [23 empty] | SOMETHING FAILED INTERNALLY, ANALYSIS ON GOING. | [59 empty] | JODY SPRADLEY | COMPLIANCE MANAGER | jspradley@coserv.com | 3368488402 |  |  |  |  | BEN DEREMER | DIRECTOR OF GAS OPERATIONS | 9037380983 | bderemer@coserv.com | COSERV GAS, LTD. EMPLOYEES WERE PERFORMING A HOT TAP ON AN IN-SITU STEEL GAS LINE AT THE ABOVE-DESCRIBED LOCATION OF INCIDENT. THEY WERE USING A MUELLER CO. MANUFACTURED HOT TAPPING TOOL AS A PART OF THIS WORK. THE RATCHET HANDLE OF THE TOOL'S MOUNTED COMPLETION MACHINE MOVED UNEXPECTEDLY AS A RESULT OF SOME YET-TO-BE-DETERMINED FAILURE INTERNAL TO THE TOOL. A COSERV GAS, LTD. EMPLOYEE WAS STRUCK BY THE RATCHET HANDLE AND SUFFERED FATAL INJURIES. THERE WAS NO RESULTING GAS LEAK.
2026-06-30 10:38 | NO | YES | NO | 20240072 | 40351 | 2024-12-22 13:46 | ORIGINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2024-11-21 23:36 | EASTERN | NO | 2024 | 3708 MILES AVE | CLAIRTON | ALLEGHENY | PA | 15025 | 40.2877 | -79.8976 |  |  |  | YES | [5 empty] | 2024-11-22 01:15 | 1417055 | 1417262 | NATURAL GAS |  | 0.99 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-11-21 23:36 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.99 | YES | 6 | 2024-11-21 23:46 | YES | OPERATOR | 2024-11-22 01:35 | 2024-11-22 00:30 | 2024-11-22 00:30 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | CUSTOMER OWNED HOUSELINE | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN AT THIS TIME, UNDER INVESTIGATION BY THE ALLEGHENY COUNTY FIRE MARSHAL INCIDENT INVESTIGATION TEAM. | CLASS 3 LOCATION | 185000 | 188695.053864905255 | 0 | 0 | 7558 | 7708.957930329480634 | 0 | 0 |  | 9.65 | 10 | 11.41176470588235294117647058823529411765 | 0 | 0 | 192568 | 79761.0426432427569855294117647058823529 | 196415.4235599406179869411764705882352941 | 0 | 0 | 8 | 0 | 0 | 1 | 0 | 0.25 | 0.25 | 1 | 192.623 | 1955-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.5 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | WAYNE DADIG | DIRECTOR STANDARDS AND COMPLIANCE | wayne.dadig@peoples-gas.com | 412-352-1576 |  | THOMAS PETROSKY | thomas.j.petrosky@peoples-gas.com | 412-554-3433 | EDWARD A. PALOMBO | VICE PRESIDENT RELIABILITY | 412-258-4453 | edward.a.palombo@peoples-gas.com | AT THIS TIME THE INCIDENT IS UNDER INVESTIGATION BY THE ALLEGHENY COUNTY CHIEF DEPUTY FIRE MARSHAL'S OFFICE, AND INCLUDES THE PA PUC GAS SAFETY DIVISION AND PA DEPARTMENT OF ENVIRONMENTAL PROTECTION. PEOPLES IS WORKING AND ASSISTING WITH ALL INVOLVED INVESTIGATING AGENCIES. BASED UPON PRELIMINARY FINDINGS, THE INVESTIGATION IS FOCUSED ON NON-JURISDICTIONAL FACILITIES WITHIN THE STRUCTURE.
2026-06-30 10:38 | NO | YES | YES | 20240074 | 41657 | 2024-12-31 14:03 | SUPPLEMENTAL | 11800 | ATMOS ENERGY CORPORATION - LOUISIANA | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2024-12-02 05:06 | CENTRAL | NO | 2024 | 535 AVONDALE GARDEN RD | AVONDALE | JEFFERSON | LA | 70094 | 29.9118 | -90.2106 |  | YES |  |  |  | YES |  |  |  | 2024-12-02 08:13 | 1417749 | 1417888 | NATURAL GAS |  | 586.54 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 5 | 5 | YES | 2024-12-02 06:26 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 26.61 | NO | 6 | 2024-12-02 05:06 | NO |  |  | 2024-12-02 05:35 | 2024-12-02 07:29 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN VALVE |  | 1952 | UNKNOWN | [7 empty] | STEEL |  | OTHER | VALVE | UNKNOWN | [6 empty] | OTHER | [8 empty] | A THIRD PARTY CEMENT TRUCK ENTERING A CONSTRUCTION SITE RAN OVER A NATURAL GAS VALVE BOX CAUSING THE RELEASE. | CLASS 3 LOCATION | 57700 | 58852.4573405677471 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.79 | 3396 | 3875.435294117647058823529411764705882353 | 0 | 0 | 61096 | 27053.8918520368867705882352941176470588 | 62727.8926346853941588235294117647058824 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 80 | 80 | 100 | 192.619(A)(1) | 1984-01-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 8 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | YES | UNKNOWN | LARGE TRUCK | ROADWAY | 6 | YES | [5 empty] | YES | THIRD PARTY CONSTRUCTION CONTRACTOR PLACED A TRAFFIC CONE ON TOP OF THE PAINTED VALVE BOX COVER. | [135 empty] | ANGELA MATHERNE | COMPLIANCE MANAGER | angela.matherne@atmosenergy.com | 504-206-7718 |  |  |  |  | ERIC SINGLETARY | VP TECH SERVICES | 504-756-9099 | eric.singletary@atmosenergy.com | THE INVESTIGATION, TO WHICH THE LOUISIANA DEPARTMENT OF CONSERVATION AND ENERGY (C&E) AND PHMSA ARE PARTIES, IS ONGOING UNDER THE DIRECTION OF THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB). THE NTSB RECENTLY MADE FACTUAL INFORMATION ABOUT THE INCIDENT AVAILABLE TO THE PUBLIC. THE RESPONSES IN THE REPORT WILL BE SUPPLEMENTED AS NECESSARY WHEN THE INFORMATION IS PERMITTED TO BE RELEASED BY THE NTSB.
2026-06-30 10:38 | NO | YES | NO | 20250001 | 40456 | 2025-01-23 18:52 | SUPPLEMENTAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2024-12-25 05:10 | PACIFIC | NO | 2024 | 105 LAWN WAY | CAPITOLA | SANTA CRUZ | CA | 95010 | 36.9723 | -121.9209 | [5 empty] | YES |  |  |  | 2024-12-27 10:21 | 1419941 | 1420056 | NATURAL GAS |  | 118 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-12-25 05:10 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 118 | YES | 3 | 2024-12-25 05:24 |  |  |  | 2024-12-25 05:40 | 2024-12-27 10:20 | NO | PUBLIC PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | STILL UNDER INVESTIGATION | UNKNOWN | UNKNOWN | [7 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 1.315 |  | 2708 | LEAK |  |  | OTHER | UNDER INVESTIGATION | [5 empty] | CLASS 3 LOCATION | 145400 | 148304.1126051741842 | 27690 | 28243.05968388771087 | 0 | 0 | 0 | 0 |  | 10.71 | 1264 | 1442.447058823529411764705882352941176471 | 0 | 0 | 174354 | 72863.4632677888678041176470588235294118 | 177989.6193478854244817647058823529411765 | 1 | 0 | 7 | 0 | 0 | 1 | 1 | 25 | 25 | 30 | 192.619(A)(2) | 2020-10-20 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS PRESSURE REMAINED CONSISTENT THROUGHOUT THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | rosa.duenas@pge.com | [5 empty] | BRIAN STOUT | REGULATORY COMPLIANCE MANAGER | 925-244-4558 | brian.stout@pge.com | ON WEDNESDAY, DECEMBER 25, 2024, AT APPROXIMATELY 0524 HOURS, PG&E WAS NOTIFIED OF A STRUCTURE FIRE AT 105 LAWN WAY IN CAPITOLA. ON DECEMBER 27, AT 0930 HOURS, PG&E CONFIRMED THERE WAS GAS ESCAPING FROM THE 1" DISTRIBUTION MAIN UPSTREAM TO THE METER SET. THERE WERE 8 GAS CUSTOMERS AFFECTED. SERVICE WAS RESTORED TO THE CUSTOMERS ON 12/28/24 AT APPROXIMATELY 1434 HOURS. FIRE DEPARTMENT, POLICE DEPARTMENT WERE ON SCENE AND THE AREA WAS BLOCKED OFF AND TRAFFIC REROUTED. THIS INCIDENT WAS REPORTED TO THE DOT (INCIDENT REPORT #1419941/1420056) AND CPUC ONCE ESTIMATED DAMAGE WAS CONFIRMED TO BE AT LEAST $145,400. THE INCIDENT IS STILL UNDER INVESTIGATION AND THE CAUSE OF INCIDENT IS YET TO BE DETERMINED. UPDATES WILL BE PROVIDED ONCE AVAILABLE.
2026-06-30 10:38 | NO | YES | NO | 20250002 | 40472 | 2025-02-03 17:32 | ORIGINAL FINAL | 11032 | SPIRE MISSOURI INC. EAST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2025-01-03 08:54 | CENTRAL | YES | 2025 | 895 GLEN ELM DR | GLENDALE | SAINT LOUIS | MO | 63122 | 38.6003 | -90.3865 | [7 empty] | YES | ABANDONED SERVICE AT THE MAIN | 2025-01-03 11:14 | 1420340 | 1420426 | NATURAL GAS |  | 8.83 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-01-03 09:24 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 8.83 | YES | 10 | 2025-01-03 08:56 | YES | OPERATOR | 2025-01-03 09:31 | 2025-01-03 09:17 | 2025-01-03 09:24 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1960 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES | 0.5 | UNKNOWN | UNKNOWN | COPPER | [10 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 401755 | 401755 | 2300 | 2300 | 500 | 500 | 0 | 0 |  | 5.34 | 47 | 47 | 0 | 0 | 404602 | 164311.7487845606257775257731958762886598 | 404602 | 0 | 0 | 2 | 0 | 0 | 10 | 0 | 45 | 45 | 60 | 192.621 M | 1960-04-09 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | YES | YES | YES | NO | NO | OTHER | MISSOURI ONE-CALL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF GAS RELEASED WAS NOT DETECTABLE BY THE SCADA SYSTEM AND THE CONTROLLER(S) TOOK NO ACTIONS THAT WOULD HAVE CONTRIBUTED TO OR CAUSED THE INCIDENT. | [12 empty] | YES | 4 | 0 | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [6 empty] | NO | NO | 18” – 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 250030078 |  | YES | CONTRACT LOCATOR | YES | YES | 2 | LOCATING ISSUE | FACILITY MARKED INACCURATELY DUE TO LOCATOR ERROR | [170 empty] | ERIN MILKERT | MANAGER DISTRIBUTION INTEGRITY | erin.milkert@spireenergy.com | 314-349-2932 |  | ERIN MILKERT | manager distribution integrity | 314-349-2932 | RANDY WILSON | DIRECTOR - PIPELINE AND SYSTEM INTEGRITY | 205-337-1337 | randy.wilson@spireenergy.com | A THIRD-PARTY EXCAVATOR WAS PERFORMING SEWER WORK AT THE NOTED ADDRESS AND DAMAGED THE 1/2-INCH COPPER SERVICE TO THE RESIDENCE. NATURAL GAS FROM THE LEAKING SERVICE LINE MIGRATED INTO THE HOME, CAUSING AN EXPLOSION AND DAMAGE TO THE RESIDENCE. THE SERVICE WAS RETIRED AT THE MAIN TO REPAIR THE CONDITION. LINE LOCATE REQUESTS WERE MADE PRIOR TO THE WORK, BUT THE LOCATE MARKS WERE NOT ACCURATE. THE COMPANY DETERMINED THE DAMAGES MET FEDERAL REPORTABLE INCIDENT CONDITIONS AT APPROXIMATELY 11:14 AM AND COMPLETED NOTIFICATION TO THE NRC. A 48-HOUR UPDATE TO THE NRC WAS MADE ON JANUARY 4, 2025, AT 8:58 PM - REPORT NUMBER 1420426.
2026-06-30 10:38 | NO | YES | NO | 20250003 | 40545 | 2025-02-25 11:16 | ORIGINAL FINAL | 4060 | ENBRIDGE GAS OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2025-01-29 12:00 | EASTERN | NO | 2025 | 230 1ST DR SW | NEW PHILADELPHIA | TUSCARAWAS | OH | 44663 | 40.4872 | -81.4475 | [5 empty] | YES |  |  |  | 2025-02-06 11:03 | 1422860 | 1422996 | NATURAL GAS |  | 1 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-01-29 12:00 | YES | OPERATOR | 2025-01-29 15:32 | 2025-01-29 12:30 | 2025-02-06 10:30 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2023 | 2022 |  |  |  |  | 4 | ASTM D2513 | POLYPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2708 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 28000 | 28000 | 200000 | 200000 | 0 | 0 |  | 3.71 | 4 | 4 | 4 | 4 | 228008 | 92588.1205830293817731958762886597938144 | 228008 | 10 | 0 | 155 | 0 | 0 | 155 | 10 | 0.5 | 0.5 | 1 | 192.623 | 2023-10-11 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOW PRESSURE DISTRIBUTION SYSTEM NOT MONITORED BY GAS CONTROL, AND LEAK WAS TOO SMALL TO BE EXPECTED TO TRIGGER A HI/LO SCADA ALARM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | YES | MEASURED DEPTH FROM GRADE | 36 | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | A502801024 | OHIO UTILITY PROTECTION SERVICE (OUPS) | Unknown | CONTRACT LOCATOR | YES | YES | 52 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [143 empty] | YES | [26 empty] | DANIEL EVANS EVANS | MANAGER OHIO PIPELINE SAFETY | daniel.a.evans@dominionenergy.com | 3305715796 |  | BRANDON JOHNSON | brandon.e.johnson@dominonenergy.com | 3308072154 | DANIEL EVANS | MANAGER OHIO PIPELINE SAFETY | 3305715796 | daniel.a.evans@dominionenergy.com | SHORTLY AFTER 12:00 EST ON JANUARY 29, 2025, ENBRIDGE GAS OHIO (EGO) BEGAN RECEIVING "NO GAS" CALLS FROM CUSTOMERS ON 1ST DR SW IN NEW PHILADELPHIA, OHIO. BY APPROXIMATELY 12:30 EST, EGO EMPLOYEES ARRIVED ON SITE TO INVESTIGATE AND DISCOVERED A THIRD-PARTY CONTRACTOR AT 230 1ST DR SW INSTALLING FIBER OPTIC CONDUIT USING HORIZONTAL DIRECTIONAL DRILLING. THE CONTRACTOR'S DRILL PATH HAD CROSSED 811 PAINT MARKINGS INDICATING THE PRESENCE OF UTILITIES BUT HAD NOT DAYLIGHTED THEM. DUE TO A LOSS OF GAS PRESSURE DOWNSTREAM OF THEIR WORK, EGO ORDERED THE CONTRACTOR TO STOP IMMEDIATELY, AND THEY COMPLIED. EGO CREWS EXPOSED THE AREA WHERE THE DRILL PATH CROSSED ACCURATELY MARKED EGO FACILITIES AND FOUND THAT THE 2" PILOT BORE HAD CROSS-BORED THE 4" MDPL LOW-PRESSURE MAINLINE. ADDITIONALLY, THE DRILLING EQUIPMENT HAD DAMAGED A NEARBY 2" WATER LINE, CAUSING WATER TO INUNDATE THE EGO FACILITY AND FLOW INTO THE GAS SYSTEM AT A HIGH RATE. GIVEN THE NATURAL GAS SYSTEM WAS OPERATING AT LESS THAN 1 PSIG, THE WATER ENTERING THE PIPELINE CREATED AN EFFECTIVE SEAL, RESULTING IN MINIMAL NATURAL GAS LOSS. EGO PROMPTLY MADE REPAIRS AND BEGAN ASSESSING THE EXTENT OF WATER IN THE GAS SYSTEM. ULTIMATELY, 165 CUSTOMERS WERE SHUT OFF DUE TO NO GAS OR LOW PRESSURE ACROSS SEVERAL INTERSECTING STREETS. AS THE NUMBER OF AFFECTED CUSTOMERS EXCEEDED 100, EGO COMMUNICATED THE OUTAGE AND ITS IMPACTS TO THE PUBLIC UTILITY COMMISSION OF OHIO. EGO CREWS, ALONG WITH MOBILIZED APPROVED CONTRACTORS, INITIATED A 24/7 OPERATION TO DEWATER MAINLINES AND SERVICES IN THE AFFECTED AREA. EGO ALSO OFFERED HOTEL ACCOMMODATIONS AND WARMING CENTERS TO AFFECTED CUSTOMERS AS OVERNIGHT TEMPERATURES WERE BELOW FREEZING. BY APPROXIMATELY 16:00 EST ON JANUARY 31, 2025, ENOUGH WATER HAD BEEN SUCCESSFULLY REMOVED FROM THE SYSTEM TO RESTORE ADEQUATE PRESSURE FOR ALL AFFECTED CUSTOMERS. BY 12:00 EST ON FEBRUARY 1, 2025, 150 CUSTOMERS HAD BEEN RESTORED TO SERVICE. THE REMAINING 15 CUSTOMERS COULD NOT BE RESTORED DUE TO NO ACCESS, BUT EGO CONTINUED OUTREACH UNTIL ALL WERE RESTORED THE FOLLOWING WEEK. ON FEBRUARY 6, 2025, A CONSOLIDATED REVIEW OF TIMESHEETS AND INVOICES FROM THE OUTAGE SHOWED THAT THE EGO RESPONSE, INCLUDING DAMAGE REPAIRS, DEWATERING, AND RESTORATION OF SERVICE, WOULD EXCEED THE $149,400 OUTLINED IN §191.3. ACCORDINGLY, EGO NOTIFIED THE NRC AND THE PUBLIC UTILITY COMMISSION OF OHIO.
2026-06-30 10:38 | NO | YES | YES | 20250004 | 40788 | 2025-02-25 15:31 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | 3600 MIDTOWN DR. | TAMPA | FL | 33607 | 2025-01-26 08:19 | EASTERN | YES | 2025 | 16970 S TAMIAMI TRL | FT. MYERS | LEE COUNTY | FL | 33908 | 26.4925 | -81.8473 | YES | [8 empty] | 2025-01-27 15:16 | 1422034 | 1422226 | NATURAL GAS |  | 368.23 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2025-01-26 08:19 | OTHER | TURNING THE EMERGENCY VALVE OFF FOR THE REGULATOR STATION. | 359.93 | NO | 0 | 2025-01-26 08:20 |  |  |  | 2025-01-26 09:16 | 2025-01-26 09:16 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2016 | UNKNOWN | [7 empty] | STEEL |  | CONTINUOUS WELDED |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | A VEHICLE DROVE THROUGH THE PROTECTIVE GUARDRAIL AND STRUCK PGS' ABOVEGROUND REGULATOR STATION. | CLASS 2 LOCATION | 0 | 0 | 34000 | 34000 | 0 | 0 | 0 | 0 |  | 0.95 | 350 | 350 | 0 | 0 | 34350 | 14091.0803799435205773195876288659793814 | 34350 | 12 | 0 | 77 | 0 | 0 | 77 | 12 | 350 | 350 | 476 | 192.619(A)(2) | 2016-10-26 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A VEHICLE DROVE THROUGH THE PROTECTIVE GUARDRAIL AND STRUCK PGS' ABOVEGROUND REGULATOR STATION. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 28 | YES |  |  | YES | [139 empty] | IYANNA JONES | COMPLIANCE ANALYST | iejones@tecoenergy.com | (407)-420-6617 |  | EDDIE WALSH | ejwalsh@tecoenergy.com | (813) 275-3778 | LINDA BARKER | SR DIR SAFETY COMPLIANCE OPERATIONS | (813) 228-4737 | ljbarker@tecoenergy.com | ON JANUARY 26, 2025, AT APPROXIMATELY 8:19 AM, PGS RECEIVED A NOTIFICATION OF A VEHICLE ACCIDENT AT THE 16900 BLOCK OF TAMIAMI TRAIL. UPON ARRIVAL, IT WAS CONFIRMED THAT A VEHICLE DROVE THROUGH THE PROTECTIVE GUARDRAIL AND STRUCK PGS' ABOVEGROUND REGULATOR STATION. THE IMPACT RESULTED IN AN IGNITION, WHICH WAS MITIGATED BY THE LOCAL FIRE DEPARTMENT. TO ENSURE SAFETY AND MAKE THE SCENE SAFE, THE EMERGENCY VALVE THAT CONTROLS THE AFFECTED SECTION OF THE SYSTEM WAS CLOSED AT 10:33 AM STOPPING THE ESCAPING GAS. APPROXIMATELY 89 CUSTOMERS EXPERIENCED SERVICE DISRUPTIONS DUE TO THE DAMAGE. A NEW REGULATOR STATION WAS INSTALLED ON THE NIGHT OF THE INCIDENT, WITH ALL REPAIRS COMPLETED THE SAME NIGHT. RESTORATION OF THE PIPELINE BEGAN THE NEXT DAY AT 8:00 AM AND WERE COMPLETED ON TUESDAY, JANUARY 28, 2025. THE IMPACT OF THE INCIDENT IS STILL BEING EVALUATED WITH ADDITIONAL INFORMATION SUPPLIED IN FUTURE REPORTING.
2026-06-30 10:38 | NO | YES | YES | 20250005 | 42441 | 2025-02-25 16:21 | SUPPLEMENTAL FINAL | 7348 | HOPE GAS, INC | 781 CHESTNUT RIDGE RD | MORGANTOWN | WV | 26505 | 2025-01-26 15:30 | EASTERN | NO | 2025 | 146 KRAMER DR | CLARKSBURG | HARRISON | WV | 26301 | 39.2727 | -80.35 |  | YES | [7 empty] | 2025-01-26 17:29 | 1421949 | 1422142 | NATURAL GAS |  | 680.81 | 0.36 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2025-01-26 15:30 | ALLOWED TO BURN OUT |  | 680.81 | YES | 699 | 2025-01-26 15:40 |  |  |  | 2025-01-26 16:30 | 2025-01-26 21:54 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 36 | YES | YES |  |  |  |  | YES | CASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1980 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | UNKNOWN |  |  |  | UNKNOWN |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 162606 | 162606 | 136486 | 136486 | 88458 | 88458 | 39292 | 39292 | TOTAL DAMAGES PAID YEAR TO DATE AND HOTEL REIMBURSEMENT COST. | 10.419 | 7093 | 7093 | 4 | 4 | 433939 | 179103.3532622733973303917525773195876288 | 433939 | 6 | 0 | 37 | 0 | 0 | 198 | 6 | 46 | 46 | 60 | 192.619(A)(2) | 1980-09-18 | PRESSURE DID NOT EXCEED MAOP | WICK |  | 0.5 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA POINT MONITORING THE SYSTEM DID NOT ALARM OR SHOW DROP IN PRESSURE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2022-06-30 | NO |  |  | NO |  |  |  |  | UNKNOWN |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | 18” – 36” |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | ETHAN GARTON | COMPLIANCE MANAGER | ethan.garton@hopegas.com | 3046413255 |  |  |  |  | SCOTT WALLACE | DIRECTOR COMPLIANCE | 3048441256 | scott.a.wallace@hopegas.com | ON JANUARY 26 AT APPROXIMATELY 3:30 PM THERE WAS AN EXPLOSION AND FATALITY AT 146 KRAMER DRIVE, CLARKSBURG, WEST VIRGINIA 26301. HOPE GAS, INC. PERSONNEL RESPONDING TO THE SCENE FOUND A SEPARATED COUPLING IN HOPE'S LINE M- 20 AT THE INTERSECTION OF S. CHESTNUT AND HARVEY STREETS, SOME 135 FEET FROM 146 KRAMER DRIVE. SUBSEQUENT FINDINGS, UPON DETAILED EXAMINATION OF THE COUPLING, SUPPORT THE CONCLUSION THAT AN EXTERNAL FORCE HAD BEEN EXERCISED ON THE COUPLING, PARTIALLY PULLING THE TWO-INCH PLASTIC LINE FROM THE BODY OF THE COUPLING, SOME TIME PRIOR TO THE JANUARY 26, 2025 EVENT. THE CAUSE OF THE FINAL SEPARATION OF THE COUPLING , THE EXPLOSION AT 146 KRAMER DRIVE, AND ANY CORRELATION BETWEEN THE SEPARATION AND THE EXPLOSION, AS WELL AS ANY OTHER SOLE CAUSE OR CONTRIBUTING FACTORS, INCLUDING SIGNIFICANT ONGOING ROADWAY, WATER, AND/OR SEWER CONSTRUCTION ACTIVITIES IN THE IMMEDIATE VICINITY, REMAIN THE SUBJECT OF ONGOING LITIGATION. HOPE CONFIRMED THAT THE NUMBER OF RESIDENTIAL BUILDINGS AFFECTED TO BE 198 (PART D6). HOPE SELECTED "NO" IN G3 BECAUSE THE SPECIFIC OPERATOR AND DATE OF THE PRIOR EXCAVATION DAMAGE IS NOT KNOWN AND IS SUBJECT OF THE ONGOING LITIGATION. HOPE SELECTED "UNKNOWN" IN G9, G10, G11, G13 AND G14 FOR THE SAME REASON. PART J HAS BEEN LEFT BLANK BECAUSE CONTRIBUTING FACTORS RELATED TO THE FINAL SEPARATION OF THE PIPE FROM THE COUPLING ARE UNKNOWN.
2026-06-30 10:38 | NO | YES | NO | 20250006 | 40568 | 2025-02-27 22:07 | ORIGINAL FINAL | 21349 | VIRGINIA NATURAL GAS | 544 S. INDEPENDENCE BLVD | VIRGINIA BEACH | VA | 23452 | 2025-01-29 03:03 | EASTERN | NO | 2025 | 764 S MILITARY HWY | VIRGINIA BEACH | VIRGINIA BEACH | VA | 23464 | 36.8206 | -76.2122 | YES | [8 empty] | 2025-01-30 13:26 | 1422213 | 1422385 | NATURAL GAS |  | 12982 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-01-29 03:03 |  |  |  | 2025-01-29 03:18 | 2025-01-29 13:00 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1958 | UNKNOWN |  |  |  |  | 18 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.304 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 36.6 | 0.5 |  | CLASS 3 LOCATION | 4002 | 4002 | 133603 | 133603 | 7220 | 7220 | 0 | 0 |  | 2.5806 | 33501 | 33501 | 0 | 0 | 178326 | 86091.9115234857718793814432989690721649 | 178326 | 40 | 0 | 478 | 0 | 0 | 478 | 40 | 133 | 140 | 150 | 192.621 M | 1958-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 100 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RUPTURE WAS REPORTED BY EMERGENCY RESPONDERS IMMEDIATELY FOLLOWING THE RELEASE. SCADA WAS NOTIFIED IMMEDIATELY AND SIMULTANEOUSLY NOTICED A DROP IN PRESSURE. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | MATERIAL FAILURE OF PIPE OR WELD | BUTT WELD | [146 empty] | BUTT WELD |  |  | FABRICATION | [29 empty] | YES | [7 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | MICHAEL SMITH | COMPLIANCE AND SYSTEM INTEGRITY MANAGER | mlsmi@southernco.com | 5408943733 |  | MICHAEL SMITH | mlsmi@southernco.com | 5408943733 | MICHAEL SMITH | COMPLIANCE AND SYSTEM INTEGRITY MANAGER | 5408943733 | mlsmi@southernco.com | RUPTURED LINE REPORTED BY EMERGENCY RESPONDERS IN THE NORTHBOUND LANE OF S MILITARY HWY NEAR 764 S MILITARY HWY, VIRGINIA BEACH, VA. PRELIMINARY FINDINGS DETERMINED THAT THE RUPTURE OCCURRED DUE TO A LACK OF FUSION IN THE GIRTH WELD. THE PIPELINE IS AN 18-INCH STEEL MAIN WITH COAL TAR COATING THAT WAS INSTALLED IN 1958. ONCE THE METALLURGICAL TESTING REPORT IS RECEIVED A SUPPLEMENTAL REPORT MAY BE SUBMITTED, AS NECESSARY.
2026-06-30 10:38 | NO | YES | NO | 20250007 | 40593 | 2025-03-06 08:54 | ORIGINAL FINAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2025-02-04 09:25 | CENTRAL | YES | 2025 | 1350 N 18TH STREET | OZARK | CHRISTIAN | MO | 65721 | 37.0304 | -93.2262 | [6 empty] | YES |  |  | 2025-02-04 15:56 | 1422740 | 1422888 | NATURAL GAS |  | 9297 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 10 | 2025-02-04 09:25 | YES | OPERATOR | 2025-02-04 09:29 | 2025-02-04 09:53 | 2025-02-04 15:56 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 15 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.2 | [6 empty] | MECHANICAL PUNCTURE | 6 | 6.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 18438 | 18438 | 500 | 500 | 0 | 0 |  | 6.3338 | 58885 | 58885 | 0 | 0 | 77823 | 55647.8446582264791058969072164948453608 | 77823 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | 235 | 235 | 275 | 192.619(A)(3) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT RESULT IN ANY ABNORMAL PIPELINE OPERATION OR PRESSURES THAT CAUSED OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [5 empty] | NO | NO | MEASURED DEPTH FROM GRADE | 15 | DEVELOPER | BULLDOZER | GRADING | NO |  |  |  | CONTRACT LOCATOR | NO | YES | 6 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | ERIN MILKERT | MANAGER DISTRIBUTION INTEGRITY | erin.milkert@spireenergy.com | 314-349-2932 |  | ERIN MILKERT | erin.milkert@spireenergy.com | 314-349-2932 | RANDY WILSON | DIRECTOR - PIPELINE AND SYSTEM INTEGRITY | 205-337-1337 | randy.wilson@spireenergy.com | A THIRD-PARTY EXCAVATOR WAS PERFORMING LAND GRADING WORK AND DAMAGED THE COMPANY'S 4-INCH STEEL MAIN. A REPAIR OF THE DAMAGE WAS MADE BY WELDING TWO, 4-INCH SHORT STOPS AND ISOLATING THE SECTION OF MAIN TO REPLACE 7-FEET OF 4-INCH STEEL MAIN. THE COMPANY'S FACILITIES WERE NOT LOCATED AS THE THIRD-PARTY EXCAVATOR FAILED TO REQUEST LOCATES PRIOR TO EXCAVATION. THE ORIGINAL DEPTH OF COVER IS UNKNOWN; HOWEVER, THE COMPANY ASSERTS THAT IT WAS GREATER THAN 15-INCHES AND AT AN APPROPRIATE DEPTH PRIOR TO LAND GRADING. AT THE TIME THE INCIDENT WAS DISCOVERED, A SIGNIFICANT AMOUNT OF SOIL HAD BEEN GRADED AND ACCUMULATED. A 48-HOUR UPDATE TO THE NRC WAS MADE ON FEBRUARY 6, 2025, AT 2:04 PM - REPORT NUMBER 1422888
2026-06-30 10:38 | NO | NO | NO | 20250008 | 40834 | 2025-03-10 15:27 | SUPPLEMENTAL | 15469 | PHILADELPHIA GAS WORKS | 800 W. MONTGOMERY AVENUE | PHILADELPHIA | PA | 19122 | 2025-02-27 08:15 | EASTERN | NO | 2025 | 1700 W. OLNEY AVE | PHILADELPHIA | PA | PA | 19141 | 40.0391 | -75.1512 | YES | [8 empty] | 2025-03-05 11:00 | 1425094 | 1425176 | NATURAL GAS |  | 4342 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2431 | 2025-02-27 08:15 | YES | OPERATOR | 2025-02-27 08:15 | 2025-02-27 08:15 | 2025-02-27 08:15 | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 37 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1911 | 1911 |  |  |  |  | 20 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | MECHANICAL PUNCTURE | 30 | 12 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 39941 | 39941 | 35425 | 35425 | 0 | 0 |  | 3.462 | 15032 | 15032 | 0 | 0 | 90398 | 42845.6499089562968670515463917525773196 | 90398 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 19 | 19 | 35 | 192.621 M | 1911-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 9.2 |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 2ND PARTY DAMAGE NOT RELATED TO CONTROLLER ACTIONS. | [12 empty] | YES | 1 | 0 | YES | 3 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) |  |  |  |  | YES | YES |  | YES |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 20250300245 |  | YES | FACILITY OWNER | YES | YES | 21 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [142 empty] | YES | [27 empty] | JOSEPH R HAWKINSON | VP FIELD OPERATIONS | joseph.hawkinson@pgworks.com | 2672496768 |  | JOSEPH R HAWKINSON | joseph.hawkinson@pgworks.com | 2672496768 | JOSEPH R HAWKINSON | VP FIELD OPERATIONS | 2672496768 | joseph.hawkinson@pgworks.com | ON THURSDAY FEBRUARY 27TH 2025 AT APPROXIMATELY 8:15AM PGW'S 2ND PARTY CONTRACTOR (DANELLA) WAS EXCAVATING WITH EQUIPMENT ON THE 1700 BLOCK OF W. OLNEY AVE. (PHILADELPHIA, PA 19141) AND PULLED A 6 INCH CAST IRON GAS MAIN STUB PIECE THAT WAS CONNECTED TO A 20 INCH CAST IRON GAS MAIN. THE 20 INCH CAST IRON MAIN FAILED AT THE CONNECTION TO THE 6" CAST IRON MAIN RESULTING IN A 30 INCH BY 12 INCH HOLE IN THE 20 INCH CAST IRON MAIN AND CAUSING A NATURAL GAS LEAK. PGW EMERGENCY PERSONNEL RESPONDED TO THE INCIDENT AND SHUT TWO MAIN VALVES TO STOP THE GAS LEAK BY 9:47AM ON 2/27/2025. THE SECTION OF 20" CAST IRON MAIN DAMAGED WAS THEN PERMANENTLY ABANDONED BY 4:40AM ON 2/28/2025. THE LOCATION OF THE 1911 6" CAST IRON STUB PIECE DAMAGED WAS NOT ACCURATELY SHOWN ON PGW MAPS. THESE HISTORIC AS BUILT RECORDS WERE OFF BY APPROXIMATELY TEN FEET. THE LINE HIT WAS NOT WITHIN THE TOLERANCE ZONE OF WHERE A PGW STRUCTURE WOULD HAVE BEEN EXPECTED. NOTE: THE ESTIMATED EVACUEES REPORTED IN PART A #22 IS NOT BASED ON ACTUAL EVACUEES BUT AN ESTIMATE MAINLY BASED ON BUILDING OCCUPANCY. PGW DID NOT EVACUATE ANY OF THE GENERAL PUBLIC BECAUSE THE GAS RUPTURE WAS IN THE MIDDLE OF THE STREET AND VENTILATING TO THE ATMOSPHERE. THE LOCAL BUILDINGS SELF EVACUATED OUT OF AN ABUNDANCE OF CAUTION.
2026-06-30 10:38 | NO | YES | NO | 20250009 | 40605 | 2025-03-10 17:55 | ORIGINAL FINAL | 2364 | DUKE ENERGY OHIO | 139 EAST FOURTH STREET PO BOX 960 - ROOM 460-ANNEX | CINCINNATI | OH | 45202 | 2024-01-30 15:00 | EASTERN | NO | 2024 | 3939 ERIE AVENUE | CINCINNATI | HAMILTON | OH | 45208 | 39.1488 | -84.4079 | YES | [5 empty] | YES |  |  | 2024-01-31 16:58 | 1390430 | 1390587 | NATURAL GAS |  | 0.01 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-01-30 15:00 | NO |  |  | 2024-01-30 15:00 | 2024-01-22 20:00 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 144 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2004 | UNKNOWN |  |  |  |  | 24 | WT API 5L GRADE X52 ERW | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.438 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 826514 | 843022.182432963794222 | 0 | 0 | 0 | 0 |  | 5.78 | 0 | 0 | 0 | 0 | 826514 | 342317.310529213031246 | 843022.182432963794222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 192 | 200 | 192.619(A)(3) | 2004-09-10 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS THE RESULT OF A LEAK ON A ENCLOSURE FITTING SO THE CONTROL ROOM WAS NOT INVOLVED. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FILLET WELD | MATERIAL/WELD/EQUIP FAILURE | FILLET WELD | MATERIAL FAILURE OF PIPE OR WELD | FILLET WELD | [146 empty] | FILLET WELD |  |  |  |  | REPAIR SLEEVE | [26 empty] | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | POOR CONSTRUCTION/INSTALLATION PROCEDURES |  |  | YES | 2004 | 192 | [84 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | THE LEAK WAS ORIGINALLY CALLED IN BY THE PUBLIC FOR ODOR IN THE AIR AND RESPONDED TO ON 01/22/24. LEAK ASSESSMENT INDICATED THAT IT WAS NON HAZARDOUS AND NOT MIGRATING INTO SUB-STRUCTURES AND STRUCTURES. A CREW WAS SENT OUT TO BEGIN EXCAVATION AND REPAIR OF THE LEAK ON 01/30/24. IT WAS DETERMINED THAT ADDITIONAL RESOURCES WOULD BE NEEDED TO COMPLETE EXCAVATION AND SHORING. ON 1/31/24 IT WAS DETERMINED THAT THE REPAIR OF LEAK WOULD MEET REPORTING CRITERIA. UTILIZING ONE VALVE AND STOPPLE, THE LEAK WAS ISOLATED WITH NO CUSTOMER INTERRUPTION. THE SEGMENT OF PIPE CONTAINING THE LEAK WAS CUT OUT AND REPLACED. THE REMOVED SECTION OF THE PIPE WAS SENT TO A FORENSIC METALLURGICAL LABORATORY FOR ANALYSIS TO DETERMINE THE ROOT CAUSE. ANALYSIS OF THE PIPE DETERMINED THE CAUSE OF THE LEAK WAS DUE TO CRACKING IN THE WELD. DUE TO THE SIZE OF THE LEAK, THE ESTIMATED VOLUME OF GAS RELEASED WILL BE DIFFICULT TO DETERMINE.
2026-06-30 10:38 | NO | YES | NO | 20250010 | 40662 | 2025-03-17 15:37 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2025-02-14 14:55 | EASTERN | NO | 2025 | 3109 HABERSHAM HILLS RD | CUMMING | FORSYTH | GA | 30041 | 34.1758 | -84.1124 |  |  |  | YES | [5 empty] | 2025-02-14 18:05 | 1423569 | 1423700 | NATURAL GAS |  | 5.6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-02-14 14:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 5.6 | NO | 2 | 2025-02-14 14:55 |  |  |  | 2025-02-14 15:21 | 2025-02-14 17:27 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1974 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ALUMINUM | [9 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 485800 | 485800 | 250 | 250 | 1409 | 1409 | 307 | 307 | ESTIMATED COST OF RESIDENTIAL METER SET | 4.17 | 23 | 23 | 0 | 0 | 487789 | 198080.8337242397004299381443298969072165 | 487789 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 52 | 52 | 60 | 192.619(A)(2) | 1974-03-05 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [218 empty] | JOSEPH CAUBO | MANAGER OF REGULATORY COMPLIANCE AND QA | jfcaubo@southernco.com | 7708284091 |  |  |  |  | LETICIA QUEZADA | DIRECTOR OF COMPLIANCE AND PRM | 6303882316 | lquezad@southernco.com | ACCORDING TO REPORTS, FIRE STARTED AT AGLC'S METER AND EXTENDED UP THE SIDE OF THE HOUSE AND THE FIRE EXTENDED ACROSS THE ATTIC. INITIAL INVESTIGATION REVEALED THAT THURSDAY (02/13/2025) EARLY AM JUST AFTER MIDNIGHT A BAD LIGHTNING STORM CAME THROUGH THIS NEIGHBORHOOD. IT APPEARS THAT THE METER HAD A SMALL FIRE THAT MELTED THE SERVICE AND THE GAS FROM THE SERVICE STARTED LEAKING AND IGNITED. THIS FIRE EXTENDED UP THE SIDE OF THE STRUCTURE AND ACROSS THE ATTIC. AGLC INITIALLY NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) UNDER NRC REPORT NUMBER 1423569. ADDITIONAL NRC REPORT NUMBER 1423700 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2026-06-30 10:38 | NO | NO | NO | 20250012 | 41952 | 2025-03-21 16:24 | SUPPLEMENTAL FINAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2025-02-20 06:58 | EASTERN | NO | 2025 | BETWEEN ROSE VALLEY RD AND LAKE RD | MORRIS RUN | TIOGA | PA | 17771 | 41.655 | -77.0059 | YES | [8 empty] | 2025-02-20 17:00 | 1424020 | 1424111 | NATURAL GAS |  | 8541 | 15 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-02-20 06:58 | NO |  |  | 2025-02-20 10:36 | 2025-02-20 17:00 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1940 | UNKNOWN |  |  |  |  | 5.25 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.227 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 15.1 | 1 |  | CLASS 1 LOCATION | 0 | 0 | 6220 | 6220 | 26930 | 26930 | 0 | 0 |  | 3.52 | 30064 | 30064 | 53 | 53 | 63267 | 37989.1564632284377175257731958762886598 | 63267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 155 | 175 | 192.619(A)(3) | 1940-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | OTHER | ALERT FROM PRESSURE MONITORING SYSTEM AT DISTRICT REGULATOR STATION. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THEIR ACTIONS DID NOT WARRANT THE NEED FOR INVESTIGATION. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROST HEAVE |  | NO | [218 empty] | CHAD REINER | STANDARDS ENGINEER | creiner@ugi.com | 484-577-6666 |  | JOHN TOUMEH | jtoumeh@ugi.com | 7176754606 | PAMELA JOCSAK | VP EHS AND TECHNICAL SUPPORT | 484-824-5508 | pjocsak@ugi.com | ***ON FEBRUARY XX, 2026, UGI SUBMITS ITS SUPPLEMENTAL AND FINAL REPORT BASED ON FINDINGS FROM THE EVENT’S MATERIAL INVESTIGATION.*** AT APPROXIMATELY 06:58 ON FEBRUARY 20, 2025, UGI RECEIVED INTERNAL ELECTRONIC, NON-SCADA, LOW-PRESSURE ALERTS AT MULTIPLE LOCAL DISTRICT REGULATOR STATIONS NEAR BLOSSBURG, PENNSYLVANIA. UGI PERSONNEL TRAVERSED A WIDE SNOW-COVERED GEOGRAPHIC AREA TO EVENTUALLY FIND A LINE BREAK. AT 12:33, TWO VALVES WERE CLOSED, STOPPING THE FLOW OF GAS TO THE DAMAGED LINE. IT WAS DISCOVERED THAT A WELD JOINT SEPARATED ON UGI'S HPDL LOCATED WITHIN A STATE FOREST RIGHT OF WAY. IN RESPONSE TO THIS INCIDENT, A 6-MILE STRETCH OF MAIN WAS ISOLATED AND ABANDONED. LAB TESTING DETERMINED THAT THE FAILURE INITIATED AT A GIRTH WELD. THE MORPHOLOGY OF THE GIRTH WELD WAS FOUND TO BE CONSISTENT WITH AN OXYACETYLENE WELD. NO EVIDENCE OF SIGNIFICANT INTERNAL OR EXTERNAL CORROSION WAS OBSERVED.
2026-06-30 10:38 | NO | NO | NO | 20250014 | 42120 | 2025-03-24 11:31 | SUPPLEMENTAL | 32074 | SUMMIT NATURAL GAS OF MISSOURI | 116 CHIEFS CT | BRANSON | MO | 65616 | 2025-02-24 11:27 | CENTRAL | YES | 2025 | 263 SHEPHERD OF THE HILLS EXPRESSWAY | BRANSON | TANEY | MO | 65616 | 36.6669 | -93.2524 | [5 empty] | YES |  |  |  | 2025-02-24 13:33 | 1424299 | 1424426 | NATURAL GAS |  | 82.64 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-02-24 12:15 | OTHER | COMPANY SQUEEZED OFF AND FIRE DEPARTMENT EXTINGUISHED THE FIRE | 42 | YES | 0 | 2025-02-24 11:49 | NO |  |  | 2025-02-24 11:49 | 2025-02-24 11:49 | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | UNDER CONCRETE PATIO | 3 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2011 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | NO | 1.25 | ASTM 2513 | US POLY | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.151 |  | 3408 | OTHER | [8 empty] | DAMAGE CAUSED BY CONCRETE SAW. | CLASS 3 LOCATION | 0 | 0 | 6350 | 6350 | 2114 | 2114 | 0 | 0 |  | 2.0968 | 173 | 173 | 0 | 0 | 8637 | 3577.785967427734973360824742268041237113 | 8637 | 1 | 0 | 0 | 6 | 0 | 0 | 1 | 38 | 38 | 50 | 192.619(A)(2) | 2011-10-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE BUSINESS | [6 empty] | NO | NO | < 18” |  | CONTRACTOR | UNKNOWN/OTHER | TELECOMMUNICATIONS | YES | 250353868 |  | YES | FACILITY OWNER | YES | YES | 9999 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | CARLA RICHARDSON | MANAGER OF PIPELINE SAFETY | crichardson@summitnaturalgas.com | 417-527-7719 |  | BRETT MAHAN | bmahan@summitnaturalgas.com | 417-926-9331 | MITCH PEBLEY | DIRECTOR OF OPERATIONS CO MO AND ME | 303-889-9455 | mpebley@summitutilities.com | ON 2/24/24, SUMMIT NATURAL GAS OF MISSOURI WAS NOTIFIED THAT A THIRD-PARTY CONTRACTOR STRUCK ONE OF ITS GAS SERVICE LINES WITH A CONCRETE SAW WHILE ATTEMPTING TO INSTALL A FIBER LINE AT 263 SHEPHERD OF THE HILLS PKWY IN BRANSON, MO. SUMMIT HAD PREVIOUSLY RESPONDED TO A LOCATE CALL MADE BY THIS CONTRACTOR, ACCURATELY LOCATING AND CLEARLY MARKING ITS FACILITIES. THE DAMAGE TO SUMMIT FACILITIES CAUSED BY THE THIRD-PARTY CONTRACTOR ULTIMATELY LED TO AN EXPLOSION IN THE STRUCTURE, CAUSING SIGNIFICANT PROPERTY DAMAGE. SUMMIT RESPONDED, SQUEEZED AND CAPPED THE SERVICE LINE LEADING TO THE PROPERTY. ***PART E6 ODORANT READ WAS MEASURED AT .08% LEL; THIS PHMSA FORM AUTOMATICALLY ROUNDS UP TO 1 SO DUE TO THIS FORM ERROR CURRENTLY ANSWERING THIS QUESTION AS NOT MEASURED*** ON FEBRUARY 27, 2026, AN ONSITE VISIT WAS CONDUCTED TO EXPOSE THE GAS LINE AT THE LOCATION OF THE CUT. DURING THIS VISIT, THE COMPANY OBTAINED ADDITIONAL INFORMATION REGARDING PIPE SPECIFICATIONS, MANUFACTURER, MATERIAL, AND DEPTH OF COVER. PIPE DEPTH OF COVER IS ACTUALLY 3.375 INCHES AT THE LOCATION OF THE CUT (FORMATTING OF THIS CELL IS IN 1,234 ONLY) PLEASE SEE ADDITIONAL COMMENTS FOR ITEMS BELOW : PART A #21C: THE COMPANY ESTIMATES THAT 82.64 MCF WAS UNINTENTIONALLY LOST, FROM THE TIME THE LINE WAS STRUCK (11:27) UNTIL THE LINE WAS SQUEEZED OFF (13:05). GAS WAS BLOWING FOR APPROXIMATELY 98 MINUTES, WHICH LEADS TO AN AVERAGE GAS LOSS OF 0.84MCF PER MINUTE. THERE WERE 48 MINUTES FROM THE LINE BEING STRUCK UNTIL THE EXPLOSION (AT 12:15). NOT ALL GAS FLOWING WOULD HAVE BEEN CONSUMED BY THE EXPLOSION, AS SOME GAS VENTED INTO THE ATMOSPHERE; HOWEVER, NO MORE THAN 40.32 MCF COULD HAVE BEEN CONSUMED BY THE EXPLOSION. THERE WAS A BRIEF FIRE IMMEDIATELY AFTER THE EXPLOSION; HOWEVER, THIS WAS QUICKLY EXTINGUISHED BY THE FIRE DEPARTMENT AND IT IS NOT POSSIBLE TO ESTIMATE WHAT VOLUME OF GAS MAY HAVE BEEN INCLUDED IN THAT POST-EXPLOSION FIRE. PART D (2A)- THE PROPERTY OWNER HAS NOT DETERMINED THE EXTENT AND SCOPE OF REPAIRS REQUIRED TO REHABILITATE THE BUILDING, AND THEREFORE IT IS NOT POSSIBLE TO ESTIMATE THE EXTENT OF THE PROPERTY DAMAGE. PART G3 (15A)- THE PROPERTY OWNER HAS NOT REOPENED THE FACILITY OR RECONNECTED SERVICE, AND IT IS CURRENTLY UNDETERMINED AS TO WHEN SERVICE WILL BE REESTABLISHED.
2026-06-30 10:38 | NO | YES | NO | 20250016 | 40705 | 2025-03-24 17:34 | SUPPLEMENTAL | 31159 | KANSAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2025-02-22 10:06 | CENTRAL | NO | 2025 | 428 S. MAIN ST. | HUTCHINSON | RENO | KS | 67501 | 38.0459 | -97.9318 | YES | YES | [7 empty] | 2025-02-22 13:35 | 1424163 | 1424341 | NATURAL GAS |  | 2513 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-02-22 10:06 | ALLOWED TO BURN OUT |  | 2513 | YES | 100 | 2025-02-22 11:45 |  |  |  | 2025-02-22 10:26 | 2025-02-22 13:33 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1936 | UNKNOWN |  |  |  |  | 10 | PLANE END STEEL | UNKNOWN | STEEL |  | OTHER | UNKNOWN SEAM TYPE | UNKNOWN | [6 empty] | OTHER | [8 empty] | ACETYLENE WELD | CLASS 3 LOCATION | 675000 | 675000 | 16490 | 16490 | 166952 | 166952 | 0 | 0 |  | 6.4056 | 16097 | 16097 | 0 | 0 | 874539 | 361688.604421282335375752577319587628866 | 874539 | 15 | 1 | 51 | 0 | 0 | 0 | 1 | 54 | 54 | 58 | 192.619(A)(3) | 1936-06-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.8 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE REDUCTIONS DUE TO THE INCIDENT WERE STILL WITHIN NORMAL RANGES. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | MATERIAL FAILURE OF PIPE OR WELD | BUTT WELD | [146 empty] | BUTT WELD |  |  | PIPE | [28 empty] | YES | [8 empty] | YES |  |  |  | POOR CONSTRUCTION/INSTALLATION PROCEDURES |  |  | NO | [70 empty] | YES | [15 empty] | RANDY SPECTOR | DIRECTOR OF ENGINEERING | randy.spector@onegas.com | 9135303219 |  |  |  |  | RANDY SPECTOR |  | 9135303219 | randy.spector@onegas.com | KGS OPERATES A 10" 58 PSIG MAOP STEEL PIPELINE LOCATED OUT FRONT AND UNDER THE SIDEWALK OF 428 S. MAIN STREET IN HUTCHINSON KANSAS. ON FEBRUARY 22 AT APPROXIMATELY 9:07 A.M. A GIRTH WELD IN THE LINE CRACKED AND BEGAN LEAKING. GAS MIGRATED FROM THE LEAKING WELD INTO THE STRUCTURE AT 428 S MAIN AND SUBSEQUENTLY IGNITED. THERE WERE NO INJURIES OR FATALITIES. KGS IS PARTICIPATING IN AN INVESTIGATION WITH NTSB, PHMSA, AND OTHER PARTIES. ADDITIONAL DETAIL IS CONTAINED IN THE 03-18-25 NTSB PRELIMINARY REPORT AT HTTPS://WWW.NTSB.GOV/INVESTIGATIONS/PAGES/PLD25FR003.ASPX.
2026-06-30 10:38 | NO | YES | NO | 20250017 | 41188 | 2025-04-01 13:02 | SUPPLEMENTAL FINAL | 31316 | COLORADO NATURAL GAS INC. | 10825 E. GEDDES AVENUE SUITE 410 | CENTENNIAL | CO | 80112 | 2025-03-09 23:20 | MOUNTAIN | YES | 2025 | NORTH PIGGOT RD AT COUNTY ROAD 153 AND EAST BISON DR. | STRAUSBURG | ARAOAHO | CO | 80136 | 39.7339 | -104.3404 | YES | [8 empty] | 2025-03-10 01:10 | 1425432 | 1425558 | NATURAL GAS |  | 2340.47 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 1 | 2025-03-09 23:20 |  |  |  | 2025-03-09 23:20 | 2025-03-09 23:20 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2020 | UNKNOWN | [7 empty] | STEEL |  | SEAMLESS |  | 0.218 | [6 empty] | OTHER | [8 empty] | VEHICLE RAN INTO REGULATOR STATION CAUSING CATASTROPHIC FAILURE | CLASS 2 LOCATION | 0 | 0 | 107011 | 107011 | 35411 | 35411 | 500 | 500 | EASEMENT STAKING | 4.183 | 9790 | 9790 | 0 | 0 | 152712 | 66008.1593499217468924536082474226804124 | 152712 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 477 | 477 | 740 | 192.619(A)(2) | 2020-12-07 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 100 |  | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL HAD NO PART IN THE INCIDENT OF RELEASE OF NATURAL GAS ' THE GAS LOSS WAS CAUSED BY AN OUT-OF-CONTROL CAR STRIKING THE REGULATOR STATION AT A HIGH RATE OF SPEED CAUSING CATASTROPHIC FAILURE OF FITTINGS AND PARTS | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | YES | UNKNOWN | PASSENGER CAR | ROADWAY | 75 | YES | YES | [141 empty] | CARLA RICHARDSON | MANAGER OF PIPELINE SAFETY | crichardson@summitnaturalgas.com | 417-527-7719 |  | CODY STOUMBAUGH | cstoumbaugh@coloradonaturalgas.com | 720-626-5143 | MITCH PEBLEY | DIRECTOR OF OPERATIONS CO MO AND ME | 303-889-9455 | mpebley@summitutilities.com | VEHICLE WAS TRAVELING WEST BOUND ON I70 FRONTAGE ROAD AT A HIGH RATE OF SPEED AND LEFT ROADWAY AND STRUCK CNG REGULATOR STATION (STRASBURG PARK REG STATION). 7-24-2025 SUPPLEMENTAL REPORT SUBMITTED TO UPDATE PART D FOR PROPERTY DAMAGE 7-29-2025 FINAL REPORT UPDATE. THE INJURIES SUSTAINED BY THE INDIVIDUAL AS A RESULT OF THE VEHICLE ACCIDENT WERE DETERMINED TO BE UNRELATED TO GAS EXPOSURE OR GAS-RELATED CAUSES. (UPDATED QUESTION PART A #10)
2026-06-30 10:38 | NO | YES | NO | 20250018 | 40739 | 2025-04-10 15:51 | ORIGINAL | 2309 | CHESAPEAKE UTILITIES CORPORATION | 500 ENERGY LANE | DOVER | DE | 19901 | 2025-03-13 23:21 | EASTERN | YES | 2025 | 409 WOOD DUCK DRIVE | CAMBRIDGE | DORCHESTER | MD | 21613 | 38.5654 | -76.1013 |  |  |  |  | YES | YES |  |  |  | 2025-03-14 17:58 | 1425873 | 1425971: 48-Hour Update to Report # 1425873 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-03-13 23:21 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 13 | 2025-03-14 16:38 |  |  |  | 2025-03-14 01:35 | 2025-03-14 16:38 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2022 | 2021 | MULTI-FAMILY RESIDENTIAL | YES | YES | NO | 0.75 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | OTHER | [8 empty] | SHEARED RISER | CLASS 3 LOCATION | 750000 | 750000 | 6720 | 6720 | 7560 | 7560 | 3920 | 3920 | COSTS ASSOCIATED WITH SUPPORTING MD STATE FIRE MARSHAL INVESTIGATION. | 0 | 0 | 0 | 0 | 0 | 768200 | 311935.0397039549464 | 768200 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 40 | 40 | 60 | 192.619(A)(2) | 2022-07-05 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 2.6 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSE OF THE INCIDENT NOT RELATED TO ANYTHING IN THE CONTROL ROOM | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | RICHARD WELSH | OPERATIONS COMPLIANCE MANAGER | rwelsh@chpk.com | 3023637997 |  | CHRISTOPHER STRYKER | cstryker@chpk.com | 302-363-7832 | RICHARD WELSH | OPERATIONS COMPLIANCE MANAGER | 3023637997 | rwelsh@chpk.com | ON MARCH 14, 2025 AT 00:18, THE OPERATOR RECEIVED NOTIFICATION OF AN EXPLOSION AT A RESIDENCE WITH FIRST RESPONDERS REQUESTING ASSISTANCE TO TERMINATE GAS SERVICE. UPON ARRIVAL, THE OPERATOR TERMINATED GAS SERVICE TO ALL SIX RESIDENTS OF THE BUILDING. DUE TO THE PHMSA INCIDENT REPORT BEING A PUBLIC DOCUMENT AND THE INCIDENT IS STILL UNDER INVESTIGATION BY THE MARYLAND FIRE MARSHAL, WE ARE PROHIBITED FROM PROVIDING ADDITIONAL DETAILS AT THIS TIME. - A-11, A-12 - NOTE THAT "FAILURE" OF EQUIPMENT HAS NOT YET BEEN ESTABLISHED THROUGH INVESTIGATION.
2026-06-30 10:38 | NO | YES | YES | 20250019 | 40745 | 2025-04-10 17:20 | ORIGINAL | 12582 | ATMOS ENERGY CORPORATION - MISSISSIPPI | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2025-03-12 09:08 | CENTRAL | YES | 2025 | 137 COUNTY ROAD 660 | PLANTERSVILLE | LEE | MS | 38862 | 34.1649 | -88.6176 |  | YES | [7 empty] | 2025-03-12 09:48 | 1425629 | 1425656, 1425860 | NATURAL GAS |  | 5874 | 388.2 | NO | [5 empty] | 0 | YES | 0 | 2 | 0 | 0 | 0 | 2 | NO | [5 empty] | 0 | 2025-03-12 09:08 | YES | OPERATOR | 2025-03-12 09:08 | 2025-03-12 09:08 | 2025-03-12 09:15 | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 84 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | COMPLETION PLUG OF A STOPPLE FITTING | 2025 | 2024 | [7 empty] | OTHER | COMPLETION PLUG OF A STOPPLE FITTING | [9 empty] | OTHER | [8 empty] | THE COMPLETION PLUG OF A STOPPLE FITTING WAS EJECTED. | CLASS 2 LOCATION | 0 | 0 | 100000 | 100000 | 50000 | 50000 | 0 | 0 |  | 3.4944 | 20526 | 20526 | 1357 | 1357 | 171883 | 78731.1878496598618556701030927835051546 | 171883 | 2285 | 215 | 14998 | 1 | 0 | 0 | 0 | 330 | 330 | 385 | 192.619(A)(2) | 1991-10-10 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 8.8 |  | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE CONTRACTOR AND INSPECTION PERSONNEL ONSITE WHO CALLED THE APPROPRIATE FIRST RESPONDERS ALONG WITH ATMOS ENERGY OPERATION PERSONNEL. GAS CONTROL DID NOT PERFORM ANY ACTION THAT CONTRIBUTED TO THE INCIDENT. | [12 empty] | YES | 1 | 0 | YES | 9 | 1 | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | FRANK H. REDD | MANAGER ENGINEERING SERVICES | frank.redd@atmosenergy.com | (601) 592-5313 | (601) 360-1492 | TERRY HERRING | terry.herring@atmosenergy.com | (662) 690-5202 | CHAD KEIM | VICE-PRESIDENT TECHNICAL SERVICES | (601) 624-1903 | chad.keim@atmosenergy.com | ATMOS ENERGY'S SECOND-PARTY CONTRACTOR WAS ATTEMPTING TO COMPLETE A STOPPLE FITTING WHEN THE COMPLETION PLUG WAS EJECTED, RESULTING IN INJURIES TO THREE CONTRACTOR EMPLOYEES AND A RELEASE OF NATURAL GAS. A MAINLINE VALVE WAS CLOSED, ELIMINATING THE RELEASE OF NATURAL GAS.
2026-06-30 10:38 | NO | YES | NO | 20250020 | 40746 | 2025-04-11 08:21 | ORIGINAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2025-03-09 16:23 | EASTERN | YES | 2025 | 859 WHITE CLOUD RD | NEW KENSINGTON | WESTMORELAND | PA | 15068 | 40.5503 | -79.6448 | YES | [8 empty] | 2025-03-10 13:13 | 1425478 | 1425619 | NATURAL GAS |  | 3403 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-03-09 16:50 |  |  |  | 2025-03-09 17:03 | 2025-03-09 16:50 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 144 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1972 | UNKNOWN |  |  |  |  | 12 | API-5LX-42 | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.219 | [6 empty] | LEAK |  |  | OTHER | LEAK NOT EXPOSED. | [5 empty] | CLASS 1 LOCATION | 0 | 0 | 164106 | 164106 | 9974 | 9974 | 0 | 0 |  | 10.6952 | 36396 | 36396 | 0 | 0 | 210476 | 100328.9707205685573146391752577319587629 | 210476 | 0 | 0 | 41 | 0 | 0 | 41 | 0 | 82 | 82 | 115 | 192.619(A)(1) | 1972-08-23 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM DID NOT CONTRIBUTE TO THIS LEAK. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | THE LEAKING SECTION OF PIPE WAS NOT EXPOSED. PIPELINE WAS REPLACED. | [45 empty] | THOMAS PETROSKY | COMPLIANCE MANAGER | thomas.j.petrosky@peoples-gas.com | 412-554-3433 |  | THOMAS PETROSKY | thomas.j.petrosky@peoples-gas.com | 412-554-3433 | EDWARD A. PALOMBO | VICE PRESIDENT RELIABILITY | (412) 258-4453 | edward.a.palombo@peoples-gas.com | A LEAK OCCURRED ON A DISTRIBUTION PIPELINE ALONG WHITE CLOUD ROAD IN NEW KENSINGTON, PA ON 3/9/2025. INITIAL RESPONSES WERE TO ISOLATE AND EXPOSE THE LEAKING PIPELINE FOR REPAIRS. DUE TO A SAFETY CONCERN REGARDING THE DEPTH OF THE PIPE IT WAS DECIDED UPON TO RENEW THE MAINLINE TO ELIMINATE THIS LEAKING PIPELINE. NEW PLASTIC MAINLINE WAS INSTALLED ON AND TIED IN ON 3/11/2025.
2026-06-30 10:38 | NO | YES | NO | 20250021 | 41528 | 2025-04-24 08:37 | SUPPLEMENTAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2025-03-22 07:50 | EASTERN | YES | 2025 | SR1 & SR124 | BLUFFTON | WELLS | IN | 46714 | 40.7427 | -85.1706 |  |  |  | YES | [5 empty] | 2025-03-31 15:54 | 1427386 | 1427528 | NATURAL GAS |  | 894 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-03-22 07:50 |  |  |  | 2025-03-22 08:07 | 2025-03-31 15:10 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2001 | 2001 | [7 empty] | STEEL |  | SEAMLESS |  | 0.155 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 2 | 2 |  | CLASS 3 LOCATION | 0 | 0 | 610365 | 610365 | 3576 | 3576 | 488 | 488 | ADMINISTRATIVE, POLICE REPORT, FILINGS | 3.415 | 3053 | 3053 | 0 | 0 | 617482 | 251981.301863713398503876288659793814433 | 617482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 120 | 138 | 192.619(A)(2) | 2001-02-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | SMALL TRUCK | ROADWAY | 98 | YES | YES |  |  | YES | [138 empty] | JOHNESE MCKINNEY | MGR. OPERATIONS COMPLIANCE | johnesemckinney@nisource.com | 2196474093 |  | JOHNESE MCKINNEY | johnesemckinney@nisource.com | 219-647-4093 | JOHNESE MCKINNEY | MGR OPERATIONS COMPLIANCE | 2196474093 | johnesemckinney@nisource.com | A SMALL PICKUP TRUCK LOST CONTROL, RAN OFF THE EASTSIDE OF ROAD DOWN AN EMBANKMENT NEAR THE BRIDGE UNDERPASS AND HIT ONE STATION OF A DUAL STATION SETUP. IMPACT CAUSED BOTH THE SEPARATION OF PIPES FEEDING THE THE STATION. BOTH THE HIGH PRESSURE SIDE AND MEDIUM PRESSURE SIDE 2" PIPES WERE SEPARATED. VALVES WERE CLOSED TO STOP THE FLOW. CAPS WERE WELDED ON THE SEPARATED PIPES. THE PRESSURE WAS MAINTAINED BY THE UNDAMAGED STATION. THE DAMAGED STATION CANNOT BE REPAIRED, THEREFORE PLANS ARE BEING DESIGNED TO REPLACE THE STATION. UPDATE 10/30/2025, THE DESTROYED STATION WILL BE REPLACE SPRING 2026. THERE ARE NO OTHER UPDATES. THIS REPORT IS CONSIDERED LAST AND FINAL.
2026-06-30 10:38 | NO | YES | YES | 20250022 | 40803 | 2025-04-25 08:51 | ORIGINAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2025-03-27 17:20 | EASTERN | YES | 2025 | 368 BLOOMFIELD AVENUE | NEWARK | ESSEX | NJ | 07107 | 40.768 | -74.1819 |  |  | YES | YES | [5 empty] | 2025-03-27 23:30 | 1427035 | 1427203 | NATURAL GAS |  | 7.39 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2025-03-27 17:20 | OTHER | GAS IGNITED, BURNT OUT, BUT NO PART OF THE STRUCTURE IGNITED OR REQUIRED FIRE TO BE EXTINGUISHED | 0.83 | YES | 0 | 2025-03-27 17:30 |  |  |  | 2025-03-27 17:58 | 2025-03-27 22:30 | NO | PUBLIC PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1958 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | YES | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 4 LOCATION | 2500 | 2500 | 2057 | 2057 | 5690 | 5690 | 0 | 0 |  | 10.37 | 77 | 77 | 0 | 0 | 10324 | 4223.604794835743411010309278350515463918 | 10324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 1 | 192.623 | 1958-09-04 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 1 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | NO | N/A Bare/Ineffectively Coated Pipe | NONE |  | NO | [19 empty] | 2024-07-11 | NO | [224 empty] | YES |  |  | HENRY VARUM | PRINCIPAL REGULATORY SPECIALIST | henry.varum@pseg.com | 732-343-3421 |  |  |  |  | CHRISTOPHER LAROSSA | DISTRICT MGR REG POLICY AND PROCEDURE | 973-896-7617 | christopher.larossa@pseg.com | ON 3/27/2025 AT 17:43 HOURS A PSE&G TECHNICIAN RESPONDED TO A NOTIFICATION OF A GAS IGNITION AT 368 NORTH 6TH STREET (SALVATORE BONTEMPO MEMORIAL PARK). THE FIRST RESPONDER ARRIVED AT 17:58 HOURS AND WAS NOTIFIED BY NEWARK FD THAT THERE WAS A GAS IGNITION WITHIN A PARK STRUCTURE AND 1 PERSON WAS TAKEN TO THE HOSPITAL BY AMBULANCE. AT 19:16 GAS TO THE STRUCTURE WAS SHUT OFF AT THE CURB, AND THE SERVICE WAS CUT OFF AT THE MAIN 22:00. A LEAK SURVEY WAS COMPLETED AND DID NOT RESULT IN ANY ADDITIONAL LEAKS. FURTHER INVESTIGATION REVEALED THAT A GAS SERVICE WAS FOUND TO BE LEAKING IN THE STRUCTURE. SHORTLY BEFORE 17:20, AN INDIVIDUAL TRESPASSED INTO THE STRUCTURE WITH A SOURCE OF IGNITION ON HIS PERSON. AT 17:20, THE SOURCE OF IGNITION IGNITED, LEADING TO THE EXPLOSION. THE INDIVIDUAL WAS RELEASED FROM THE HOSPITAL THE NEXT MORNING WITH MINOR INJURIES.
2026-06-30 10:38 | NO | YES | NO | 20250023 | 40807 | 2025-04-25 12:09 | ORIGINAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2025-03-28 08:57 | EASTERN | YES | 2025 | 36 SUNNINGDALE DR | GROSSE POINTE SHORES | WAYNE COUNTY | MI | 48236 | 42.4322 | -82.8807 | [5 empty] | YES |  |  |  | 2025-03-28 10:15 | 1427074 | 1427241 | NATURAL GAS |  | 129 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-03-28 08:57 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 129 | NO | 0 | 2025-03-28 08:57 | YES | OPERATOR | 2025-03-28 08:57 | 2025-03-28 08:57 | 2025-03-28 09:45 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNKNOWN | UNKNOWN | UNKNOWN | [7 empty] | OTHER | METER ASSEMBLY | [9 empty] | LEAK |  |  | OTHER | MULTIPLE | [5 empty] | CLASS 3 LOCATION | 1149000 | 1149000 | 8357 | 8357 | 0 | 0 | 0 | 0 |  | 3.77 | 486 | 486 | 0 | 0 | 1157843 | 470351.8177480771482856494845360824742268 | 1157843 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 57 | 57 | 60 | 192.619(A)(2) | 2005-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 10 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | SOURCE OF IGNITION UNKNOWN. | [45 empty] | JUSTIN C MORRIS | ENGINEER | justin.morris@dteenergy.com | 2484621760 |  |  |  |  | JUSTIN C MORRIS | ENGINEER | 2484621760 | spartan0126@yahoo.com | GAS LEAK CALLED IN BY CUSTOMER FOR SINGLE FAMILY RESIDENCE AT 08:12AM ON 3/28/25. DTE GAS TECHNICIAN ARRIVED AT 08:45AM AND DISCOVERED 3 LEAKS AT METER MANIFOLD. ONE LEAK FOUND AT REGULATOR BODY SCREW, WAS TIGHTENED AND LEAK STOPPED. SECOND LEAK WAS ABOVE SHUT-OFF VALVE ON INSULATED UNION. GAS TO RESIDENCE WAS SHUT OFF VIA LOCKWING VALVE. A THIRD LEAK WAS BELOW THE SHUT-OFF VALVE. AT 8:50, TECHNICIAN WENT TO VEHICLE TO CALL FOR A DISTRIBUTION CREW TO CUT THE SERVICE. AT APPROXIMATELY 08:57, GAS IGNITED AND 911 WAS CALLED. TECHNICIAN WAS AT VEHICLE IN DRIVEWAY AT TIME OF IGNITION, WHICH WAS VERIFIED VIA HOME SECURITY VIDEO FOOTAGE. CAUSE OF IGNITION IS UNKNOWN. RESIDENCE CAUGHT FIRE AND IS A TOTAL LOSS. SERVICE IS 1-1/4" MDPE PIPE OPERATING AT 57PSIG WITH MAOP 60PSIG INSTALLED IN 2005. GAS WAS SHUT OFF VIA PINCH-OFF AT 11:50AM. LEAK CHECKS FOUND NO GAS IN THE GROUND AND ODORANT LEVELS ADEQUATE. LOST GAS CALCULATED TO BE 129 MCF. NO INJURIES OR FATALITIES.
2026-06-30 10:38 | NO | NO | NO | 20250024 | 40821 | 2025-04-30 09:10 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2025-03-06 14:15 | EASTERN | NO | 2025 | SKYHAWK DR & CENTERVILLE RD | CHANTILLY | FAIRFAX | VA | 20151 | 38.8997 | -77.4281 | [5 empty] | YES |  |  |  | 2025-04-01 12:01 | 1427443 | 1427582 | NATURAL GAS |  | 3364.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-03-06 14:17 |  |  |  | 2025-03-06 15:13 | 2025-03-06 15:13 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 72 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1998 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | UNKNOWN | MECHANICAL PUNCTURE | 8 | 4 | [7 empty] | CLASS 4 LOCATION | 3538 | 3538 | 73 | 73 | 14569 | 14569 | 999 | 999 | ADMIN FEE: INCLUDES DISPATCH, DAMAGE PREVENTION, COLLECTIONS & CORP. ACCOUNTING | 2.1544 | 7248 | 7248 | 0 | 0 | 26427 | 13690.8287504162728234639175257731958763 | 26427 | 28 | 0 | 0 | 0 | 0 | 0 | 28 | 55 | 55 | 60 | 192.619(A)(1) | 1998-11-30 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE TO THE MAIN. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | COUNTY ROAD | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | B505902226 |  | Unknown | CONTRACT LOCATOR | YES | YES | 5 | LOCATING ISSUE | FACILITY MARKED INACCURATELY DUE TO LOCATOR ERROR | [170 empty] | ARTHUR M GROFF | SUPERVISOR PIPELINE SAFETY AND COMPLIANCE | agroff@washgas.com | 5713187993 |  |  |  |  | STACEY FORD | VP EHS-UTILITIES | 5716517504 | stacey.ford@washgas.com | ON MARCH 6, 2025, AT APPROXIMATELY 14:15, RP CONSTRUCTION STRUCK A 4-INCH PLASTIC GAS MAIN USING A DIRECTIONAL DRILL AT THE INTERSECTION OF CENTREVILLE ROAD AND SKYHAWK DRIVE IN CHANTILLY, VA. WASHINGTON GAS WAS PROMPTLY NOTIFIED OF THE INCIDENT AT 14:17 VIA FIREBOARD. THE IMPACT RESULTED IN A PUNCTURED PLASTIC MAIN, CAUSING A GAS LEAK. WASHINGTON GAS PERSONNEL ARRIVED ON-SITE AT 15:13 AND SUCCESSFULLY STOPPED THE GAS FLOW AT 19:29 BY SQUEEZE, WHICH LED TO AN OUTAGE AFFECTING 28 CUSTOMERS. SERVICE WAS RESTORED TO ALL IMPACTED CUSTOMERS.
2026-06-30 10:38 | NO | NO | NO | 20250025 | 41953 | 2025-04-30 15:27 | SUPPLEMENTAL FINAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2025-03-31 16:12 | EASTERN | NO | 2025 | PARK ST. | WATSONTOWN | NORTHUMBERLAND | PA | 17777 | 41.077 | -76.8578 | YES | [8 empty] | 2025-03-31 18:07 | 1427339 | 1427503 | NATURAL GAS |  | 9191 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 11 | 2025-03-31 16:12 |  |  |  | 2025-03-31 16:25 | 2025-03-31 16:26 | NO | PUBLIC PROPERTY | ABOVEGROUND | OVERHEAD CROSSING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | UNKNOWN |  |  |  |  | 6.625 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.276 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 18.9 | 1 |  | CLASS 3 LOCATION | 0 | 0 | 44823 | 44823 | 10000 | 10000 | 0 | 0 |  | 2.4 | 22058 | 22058 | 0 | 0 | 76881 | 40226.1722613570139403298969072164948454 | 76881 | 1 | 1 | 0 | 0 | 0 | 8 | 2 | 305 | 308 | 325 | 192.619(A)(3) | 1969-01-07 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.1 |  | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THEIR ACTIONS DID NOT WARRANT THE NEED FOR INVESTIGATION. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | [56 empty] | TREES/VEGETATION ROOTS | [5 empty] | YES |  |  |  | YES | STRONG WINDS, THUNDERSTORMS, HEAVY RAINS | [181 empty] | YES |  | YES | [29 empty] | CHAD REINER | STANDARDS ENGINEER | creiner@ugi.com | 484-577-6666 |  | JOHN TOUMEH | jtoumeh@ugi.com | 717-675-4606 | PAMELA JOCSAK | VP EHS AND TECHNICAL SUPPORT | 484-824-5508 | pjocsak@ugi.com | ***ON FEBRUARY 19, 2026 UGI IS FILING A SUPPLEMENTAL AND FINAL REPORT BASED ON FINDINGS FROM THE EVENT’S MATERIAL INVESTIGATION.*** AT 16:12 ON MARCH 31, 2025, UGI RECEIVED A CALL FROM THE LOCAL FIRE DEPARTMENT REGARDING A BREAK ON UGI'S HIGH PRESSURE 6" STEEL MAIN LINE. ONCE ON SITE IT WAS DISCOVERED THAT A LARGE DIAMETER DECAYING TREE FELL ONTO A PORTION OF EXPOSED MAIN THAT SPANNED A DRAINAGE TRENCH. HEAVY RAINSTORMS EXISTED AT THE TIME OF THE INCIDENT. THE TREE THAT DAMAGED THE MAIN WAS LOCATED OUTSIDE OF UGI'S PIPELINE RIGHT OF WAY. UGI EVACUATED ELEVEN INDIVIDUALS FROM EIGHT LOCAL HOMES. A CRITICAL VALVE WAS CLOSED TO STOP FLOW OF GAS, WHICH SHUT DOWN SERVICE TO ONE INDUSTRIAL AND ONE COMMERCIAL CUSTOMER. SERVICE WAS RESTORED TO ALL CUSTOMERS ON APRIL 1, 2025 AT APPROXIMATELY 18:15. LAB TESTING DETERMINED THAT THE FAILURE INITIATED AT THE GIRTH WELD. NO EVIDENCE OF SIGNIFICANT INTERNAL OR EXTERNAL CORROSION WAS OBSERVED ON THE PIPE OR THE GIRTH WELD. THE ROOT CAUSE OF THIS EVENT REMAINS NATURAL FORCE DAMAGE CAUSED FROM STRONG WINDS AND STORMY CONDITIONS THAT CAUSED A TREE TO UPROOT AND FALL ON THE MAIN.
2026-06-30 10:38 | NO | YES | NO | 20250026 | 40886 | 2025-05-09 14:05 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2025-04-10 15:29 | CENTRAL | YES | 2025 | 8075 FM 2757 | FORNEY | KAUFMAN | TX | 75126 | 32.6734 | -96.4736 | [5 empty] | YES |  |  |  | 2025-04-11 11:39 | 1428322 | 1428414 | NATURAL GAS |  | 1034 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-04-10 16:19 |  |  |  | 2025-04-10 16:19 | 2025-04-11 10:57 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 300 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2021 | 2021 |  |  |  |  | 8 | ASTM PE4710 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | MECHANICAL PUNCTURE | 5 | 5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 454000 | 454000 | 0 | 0 | 0 | 0 |  | 9.98 | 10319 | 10319 | 0 | 0 | 464319 | 192755.2249156921647010309278350515463918 | 464319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 70 | 99 | 192.619(A)(2) | 2021-12-07 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [5 empty] | YES |  |  | NO | NO | MEASURED DEPTH FROM GRADE | 300 | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | TX2559191862 | TEXAS 811 | NO | CONTRACT LOCATOR | NO | NO |  | NOTIFICATION ISSUE | EXCAVATOR DUG OUTSIDE AREA DESCRIBED ON TICKET | [170 empty] | BILL BROOKS | DIRECTOR OF REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 806-787-9422 |  | SERGIO PALACIOS | sergio.palacios@atmosenergy.com | 214) 673-5993 | MARC ROTHBAUER | VP COMPLIANCE AND REGULATORY REPORTING | 469-236-8616 | marc.rothbauer@atmosenergy.com | ON APRIL 10, 2025, A THIRD-PARTY EXCAVATOR DAMAGED AN ATMOS ENERGY 8-INCH POLYETHYLENE GAS MAIN. ATMOS ENERGY RECEIVED A NOTIFICATION FROM THE KAUFMAN COUNTY SHERIFFS DEPARTMENT AT 3:29 P.M. AN ATMOS ENERGY TECHNICIAN ARRIVED ON SITE AND GRADED THE LEAK AT 04:19 P.M. THE TECHNICIAN REQUESTED ADDITIONAL RESOURCES AT 4:24 P.M. THE RELEASE WAS SECURED AT 01:09 A.M. ON APRIL 11, 2025. CONFIRMED DISCOVERY OCCURRED ON APRIL 11, 2025, AT 10:57 A.M. WHEN AN ESTIMATE FOR PERMANENT REPAIRS WAS PRESENTED THAT EXCEEDED THE REPORTING THRESHOLD. AFTER FURTHER INVESTIGATION, IT WAS DETERMINED THAT THE THIRD-PARTY EXCAVATOR WAS DIGGING, BY OPEN TRENCH, OUTSIDE THE AREA DESCRIBED IN 811 LOCATE TICKET. THE MAIN WAS APPROXIMATELY 25 FEET DEEP WHERE DAMAGED. THE PERMANENT REPAIR WAS COMPLETED ON APRIL 12, 2025.
2026-06-30 10:38 | NO | YES | YES | 20250027 | 41239 | 2025-05-09 15:28 | SUPPLEMENTAL | 12606 | THE EMPIRE DISTRICT GAS COMPANY | 602 JOPLIN STREET | JOPLIN | MO | 64801 | 2025-04-09 16:20 | CENTRAL | YES | 2025 | 1717 FRANKLIN AVE | LEXINGTON | LAFAYETTE | MO | 64067 | 39.184 | -93.8744 |  | YES | [5 empty] | YES | TURNED OFF TWO GATE STATIONS TO ISOLATE SYSTEM | 2025-04-09 20:19 | 1428183 | 1428186, 1428188, 1428365 (48hr Update) | NATURAL GAS |  | 53.68 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 2025-04-09 19:42 | OTHER | TOWN GAS FLOW WAS SHUT DOWN AT CITY GATE STATIONS | 1 | YES | 2 | 2025-04-09 16:39 | YES | OPERATOR | 2025-04-09 20:08 | 2025-04-09 16:39 | 2025-04-09 16:39 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 | NO | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1989 | UNKNOWN |  |  |  |  | 4 | PE2406 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 525722 | 525722 | 616386 | 616386 | 44085 | 44085 | 0 | 0 |  | 7.0364 | 378 | 378 | 0 | 0 | 1186571 | 481972.995674728749819505154639175257732 | 1186571 | 223 | 0 | 1685 | 0 | 0 | 1685 | 223 | 30 | 30 | 35 | 192.619(A)(4) | 1988-12-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.1 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE | [12 empty] | YES | 6 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | UNKNOWN |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | YES | 18” – 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | MO250941591 |  | NO | FACILITY OWNER | UNKNOWN/OTHER | UNKNOWN/OTHER |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | UNDER NTSB INVESTIGATION,DOCKET#PLD25LR004 | [169 empty] | RONALD SNIDER | REGIONAL DIRECTOR OPERATIONS | ronald.snider@libertyutilities.com | 573-225-7834 |  |  |  |  | MICHAEL D BEATTY | PRESIDENT | 573-755-0108 | mike.beatty@libertyutilities.com | PLEASE REFER TO THE 05-05-2025 NTSB PRELIMINARY REPORT FOR ITS IN DOCKET# PLD25LR004, AVAILABLE AT THE LINK PROVIDED. (HTTPS://WWW.NTSB.GOV/INVESTIGATIONS/PAGES/PLD25LR004.ASPX) CONTAINS THE FOLLOWING DESCRIPTION OF THE INCIDENT: 'ON APRIL 9, 2025, ABOUT 7:42 P.M. LOCAL TIME, A NATURAL GAS-FUELED EXPLOSION AND FIRES IN LEXINGTON, MISSOURI, DESTROYED ONE SINGLE-FAMILY RESIDENCE (1717 FRANKLIN AVENUE) AND DAMAGED TWO OTHERS, RESULTING IN ONE FATALITY AND TWO INJURIES. THE EXPLOSION OCCURRED MORE THAN 3 HOURS AFTER ALFRA CONSTRUCTION, LLC, A DRILLING SUBCONTRACTOR INSTALLING A FIBER OPTIC LINE FOR SELLENRIEK CONSTRUCTION, DRILLED INTO AN UNMARKED SECTION OF A CAPPED UNDERGROUND GAS DISTRIBUTION MAIN LOCATED NEAR THE RESIDENCES. THE GAS MAIN WAS OPERATED BY LIBERTY UTILITIES, A SUBSIDIARY OF ALGONQUIN POWER AND UTILITIES CORPORATION, WHICH PROVIDES GAS SERVICE TO THE AREA. 'FIVE DAYS BEFORE THE ACCIDENT, ON APRIL 4, ALFRA CONSTRUCTION CALLED MISSOURI 811 TO HAVE ANY BURIED UTILITIES IN THE AREA MARKED.[2] LIBERTY UTILITIES SENT A LOCATOR TO MARK ITS ASSETS BY PAINTING AND FLAGGING AND REPORTED THAT THIS WORK WAS FINISHED ON APRIL 7.(3) THE LOCATION OF THE [CAPPED] GAS MAIN SECTION INVOLVED IN THE ACCIDENT WAS NOT IDENTIFIED OR MARKED DURING THIS PROCESS. 'SHORTLY AFTER 4:00 P.M. ON THE DAY OF THE ACCIDENT, THE ALFRA CONSTRUCTION WORK CREW MEMBER OPERATING THE DRILL FELT THE DRILL STRIKE AN OBJECT. THE WORK CREW SAW AND SMELLED ODORIZED NATURAL GAS BEING RELEASED. THE WORK CREW'S SUPERVISOR CALLED 911 AND 811 AND REPORTED A DAMAGED GAS LINE. UNITS FROM THE LEXINGTON FIRE DEPARTMENT ARRIVED ABOUT 4:20 P.M.; PERSONNEL FROM LIBERTY UTILITIES BEGAN ARRIVING ABOUT 4:39 P.M. LIBERTY UTILITIES PERSONNEL ATTEMPTED TO ISOLATE THE LEAK BY SQUEEZING OFF THE MAIN BUT DID NOT SUCCEED IN STOPPING THE FLOW OF GAS.[4] AT THE DIRECTION OF LIBERTY UTILITIES, A BUSINESS ABOUT 15 FEET FROM THE LEAK WAS EVACUATED BEFORE THE EXPLOSION. OTHER NEARBY BUILDINGS WERE NOT EVACUATED, INCLUDING THE DESTROYED AND DAMAGED RESIDENCES, WHICH RANGED FROM 80 TO 160 FEET FROM THE LEAK. THE DAMAGED MAIN WAS ISOLATED ABOUT 8:10 P.M., AFTER THE EXPLOSION. THE GAS MAIN INVOLVED IN THIS ACCIDENT WAS A 4-INCH POLYETHYLENE (PLASTIC) PIPE OPERATING AT 30 POUNDS PER SQUARE INCH GAUGE PRESSURE; ITS MAXIMUM ALLOWABLE OPERATING PRESSURE WAS 35 POUNDS PER SQUARE INCH GAUGE.'
2026-06-30 10:38 | NO | YES | NO | 20250028 | 41957 | 2025-05-16 11:47 | SUPPLEMENTAL FINAL | 13062 | NATIONAL FUEL GAS DISTRIBUTION CORP - NEW YORK | 6363 MAIN ST. | WILLIAMSVILLE | NY | 14221 | 2025-04-18 19:32 | EASTERN | YES | 2025 | 167 ORANGE ST | BUFFALO | ERIE | NY | 14204 | 42.8992 | -78.858 |  |  | YES | [6 empty] | 2025-04-18 20:36 | 1428915 | 1429005 | NATURAL GAS |  | 4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-04-18 19:32 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 4 | YES | 1 | 2025-04-18 19:36 |  |  |  | 2025-04-18 19:50 | 2025-04-18 20:02 | NO | PRIVATE PROPERTY | TRANSITION AREA | SOIL/AIR INTERFACE |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1933 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 185000 | 185000 | 300 | 300 | 3000 | 3000 | 0 | 0 |  | 3.09 | 12 | 12 | 0 | 0 | 188312 | 76470.8093534585802597938144329896907216 | 188312 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0.36 | 0.36 | 0.43 | 192.623 | 1933-08-16 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 1 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HOUSE SHIFTED DUE TO STRUCTURAL FAILURE CAUSING RISER TO BEND AT GROUND LEVEL | [110 empty] | YES | [43 empty] | STEVEN MONNIE | SENIOR MANAGER | monnies@natfuel.com | 814-871-8204 |  |  |  |  | CHRIS MAZERBO | ASSISTANT SUPERINTENDENT | 716-696-6451 | mazerboc@natfuel.com | AT APPROXIMATELY 19:36 (7:36 PM EST) ON APRIL 18, 2025, NATIONAL FUEL GAS DISTRIBUTION CORPORATION ("NFG") WAS NOTIFIED BY THE BUFFALO FIRE DEPARTMENT OF A POTENTIAL GAS RELATED FIRE AND EXPLOSION AT 167 ORANGE STREET. A NFG FIRST RESPONDER ARRIVED ON-SITE AT APPROXIMATELY 19:50 AND CONFIRMED DISCOVERY WAS MADE AT APPROXIMATELY 20:02 WHEN THE BELOW GRADE CURB VALVE WAS CLOSED TO SHUTOFF GAS FLOW TO THE RESIDENCE. NFG NOTIFIED THE NRC ON 4/18/2025 AT APPROXIMATELY 20:36 (NRC REPORT #1428915) AND MADE A 48-HOUR FOLLOW-UP NOTIFICATION ON 4/20/2025 AT APPROXIMATELY 17:20 (NRC REPORT #1429005). THERE WERE NO FATALITIES OR INJURIES NECESSITATING IN-PATIENT HOSPITALIZATION AS A RESULT OF THIS EVENT. THE RESIDENCE INVOLVED IN THE INCIDENT WAS OF "OFF-GRADE" CONSTRUCTION MEANING THE HOUSE WAS SUPPORTED BY NUMEROUS CINDERBLOCK PILINGS, MANY OF WHICH WERE TILTED. THIRD PARTY INVESTIGATION FOUND SIGNIFICANT ROT IN THE WOODEN RIM JOIST NEAR THE PILING CLOSEST TO THE SERVICE RISER, COMPROMISING THE STRUCTURAL INTEGRITY OF THE RESIDENCE. HORIZONTAL SHIFTING OF THE STRUCTURE EXERTED A FORCE ON THE SERVICE RISER CAUSING IT TO BEND. ACCELERATED, LOCALIZED ATMOSPHERIC CORROSION DEVELOPED ON THE EXTERIOR (TENSION SIDE) OF THE BEND EVENTUALLY LEADING TO A CRACK TO FORM IN THE RISER.
2026-06-30 10:38 | NO | NO | NO | 20250030 | 40919 | 2025-05-21 13:11 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2025-04-26 23:20 | EASTERN | YES | 2025 | 863 CLARKWAY DRIVE | EDEN | ROCKINGHAM | NC | 27288 | 36.5195 | -79.7716 | YES | [8 empty] | 2025-04-27 04:40 | 1429561 | 1429647 | NATURAL GAS |  | 628.02 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-04-26 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 628.02 | NO | 0 | 2025-04-26 23:47 |  |  |  | 2025-04-26 23:47 | 2025-04-26 23:47 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1983 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | VEHICLE DAMAGE BY DWI DRIVER TO REGULATOR STATION | CLASS 3 LOCATION | 0 | 0 | 43867 | 43867 | 1500 | 1500 | 0 | 0 |  | 4.5 | 2826 | 2826 | 0 | 0 | 48193 | 20723.2967492113634654432989690721649485 | 48193 | 0 | 0 | 50 | 0 | 0 | 50 | 0 | 54 | 54 | 60 | 192.619(A)(1) | 2002-10-22 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  |  | YES |  |  | YES | UNKNOWN | PASSENGER CAR | ROADWAY | 3 | YES |  | YES | [140 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | A GAS REGULATOR STATION WAS STRUCK BY A DWI DRIVER AND CAUGHT FIRE AS A RESULT. THE DAMAGE RESULTED IN 50 CUSTOMER OUTAGES.
2026-06-30 10:38 | NO | YES | YES | 20250031 | 41663 | 2025-05-22 12:11 | SUPPLEMENTAL FINAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2025-04-22 17:10 | CENTRAL | YES | 2025 | 9509 GRANDVIEW RD | KANSAS CITY | JACKSON | MO | 64137 | 38.9537 | -94.5499 |  | YES | [7 empty] | 2025-04-22 19:38 | 1429178 | 1429366 | NATURAL GAS |  | 186.22 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2025-04-22 18:08 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 159.62 | NO | 16 | 2025-04-22 17:10 | YES | OPERATOR | 2025-04-22 17:20 | 2025-04-22 17:36 | 2025-04-22 19:17 | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1929 | UNKNOWN |  |  |  |  | 10 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | .5" HOLE FROM 1-INCH NIPPLE | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 175915 | 175915 | 500 | 500 | 0 | 0 |  | 6.333 | 1179 | 1179 | 0 | 0 | 177594 | 72595.2334557581594047422680412371134021 | 177594 | 0 | 0 | 16 | 1 | 1 | 16 | 0 | 130.24 | 130 | 150 | 192.619(A)(3) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT RESULT IN ANY ABNORMAL PIPELINE OPERATION OR PRESSURES THAT CAUSED OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | YES | 2 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | 18” – 36” |  | UTILITY | BACKHOE/TRACKHOE | WATER | YES | 251045717 |  | YES | CONTRACT LOCATOR | YES | YES | 24 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [169 empty] | YES | ERIN MILKERT | MANAGER DISTRIBUTION INTEGRITY | erin.milkert@spireenergy.com | 314-349-2932 |  | ERIN MILKERT | erin.milkert@spireenergy.com | 314-349-2932 | RANDY WILSON | DIRECTOR - PIPELINE AND SYSTEM INTEGRITY | 205-337-1337 | randy.wilson@spireenergy.com | A THIRD-PARTY EXCAVATOR WAS BACKFILLING WHEN THEY DAMAGED A 1-INCH NIPPLE ON A 10-INCH STEEL NATURAL GAS PIPELINE. ALTHOUGH THE COMPANY'S PROCEDURES STATE THAT OPERATION OF MECHANIZED EQUIPMENT SHALL CEASE IMMEDIATELY AND SHALL NOT BE PERMITTED TO RESUME WHERE THERE IS A SUDDEN, UNCONTROLLED RELEASE OF GAS DURING EXCAVATION ACTIVITIES, A MINI EXCAVATOR WAS USED DURING THE COMPANY'S RESPONSE TO THE DAMAGE, AND THE NATURAL GAS IGNITED. THE CONDITION WAS MADE SAFE BY CLOSING TWO NEARBY VALVES AND REPAIR WAS COMPLETED BY REMOVING THE DAMAGED 1-INCH NIPPLE AND WELDING ON A PUMPKIN. TWO COMPANY EMPLOYEES WERE INJURED AS A RESULT OF THE INCIDENT AND TRANSPORTED TO THE HOSPITAL. ONE EMPLOYEE WAS ADMITTED FOR EXTENDED TREATMENT AND THE SECOND EMPLOYEE WAS TREATED AND RELEASED. THE MINI-EXCAVATOR AND A NEARBY REGULATOR STATION WERE ALSO DAMAGED BY THE FIRE DURING THE INCIDENT. A 48-HOUR UPDATE TO THE NRC WAS MADE ON APRIL 24, 2025, AT 15:34 - REPORT NUMBER 1429366
2026-06-30 10:38 | NO | YES | NO | 20250032 | 40926 | 2025-05-22 14:37 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2025-04-10 11:05 | EASTERN | YES | 2025 | 6769 GORDON ROAD | WILMINGTON | NEW HANOVER | NC | 28411 | 34.2639 | -77.8319 | [5 empty] | YES |  |  |  |  | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 946.82 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-04-10 11:14 | NO |  |  | 2025-04-10 11:51 | 2025-04-10 11:51 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 78 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2003 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 206970 | 206970 | 0 | 0 | 0 | 0 |  | 4.5 | 4261 | 4261 | 0 | 0 | 211231 | 87512.4691949606773884536082474226804124 | 211231 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | 55 | 55 | 75 | 192.619(A)(2) | 2003-02-20 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXCAVATION DAMAGE FROM A TELECOM INSTALL. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [5 empty] | NO | NO | > 36” |  | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | C250792179 |  | Unknown | CONTRACT LOCATOR | YES | YES | 8 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | CONTRACTOR BORED INTO A 6" PLASTIC MAIN WHILE INSTALLING A FIBER CONDUIT. THE DAMAGE RESULTED IN 7 CUSTOMER OUTAGES. USE OF MECHANIZED EQUIPMENT IN THE TOLERANCE ZONE & EXCAVATOR FAILED TO SUPPORT AND PROTECT FACILITIES. THE NATIONAL RESPONSE CENTER (NRC) WAS NOT NOTIFIED BECAUSE AT THE TIME OF THE INCIDENT IT WAS NOT EXPECTED TO MEET THE REPORTING THRESHOLD.
2026-06-30 10:38 | NO | YES | NO | 20250034 | 40992 | 2025-06-05 11:28 | ORIGINAL | 12438 | MIDDLE TENNESSEE NATURAL GAS UTIL DIST | P.O. BOX 670, 1030 WEST BROAD ST | SMITHVILLE | TN | 37166 | 2025-05-07 08:26 | CENTRAL | YES | 2025 | 9700 MANCHESTER HWY | MORRISON | WARREN | TN | 37357 | 35.6057 | -85.91 | YES |  | YES | YES | [5 empty] | 2025-05-13 17:29 | 1431008 | N/A | NATURAL GAS |  | 1693 | 408 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-05-07 08:26 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2025-05-07 09:07 | 2025-05-07 09:05 | 2025-05-07 09:05 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 168 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1990 | 1990 |  |  |  |  | 8 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.21 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 2 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 195282 | 195282 | 13500 | 13500 | 0 | 0 |  | 9.54 | 16151 | 16151 | 3892 | 3892 | 228825 | 101101.630763153640684618556701030927835 | 228825 | 41 | 11 | 122 | 0 | 0 | 122 | 52 | 296 | 296 | 350 | 192.619(A)(2) | 1990-05-07 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS CAUSED BY A 3RD PARTY AND A CONTROLLER HAD NO EFFECT ON THE OUTCOME. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | YES | [5 empty] | NO | YES | MEASURED DEPTH FROM GRADE | 168 | CONTRACTOR | DIRECTIONAL DRILLING | SEWER (SANITARY/STORM) | YES | 250993311 |  | YES | FACILITY OWNER | YES | YES | 13 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | MATT STENNETT | VICE PRESIDENT - ENGINEERING | mstennett@mtng.com | 931-754-3515 |  | MATT STENNETT | mstennett@mtng.com | 931-754-3515 | MATT STENNETT | VICE PRESIDENT - ENGINEERING | 931-754-3515 | mstennett@mtng.com | A CONTRACTOR WAS INSTALLING A SEWER MAIN USING A DIRECTIONAL DRILLER. DURING THE PROCESS THE CONTRACTOR DRILLED INTO AN 8-INCH DISTRIBUTION MAIN. ORIGINALLY WHEN THIS INCIDENT OCCURRED THE PRICE POINT FOR DAMAGE WAS SUSPECTED TO BE AROUND THE (30000) DOLLAR RANGE. IT WAS AFTER FURTHER INVESTIGATION THAT AN ADDITIONAL (400) FEET OF LINE WAS DAMAGED AND NEED TO BE REPLACED, UPPING THE PRICE POINT FOR DAMAGES.
2026-06-30 10:38 | NO | NO | NO | 20250035 | 40997 | 2025-06-06 07:55 | ORIGINAL FINAL | 4060 | ENBRIDGE GAS OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2025-05-07 11:33 | EASTERN | YES | 2025 | 1684 MECHANICSBURG ROAD | WOOSTER | WAYNE | OH | 44691 | 40.8174 | -81.9686 | YES | [8 empty] | 2025-05-07 12:09 | 1430464 | 1430588 | NATURAL GAS |  | 255 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-05-07 11:33 | ALLOWED TO BURN OUT |  | 5 | YES | 2 | 2025-05-07 10:39 | YES | OPERATOR | 2025-05-07 11:34 | 2025-05-07 11:00 | 2025-05-07 11:33 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 49 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2020 | 2019 |  |  |  |  | 4 | ASTM D2513 | POLYPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 30000 | 30000 | 500 | 500 | 14500 | 14500 | 0 | 0 |  | 4.45 | 1135 | 1135 | 0 | 0 | 46135 | 19197.0666641763090721649484536082474227 | 46135 | 0 | 0 | 37 | 0 | 0 | 38 | 0 | 55 | 55 | 80 | 192.619(A)(2) | 2020-03-27 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.4 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM WOULD NOT HAVE DETECTED LEAK DUE SMALL MAGNITUDE IN OVERALL SYSTEM OPERATION. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [5 empty] | NO | YES | MEASURED DEPTH FROM GRADE | 49 | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | A511502571 | OHIO 811 | YES | CONTRACT LOCATOR | YES | YES | 12 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | DANIEL EVANS | MANAGER GAS OPERATIONS | daniel.a.evans@dominionenergy.com | 3305715796 |  |  |  |  | DANIEL EVANS | MANAGER GAS OPERATIONS | 3305715796 | daniel.a.evans@dominionenergy.com | AT APPROXIMATELY 10:40AM EDT ON MAY 7, 2025, AN ENBRIDGE GAS OHIO 4" INTERMEDIATE PRESSURE (IP) DISTRIBUTION MAINLINE (MAOP 80PSIG) WAS DAMAGED BY A 3RD PARTY CONTRACTOR. THE CONTRACTOR WAS INSTALLING BROADBAND FIBER BY MEANS OF HORIZONTAL DIRECTIONAL DRILLING (HDD) IN A TRAILER PARK LOCATED AT 1684 MECHANICSBURG ROAD IN WOOSTER, OHIO. AFTER BEING NOTIFIED OF THE DAMAGE BY A CALL FROM THE EXCAVATOR, ENBRIDGE OPERATIONS ARRIVED AT THE SCENE AND BEGAN LEAK DETECTING TO DETERMINE THE EXACT LOCATION OF THE HIT. A VALVE SOUTH OF THE HIT LOCATION WAS FOUND AND OPERATIONS BEGAN DIGGING NORTH OF THE LOCATION TO SQUEEZE OFF THE MAIN LINE. BAR HOLING FOUND LOW LEVELS OF GAS UNDER THE SKIRT OF THE NEAREST MOBILE HOME AND THE TWO RESIDENTS WERE EVACUATED AS A PRECAUTION. AT APPROXIMATELY 11:30AM AN UNOCCUPIED TRAILER AT LOT 80 ON THE EAST SIDE OF ROSE BLVD EXPLODED. NO ONE WAS IN THE HOME AT THE TIME AND THERE WERE NO INJURIES OR FATALITIES. ENBRIDGE CREWS WERE WORKING ON ROSE BLVD AT THE TIME OF THE EXPLOSION, AND PLANNING TO BEGIN BAR HOLE TESTING OF LOT 80 WHILE CONTINUING TO MAKE EFFORTS TO ISOLATE THE LINE. IT IS BELIEVED THAT THE GAS HAD MIGRATED UNDERGROUND VIA AN UNDETERMINED PATHWAY TO THE TRAILER ON LOT 80 AND ACCUMULATED IN THE SKIRT UNDERNEATH THE TRAILER UNTIL AN UNKNOWN IGNITION SOURCE CAUSED THE EXPLOSION. OPERATIONS CREWS SUBSEQUENTLY CLOSED THE VALVE FEEDING THE ENTIRE TRAILER PARK AND CONTINUED BAR HOLING THE SURROUNDING AREA. 911 WAS CALLED AND ALL RESIDENTS WERE EVACUATED. THE WOOSTER FIRE DEPARTMENT AND POLICE DEPARTMENT ARRIVED SHORTLY AFTER. NOTIFICATIONS OF THE INCIDENT WERE COMPLETED TO THE NATIONAL RESPONSE CENTER AND PUBLIC UTILITIES COMMISSION OF OHIO AT APPROXIMATELY 12:15PM. THE ENBRIDGE DAMAGE PREVENTION TEAM CONFIRMED THAT AN 811 TICKET HAD BEEN CALLED IN BY THE DAMAGING PARTY AND THAT ENBRIDGE FACILITIES HAD BEEN PROPERLY MARKED AT THE HIT LINE LOCATION. ENBRIDGE OPERATIONS EXCAVATED THE HIT LINE LOCATION AND CONFIRMED THE 3RD PARTY COMPANY HAD STRUCK THE 4" IP MAINLINE WITH THE 2" PILOT BORE, AND THE 3RD PARTY HAD NOT DAYLIGHTED THE MAINLINE PRIOR TO THE DAMAGE. SUBSEQUENT TESTING FOUND THAT ENBRIDGE FACILITIES IN THE AREA WERE OPERATING COMPLIANTLY. APPROXIMATELY 37 CUSTOMERS WERE OUT OF SERVICE DUE TO THE CLOSURE OF THE VALVE TO THE TRAILER PARK TO ISOLATE THE SYSTEM. AFTER CUTTING OUT AND REPLACING THE SECTION OF DAMAGED MAIN, EGO CREWS PURGED THE MAINLINE BACK INTO SERVICE AND BEGAN LIGHT UPS TO EFFECTED CUSTOMERS AT 8:00PM AND COMPLETED TURN-ONS AT 11:00PM TO ALL BUT 7 CUSTOMERS DUE TO NO ACCESS. THE REMAINING 7 CUSTOMERS WERE RESTORED TO SERVICE IN THE FOLLOWING DAYS AS THEY GRANTED ACCESS. AFTER REPORTING THE EVENT TO THE NRC, IT WAS DETERMINED THAT THE EVENT DID NOT MEET THE CRITERIA DEFINED IN §191.3(1) FOR AN INCIDENT, BUT ENBRIDGE IS FILING THIS REPORT UNDER §191.3(3) AS A SIGNIFICANT EVENT THAT COULD HAVE RESULTED IN MORE SEVERE OUTCOMES.
2026-06-30 10:38 | NO | NO | NO | 20250036 | 41073 | 2025-06-18 14:14 | SUPPLEMENTAL FINAL | 18408 | DOMINION ENERGY SOUTH CAROLINA, INC. | 601 TAYLOR ROAD | CAYCE | SC | 29033 | 2025-05-03 14:07 | EASTERN | NO | 2025 | HARDEN ST. @ SLIGHS AVE. | COLUMBIA | RICHLAND | SC | 29205 | 34.0244 | -81.0273 |  | YES |  |  |  |  | YES |  |  | 2025-05-05 11:42 | 1430255 | 1430444 | NATURAL GAS |  | 4173 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-05-03 14:07 | YES | OPERATOR | 2025-05-03 14:07 | 2025-05-03 14:45 | 2025-05-03 14:07 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1982 | UNKNOWN |  |  |  |  | 2 | ASTM D2513 | ALDYL A | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 2 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 48630 | 48630 | 0 | 0 | 0 | 0 |  | 7.09 | 29587 | 29587 | 0 | 0 | 78217 | 43843.3106946741602032989690721649484536 | 78217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 45 | 60 | 192.619(A)(2) | 1982-12-08 | PRESSURE DID NOT EXCEED MAOP | DRIP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CALL IN BY THE THIRD-PARTY CONTRACTOR. THIS WAS A 2" DISTRIBUTION MAIN. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | YES | > 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | 2504172523 |  | Unknown | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [143 empty] | YES | [26 empty] | JOHNNY EUGENE EUSTACE | COMPLIANCE SUPERVISOR | johnny.e.eustace@dominionenergy.com | 8039771302 |  |  |  |  | JOHNNY EUGENE EUSTACE | COMPLIANCE SUPERVISOR | 8039771302 | johnny.e.eustace@dominionenergy.com | A THIRD-PARTY CONTRACTOR CAME INTO CONTACT WITH A 2" PL GAS MAIN AT HARDEN ST. AND SLIGHS AVE. IN COLUMBIA, SC ON THE AFTERNOON OF SATURDAY, MAY 3, 2025. NO CUSTOMERS EXPERIENCED AN INTERRUPTION OF GAS SERVICE AS A RESULT OF THE INCIDENT. THE REPAIR COST WAS OVER THE $5000.00 REPORTABLE THRESHOLD. THE TOTAL COST OF REPAIR IS: $78,217.65. THE LOST GAS EXCEEDED THE 3000 MCF PHMSA REPORTABLE THRESHOLD AND TOTALED 4173 MCF.
2026-06-30 10:38 | NO | YES | NO | 20250037 | 41092 | 2025-07-01 14:57 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2025-06-05 15:00 | CENTRAL | YES | 2025 | 174 CYPRESS ST | ABILENE | TAYLOR | TX | 79602 | 32.4503 | -99.7342 |  | YES |  |  |  |  | YES |  |  | 2025-06-05 19:08 | 1433245 | 1433347 | NATURAL GAS |  | 204 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 10 | 2025-06-05 15:29 | YES | OPERATOR | 2025-06-05 15:29 | 2025-06-05 15:29 | 2025-06-25 14:55 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | UNKNOWN |  |  |  |  | 10 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 6 | 8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 461744 | 461744 | 0 | 0 | 0 | 0 |  | 10.159 | 2072 | 2072 | 0 | 0 | 463816 | 189183.1221463899859457319587628865979381 | 463816 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 0.4 | 0.4 | 0.75 | 192.619(A)(1) | 1969-11-12 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | 18” – 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | CURB/SIDEWALK | YES | 2564834420 | TEXAS 811 | YES | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | BILL BROOKS | DIRECTOR OF REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 806-787-9422 |  | EVA DAMIANO | eva.damiano@atmosenergy.com | 325-690-7506 | MARC ROTHBAUER | VP COMPLIANCE AND REGULATORY REPORTING | 214-206-2912 | marc.rothbauer@atmosenergy.com | ON JUNE 5, 2025, AT APPROXIMATELY 3:18 P.M., ATMOS ENERGY RECEIVED A CALL REPORTING A DAMAGE TO OUR FACILITIES AT 174 CYPRESS STREET, ABILENE, TEXAS. THE 10-INCH LOW PRESSURE MAIN WAS DENTED SEVERAL TIMES AND PUNCTURED IN ONE LOCATION CAUSING A RELEASE OF GAS. THIS AREA WAS ACCURATELY MARKED BY ATMOS ENERGY’S LOCATOR CONTRACTOR ON MAY 30, 2025 IN RESPONSE TO A LOCATE TICKET RECEIVED ON MAY 28, 2025. THE THIRD-PARTY CONTRACTOR WAS REMOVING TREES ALONG THE CITY SIDEWALK, WITH MECHANIZED EQUIPMENT, AND FAILED TO MAINTAIN CLEARANCE OF THE MARKED LINES. THE RELEASE WAS SECURED AT 3:13 A.M. ON JUNE 6, 2025. CONFIRMED DISCOVERY OF THIS EVENT OCCURRED ON JUNE 25, 2025, AT 2:55 P.M., WHEN THE ESTIMATE TO REPLACE THE DAMAGED SEGMENTS OF MAIN WAS PREPARED. NOTE THAT THE NUMBER IN A22 REFLECTS THE NUMBER OF BUSINESSES THAT WERE EVACUATED. THE NUMBER OF INDIVIDUALS WHO EXITED THOSE BUSINESSES IS UNKNOWN.
2026-06-30 10:38 | NO | YES | YES | 20250038 | 41098 | 2025-07-01 21:14 | ORIGINAL | 18104 | CPS ENERGY | 500 MCCULLOUGH | SAN ANTONIO | TX | 78215 | 2025-05-31 21:46 | CENTRAL | NO | 2025 | 7914 LAUREL BEND | SAN ANTONIO | BEXAR | TX | 78250 | 29.5165 | -98.6849 | [7 empty] | YES | SERVICE TAPPING TEE | 2025-06-01 05:43 | 1432760 |  | NATURAL GAS |  | 316.8 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2025-05-31 21:46 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.01 | YES | 8 | 2025-05-31 21:56 |  |  |  | 2025-05-31 22:35 | 2025-05-31 23:45 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 42 | YES | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1980 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1.315 | ASTM 2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3350 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 200000 | 200000 | 0 | 0 | 16000 | 16000 | 0 | 0 |  | 8.7 | 2756 | 2756 | 0 | 0 | 218756 | 89953.4663797988608659793814432989690722 | 218756 | 0 | 0 | 1 | 0 | 0 | 5 | 0 | 12 | 9 | 33 | 192.619(A)(2) | 1980-03-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.1 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DURING THE INITIAL FAILURE INVESTIGATION ALL FACTORS WERE REVIEWED, THE CONTROLLER'S ACTION OR CONTROL ROOM ISSUES WERE NOT DETERMINED TO BE A CONTRIBUTING FACTOR. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 1980 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [13 empty] | YES | CPS ENERGY CONTINUES TO INVESTIGATE WHETHER A CONSTRUCTION DEFECT, MATERIAL DEFECT, WEATHER AND/OR GROUND MOVEMENT, OR A COMBINATION OF THOSE FACTORS, CAUSED OR CONTRIBUTED TO THIS INCIDENT. A DETERMINATION HAS NOT YET BEEN MADE. ITEMS NUMBERED 11 AND 12 ON THIS PAGE ARE REQUIRED FOR FORM SUBMITTAL. ACCORDINGLY, CPS ENERGY WILL CHOOSE “OTHER” ON NUMBER 11 AND PICK THE FIRST DROP DOWN OPTIONS ON NUMBER 12. | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [50 empty] | YES | [35 empty] | THOMAS E LINERODE | MGR GAS OPERATIONS COMPLIANCE | telinerode@cpsenergy.com | 2102191322 |  |  |  |  | THOMAS E LINERODE | MGR GAS OPERATIONS COMPLIANCE | 2102191322 | telinerode@cpsenergy.com | ON 5/31/2025, THE CPS ENERGY SYSTEM OPERATOR RECEIVED CALLS FROM THE SAN ANTONIO FIRE DEPARTMENT INDICATING A STRUCTURE FIRE. THE ADDRESS PROVIDED TO CPE ENERGY WAS 7902 LAUREL BEND. AT APPROXIMATELY 9:56 P.M., A GAS FIRE ORDER WAS CREATED, AND CPS ENERGY DISPATCHED A GAS TROUBLEMEN (C/K/A A GAS TECHNICIAN) TO THE SCENE. THE GAS TROUBLEMAN ARRIVED AT APPROXIMATELY 10:35 P.M. AND FOUND THE STRUCTURE AT 7914 LAUREL BEND TO HAVE BEEN DAMAGED IN AN EXPLOSION AND FIRE. THE GAS TROUBLEMAN, ACTING AS A FIRST RESPONDER, BEGAN MAKING THE SCENE SAFE, EVACUATING THE RESIDENTS OF LAUREL BEND, AND ENSURING CPS ENERGY GAS AND ELECTRIC SERVICE METERS WERE SHUT OFF FOR THE SUBJECT PROPERTY AND THE SURROUNDING. HOMES INCLUDING 7926, 7922, 7918, AND 7910 LAUREL BEND. HE THEN BEGAN BAR HOLE TESTING NEAR 7914 LAUREL BEND. UPON SEEING POSITIVE READS, HE CONTACTED HIS FOREMAN AND RELAYED THAT THERE HAD BEEN AN INCIDENT POSSIBLY INVOLVING NATURAL GAS. THE FOREMAN CONTACTED THE CPS ENERGY MANAGER OF GAS SERVICES AND HEADED TO THE SCENE TO ASSIST THE TROUBLEMAN. THE MANAGER ARRIVED AT APPROXIMATELY 11:45 P.M. AND, AFTER CONSULTING WITH THE TROUBLEMAN, THE FOREMAN, AND FIRE CREWS, DETERMINED THAT NATURAL GAS MAY HAVE BEEN INVOLVED IN THE EXPLOSION. ACCORDINGLY, THE MANAGER CALLED IN ADDITIONAL PERSONNEL, NOTIFIED THE DIRECTOR OF GAS CONSTRUCTION AND THE VICE PRESIDENT OF GAS SOLUTIONS, AND CONTACTED THE RAILROAD COMMISSION AT APPROXIMATELY 12:05 A.M. ON 6/1/2025. THE CPS ENERGY CREW AT THE SCENE, WHICH WAS COMPRISED OF VARIOUS CRAFTS AND SPECIALTIES, INCLUDING A LEAK CREW, CONTINUED BAR HOLE TESTING AND PERFORMING OTHER ANALYSES OF CPS ENERGY EQUIPMENT AND FACILITIES THROUGHOUT THE NIGHT. ADDITIONAL RESOURCES WERE CALLED AS APPROPRIATE AND AS NEEDED TO ASSIST THE CREW AND THE DISPLACED RESIDENTS OF LAUREL BEND. A REPRESENTATIVE OF THE RAILROAD COMMISSION ARRIVED ON SCENE AT APPROXIMATELY 8:45 A.M. CPS ENERGY FOUND A LEAK AT THE BUTT FUSE TO THE SERVICE TAP TO 7918 LAUREL BEND AT APPROXIMATELY 10:00 A.M. ON 6/1/2025. A CPS ENERGY LEAK CREW STOPPED THAT LEAK SHORTLY THEREAFTER AT APPROXIMATELY 10:20 A.M. AND MADE THE NECESSARY REPAIR. DURING THE COURSE OF THE INVESTIGATION OF THE AREA, CPS ENERGY CREWS ALSO DISCOVERED WHAT MAY HAVE BEEN A MINISCULE LEAK AT THE SERVICE TAP CAP AT 7914 LAUREL BEND AND FOUND A PITTED RISER AT 7922 LAUREL BEND. CPS ENERGY DOES NOT BELIEVE EITHER OF THESE TWO CONDITIONS CAUSED OR CONTRIBUTED TO THIS EVENT. IN FACT, THE SOAP BUBBLE ONE CREW MEMBER CLAIMS TO HAVE SEEN AT THE CAP AT 7914 LAUREL BEND WAS UNOBSERVABLE TO THE REST OF THE CREW AND MAY HAVE BEEN A RESULT OF THE DIGGING. HOWEVER, BOTH WERE REMEDIATED OUT OF AN ABUNDANCE OF CAUTION.
2026-06-30 10:38 | NO | YES | NO | 20250039 | 41341 | 2025-07-06 03:23 | SUPPLEMENTAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2025-06-06 10:30 | CENTRAL | YES | 2025 | WOLF'S CROSSING RD AND 5TH ST | OSWEGO | KENDALL | IL | 60543 | 41.6921 | -88.2929 | [5 empty] | YES | YES |  |  | 2025-06-06 15:08 | 1433337 | 1433523 | NATURAL GAS |  | 2329 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-06-06 10:30 | OTHER | FLOW CONTROL CUT OFF FUEL (NATURAL GAS) TO THE FIRE AT THE DAMAGE LOCATION. | 2329 | NO | 0 | 2025-06-06 10:51 |  |  |  | 2025-06-06 11:10 | 2025-06-06 14:00 | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2025 | UNKNOWN |  |  |  |  | 6 | ASTM D2513 | J.M. EAGLE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2708 | MECHANICAL PUNCTURE | 36 | 10 | [7 empty] | CLASS 3 LOCATION | 500000 | 500000 | 17200 | 17200 | 16500 | 16500 | 0 | 0 |  | 5.4 | 12577 | 12577 | 0 | 0 | 546277 | 226957.1704309454585855670103092783505155 | 546277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 58 | 60 | 192.619(A)(2) | 2025-04-18 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | 18” – 36” |  | DEVELOPER | GRADER/SCRAPER | GRADING | YES | A251432401 | J.U.L.I.E. (ILLINOIS) | YES | CONTRACT LOCATOR | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | JOSE L. DELREAL | MANAGER - OPERATIONS QUALITY ASSURANCE | jdelrea@southernco.com | 6309184934 |  | JOSE L. DELREAL | jdelrea@southernco.com | 6309184934 | PAMELA L. REID | MANAGER - COMPLIANCE AND QA | 2244570663 | preid@southernco.com | WHILE GRADING THE AREA, THE GRADER STRUCK THE GAS MAIN RELEASING GAS TO ATMOSPHERE. THE RELEASED GAS IGNITED, DAMAGING THE GRADER AND AN ADDITIONAL TWO PIECES OF CONSTRUCTION EQUIPMENT. THE FIRE SERVICE RESPONDED TO THE INCIDENT. THE FIRE WAS CONTAINED TO THE AREA OF THE DAMAGE AND WAS ALLOWED TO BURN BY THE FIRE SERVICE. THE FIRE WAS EXTINGUISHED SOON AFTER NICOR GAS CREWS STOPPED THE GAS FLOW AT THREE LOCATIONS AWAY FROM THE FIRE. DUE TO THE EXTENSIVE GRADING ACTIVITY, THE DEPTH OF THE DAMAGED 6" PE WAS DIFFICULT TO ASCERTAIN. THE RESPONSES TO PART B, ITEM 3A AND G3, ITEM 8, ARE ESTIMATED BASED ON ANOTHER LOCATION EXPOSED FURTHER TO THE EAST OF THE INCIDENT SITE. THIS FACILITY WAS NEWLY INSTALLED. THE AS-BUILT WAS STILL BEING PROCESSED BY THE GIS DEPARTMENT AT THE TIME OF THE DAMAGE. THE CALL TO THE NATIONAL RESPONSE CENTER WAS INITIATED AT 14:47. HOWEVER, THE CALL WAS ON HOLD FOR APPROXIMATELY 21 MINUTES BEFORE AN NRC OPERATOR TOOK THE CALL AND BEGAN TAKING INFORMATION ON THE INCIDENT.
2026-06-30 10:38 | NO | YES | YES | 20250040 | 41629 | 2025-07-12 22:06 | SUPPLEMENTAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2025-06-12 14:05 | CENTRAL | YES | 2025 | 14109 KENNETH COURT | CRESTWOOD | COOK | IL | 60445 | 41.636 | -87.7293 |  |  |  | YES | [5 empty] | 2025-06-12 18:27 | 1433929 | 1434029 | NATURAL GAS |  | 5.74 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2025-06-12 14:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 5.74 | YES | 0 | 2025-06-12 14:56 |  |  |  | 2025-06-12 14:51 | 2025-06-12 14:56 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1992 | 1992 | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.625 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 2406 | LEAK |  |  | OTHER | STILL UNDER INVESTIGATION | [5 empty] | CLASS 3 LOCATION | 308043 | 308043 | 200 | 200 | 11692 | 11692 | 0 | 0 |  | 5.4 | 31 | 31 | 0 | 0 | 319966 | 129937.9484480446739911340206185567010309 | 319966 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 24.69 | 25 | 28 | 192.619(A)(2) | 1992-12-10 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | PAMELA L. REID | MANAGER - COMPLIANCE AND QA | preid@southernco.com | 2244570663 |  | PAMELA L. REID | preid@southernco.com | 2244570663 | PAMELA L. REID | MANAGER - COMPLIANCE AND QA | 2244570663 | preid@southernco.com | PER NATIONAL TRANSPORTATION SAFETY BOARD ("NTSB") INVESTIGATION ID PLD25FR006, THE FOLLOWING INFORMATION IS PRELIMINARY AND SUBJECT TO CHANGE. ON JUNE 12, 2025, A NATURAL GAS-FUELED EXPLOSION AND FIRE DESTROYED A SINGLE-FAMILY RESIDENCE AT 14109 KENNETH COURT IN CRESTWOOD, ILLINOIS. THE EXPLOSION KILLED ONE PERSON AND DAMAGED NEIGHBORING RESIDENCES. NICOR GAS PROVIDED NATURAL GAS SERVICE TO THE HOME AND THE NEIGHBORING RESIDENCES. THE CRESTWOOD FIRE DEPARTMENT RESPONDED TO THE EXPLOSION AND FIRE AT ABOUT 2:16 P.M. NICOR GAS ARRIVED ON THE SCENE AT ABOUT 2:40 P.M. AND DISCONNECTED AND CAPPED THE SERVICE LINE AT ABOUT 4:44 P.M. ON JUNE 13, 2025, NICOR GAS PERFORMED A PRESSURE TEST OF THE SERVICE LINE. THE SERVICE LINE DID NOT HOLD PRESSURE, INDICATING A LEAK. AFTER NATIONAL TRANSPORTATION SAFETY BOARD (NTSB) INVESTIGATORS ARRIVED ON SCENE, NICOR GAS PERFORMED FLOW TESTS ON THE SERVICE LINE TO ESTIMATE THE SIZE OF THE LEAK. BARHOLE TESTING CONDUCTED BY NICOR GAS CONFIRMED THE PRESENCE OF GAS IN THE GROUND NEAR THE FOUNDATION OF THE HOME. NICOR GAS LOCATED AND MARKED UNDERGROUND UTILITIES AT THE ACCIDENT SITE AND OBTAINED GAS CONSUMPTION DATA FROM THE HOME’S GAS METER. THE AMI DEVICE REGISTERED UNUSUALLY HIGH USAGE AT THIS PREMISE PRIOR TO THE INCIDENT. THE INVESTIGATION AS TO THE CAUSE OF THE INCIDENT IS ONGOING. WHILE ON SCENE, NTSB INVESTIGATORS COMPLETED THE FOLLOWING ACTIONS: EXAMINED THE ACCIDENT SITE, SECURED A SECTION OF THE SERVICE LINE CONTAINING THE LEAK FOR EXAMINATION AT THE NTSB’S MATERIALS LABORATORY IN WASHINGTON, DC, REVIEWED THE ACCIDENT HOME’S GAS CONSUMPTION DATA OVER THE PAST YEAR, WHICH WAS HIGHER THAN THE NEIGHBORING RESIDENCES, REQUESTED DOCUMENTATION FROM NICOR GAS, REQUESTED COMMUNICATION LOGS FROM NICOR GAS AND THE CRESTWOOD FIRE DEPARTMENT, AND CONDUCTED INTERVIEWS. (HTTPS://WWW.NTSB.GOV/INVESTIGATIONS/PAGES/PLD25FR006.ASPX)
2026-06-30 10:38 | NO | YES | YES | 20250041 | 42149 | 2025-07-21 12:24 | SUPPLEMENTAL FINAL | 4060 | ENBRIDGE GAS OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2025-06-23 16:17 | EASTERN | YES | 2025 | 7051 GARDEN VALLEY AVE | CLEVELAND | CUYAHOGA | OH | 44104 | 41.4738 | -81.6394 |  |  | YES | YES | [5 empty] | 2025-06-23 18:01 | 1434926 | 1435113 | NATURAL GAS |  | 0 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 4 | 4 | YES | 2025-06-23 16:17 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 5 | YES | 150 | 2025-06-23 17:07 |  |  |  | 2025-06-23 17:05 | 2025-06-23 17:07 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | 2009 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES |  |  |  | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | UNKNOWN AT THIS TIME | CLASS 3 LOCATION | 2500000 | 2500000 | 2500 | 2500 | 7500 | 7500 | 0 | 0 |  | 3.7 | 0 | 0 | 0 | 0 | 2510000 | 1019209.77565338052 | 2510000 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0.45 | 0.45 | 1 | 192.623 | 1959-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.5 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SIZE OF RELEASE NOT LARGE ENOUGH TO AFFECT SYSTEM PRESSURES. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | DANIEL EVANS |  | daniel.a.evans@dominionenergy.com |  |  | DANIEL EVANS | daniel.a.evans@dominionenergy.com | 3305715796 | DANIEL EVANS | MANAGER PIPELINE SAFETY | 3305715796 | daniel.a.evans@dominionenergy.com | NARRATIVE EXCEEDS CHARACTER LIMIT. COMPLETE NARRATIVE EMAILED TO USDOT PHMSA ACCIDENT INVESTIGATION DIVISION ON 4/10/26
2026-06-30 10:38 | NO | YES | NO | 20250043 | 41189 | 2025-07-30 15:57 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2025-07-16 09:13 | CENTRAL | YES | 2025 | 6511 CLARKSVILLE HIGHWAY | JOELTON | DAVIDSON | TN | 37080 | 36.3215 | -86.9078 | YES | [8 empty] | 2025-07-16 16:21 | 1437101 | 1437238 | NATURAL GAS |  | 12 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-07-16 08:13 | ALLOWED TO BURN OUT |  | 12 | NO | 0 | 2025-07-16 09:13 | YES | OPERATOR | 2025-07-16 09:46 | 2025-07-16 10:15 | 2025-07-16 10:15 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1997 | 1995 | [7 empty] | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.365 | [6 empty] | OTHER | [8 empty] | LIGHTNING STRUCK VALVE. | CLASS 2 LOCATION | 0 | 0 | 250000 | 250000 | 5000 | 5000 | 0 | 0 |  | 4.6 | 55 | 55 | 0 | 0 | 255055 | 103590.0100660712496907216494845360824742 | 255055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 130 | 150 | 192.619(A)(4) | 1997-01-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LIGHTNING STRUCK VALVE. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | ON THE MORNING OF JULY 16TH, 2025, THERE WAS INCLEMENT WEATHER IN THE AREA. GAS CONTROL NOTIFIED LOCAL OPERATIONS OF A HIGH-PRESSURE ALARM AT K.P. STATION. LOCAL OPERATIONS WERE DISPATCHED TO THE SCENE WHERE THEY CAME UPON AN IGNITION EVENT AT THE STATION. OPERATIONS CONTACTED GAS CONTROL TO ISOLATE THE OUTLET OF THE STATION AND THE LOCAL FIRE DEPARTMENT. THE SUPPLIER WAS CONTACTED TO SHUT IN THE INLET TAP OF THE STATION. FIRE WAS ALLOWED TO BURN OUT, AND ONCE SITE WAS DEEMED SAFE, INVESTIGATION AND REPAIRS BEGAN. THE DAMAGED RUN OF THE STATION WAS LOCKED OUT. THE STATION WAS BROUGHT BACK INTO SERVICE USING THE UNDAMAGED RUN. REPAIR COMPLETED AND STATION PUT BACK IN SERVICE.
2026-06-30 10:38 | NO | YES | YES | 20250045 | 41419 | 2025-08-01 21:04 | SUPPLEMENTAL FINAL | 12876 | ENBRIDGE GAS UTAH/ WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2025-07-05 22:17 | MOUNTAIN | YES | 2025 | 5174 W 13400 S (SUITE 102) | HERRIMAN | SALT LAKE | UT | 84096 | 40.5081 | -112.0143 | [5 empty] | YES |  |  |  | 2025-07-06 00:24 | 1436117 | 1436255 | NATURAL GAS |  | 72.53 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES | 2025-07-05 22:17 | OPERATOR/CONTRACTOR |  | 0 | YES | 0 | 2025-07-05 23:20 |  |  |  | 2025-07-05 23:00 | 2025-07-05 23:00 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 2013 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 10 |  |  | 2708 | OTHER | [8 empty] | VEHICLE STRUCK RISER. | CLASS 3 LOCATION | 3500000 | 3500000 | 0 | 0 | 5015 | 5015 | 0 | 0 |  | 8.05 | 584 | 584 | 0 | 0 | 3505599 | 1423720.86863161026722329896907216494845 | 3505599 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 45 | 45 | 60 | 192.619(A)(2) | 2013-10-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 45 | NO | [118 empty] | YES | [23 empty] | STEVE BURSETT | SUPERVISOR PIPELINE COMPLIANCE | steve.bursett@dominionenergy.com | 801-548-7520 |  | STEVE BURSETT | steve.bursett@dominionenergy.com | 801-548-7520 | RYAN JAMISON | MANAGER GAS OPERATIONS | 801-574-0111 | ryan.jamison@dominionenergy.com | ENBRIDGE GAS UTAH RESPONDED WHEN A VEHICLE HIT A1 1/4” RISER LOCATED APPROXIMATELY 45 FEET FROM THE STREET CAUSING A RELEASE OF GAS, FIRE, AND AN EVENTUAL EXPLOSION. THE RISER WAS FED BY A 6-INCH MAIN. DUE TO THE SERVICE LINE TAP’S PROXIMITY TO THE FIRE, IT COULD NOT BE ACCESSED AND THE 6-INCH MAIN HAD TO BE SQUEEZED OFF IN TWO LOCATIONS TO SHUT OFF THE FLOW OF NATURAL GAS. THREE INDIVIDUALS WERE TRANSPORTED TO HOSPITAL AS A RESULT OF THE VEHICLE ACCIDENT AND SUBSEQUENT IGNITION OF ESCAPING GAS, CONSISTING OF TWO VEHICLE OCCUPANTS AND ONE BYSTANDER WHO TRIED TO ASSIST THE VEHICLE OCCUPANTS. NOTE: IN REFERENCE TO SECTION A, 22 "NUMBER OF GENERAL PUBLIC EVACUATED", ANY EVACUATIONS WERE CONDUCTED BY THE FIRE DEPARTMENT PRIOR TO EGUWI'S ARRIVAL AND ACTUAL NUMBER IS NOT KNOWN.
2026-06-30 10:38 | NO | YES | NO | 20250046 | 41238 | 2025-08-08 19:18 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2025-07-10 15:00 | CENTRAL | YES | 2025 | 6225 CROMWELL MARINE CREEK RD | FORT WORTH | TARRANT | TX | 76179 | 32.8524 | -97.4186 |  | YES |  |  |  | YES |  |  |  | 2025-07-15 17:35 | 1436999 | 1437154 | NATURAL GAS |  | 204 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-07-10 16:35 |  |  |  | 2025-07-10 16:35 | 2025-07-15 16:23 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 180 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2023 | 2023 |  |  |  |  | 6 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 284000 | 284000 | 0 | 0 | 0 | 0 |  | 10.664 | 2175 | 2175 | 0 | 0 | 286175 | 117092.338479892087587628865979381443299 | 286175 | 0 | 0 | 1656 | 0 | 0 | 1656 | 0 | 43 | 43 | 60 | 192.619(A)(2) | 1969-11-12 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2568982587 | TEXAS 811 | Unknown | CONTRACT LOCATOR | YES | YES | 33 | NOTIFICATION ISSUE | EXCAVATOR DUG OUTSIDE AREA DESCRIBED ON TICKET | [170 empty] | BILL BROOKS | DIRECTOR OF REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 806-787-9422 |  | BRANDON WALTON | brandon.walton@atmosenergy.com | 214-491-0443 | MARC ROTHBAUER | VP COMPLIANCE AND REGULATORY REPORTING | 469-236-8616 | marc.rothbauer@atmosenergy.com | ON JULY 10, 2025, AT APPROXIMATELY 3:00 P.M., ATMOS ENERGY RECEIVED NOTIFICATION THAT A THIRD-PARTY EXCAVATOR HAD DAMAGED A 6-INCH POLYETHYLENE GAS MAIN. AN ATMOS ENERGY TECHNICIAN ARRIVED ON SITE AND GRADED THE LEAK AT 04:35 P.M. THE TECHNICIAN REQUESTED ADDITIONAL RESOURCES AT 4:36 P.M. THE RELEASE WAS SECURED AT APPROXIMATELY 12:00 A.M. ON JULY 11, 2025. DUE TO THE THIRD-PARTY DAMAGE, ON JULY 11, 2025, AT APPROXIMATELY 3:00 A.M., AN OUTAGE OF 1656 CUSTOMERS OCCURRED WHILE COMPLETING REPAIRS. GAS WAS RESTORED TO THE MAIN AT 12:17 P.M. ON JULY 11, 2025. SERVICE RESTORATION TO THE CUSTOMERS WAS CONCLUDED AT 12:55 P.M. ON JULY 12, 2025. CONFIRMED DISCOVERY OCCURRED ON JULY 15, 2025, AT 4:23 P.M. WHEN AN ESTIMATE OF THE PERMANENT REPAIRS WAS PRESENTED AND COMBINED WITH THE ADDITIONAL COST OF THE OUTAGE RELIGHT, THE TOTAL OF WHICH EXCEEDED THE REPORTING THRESHOLD. AFTER FURTHER INVESTIGATION, IT WAS DETERMINED THAT THE THIRD-PARTY EXCAVATOR WAS DIGGING BY OPEN TRENCH OUTSIDE THE SCOPE OF THE AREA DESCRIBED IN 811 LOCATE TICKET. THE PERMANENT REPAIR WAS COMPLETED ON JULY 17, 2025.
2026-06-30 10:38 | NO | YES | NO | 20250047 | 41247 | 2025-08-13 18:29 | ORIGINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2025-07-14 23:54 | EASTERN | YES | 2025 | 643 PARKVIEW AVE | NORTH PLAINFIELD | SOMERSET | NJ | 07063 | 40.768 | -74.1819 |  |  | YES | YES | YES |  |  |  |  | 2025-07-15 08:43 | 1427035 | 1427203 | NATURAL GAS |  | 2.32 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-07-14 23:54 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 2.3 | YES | 0 | 2025-07-14 23:54 |  |  |  | 2025-07-15 00:15 | 2025-07-14 23:54 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | UNDER INVESTIGATION | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | LEAK |  |  | OTHER | UNDER INVESTIGATION | [5 empty] | CLASS 4 LOCATION | 525000 | 525000 | 7965 | 7965 | 11339 | 11339 | 0 | 0 |  | 94.04 | 218 | 218 | 0 | 0 | 544522 | 221197.4498687396811275876288659793814433 | 544522 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 32.4 | 32.4 | 35 | 192.619(A)(2) | 2015-09-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 7.2 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | HENRY VARUM | PRINCIPAL REGULATORY SPECIALIST | henry.varum@pseg.com | 732-343-3421 |  | HENRY VARUM | henry.varum@pseg.com | 732-343-3421 | CHRISTOPHER LAROSSA | DISTRICT MGR REG POLICY AND PROCEDURE | 973-896-7617 | christopher.larossa@pseg.com | ON MONDAY, JULY 14, 2025, PSE&G WAS NOTIFIED OF A HOUSE EXPLOSION AT 643 PARKVIEW AVENUE, NORTH PLAINFIELD THAT OCCURRED AT APPROXIMATELY 23:54 HRS. THE LOCAL FIRE DEPARTMENT WAS ABLE TO EXTINGUISH THE FIRE ON 7/15/2025 AT 00:07 HRS. A PSE&G TECHNICIAN WAS ON SITE AT 00:15 HRS. GAS TO THE HOME WAS SHUT OFF AT THE CURB AT APPROXIMATELY 01:00 HRS FOLLOWED BY AN ADDITIONAL 7 HOMES HAVING GAS SHUT OFF AT THE CURB FOR PRECAUTIONARY REASONS AT 02:05 HRS. AT THE TIME OF THIS INCIDENT THE AREA WAS EXPERIENCING SEVERE FLOODING AND RESIDENTS IN THAT AREA HAD ALREADY BEEN EVACUATED EARLIER THAT DAY. WATER LEVELS OBSERVED COMPLETELY SUBMERGED BASEMENTS IN THAT AREA, AND REACHED AS HIGH AS 4 FEET OF THE FIRST FLOOR AT 643 PARKVIEW AVE. A LEAK INVESTIGATION CONSISTING OF A WALKING SURVEY AND A LEAK MOBILE SURVEY WAS CONDUCTED WITH 0% OPEN AIR READINGS. A PRESSURE TEST OF THE SERVICE UP TO THE HEAD OF SERVICE VALVE LOCATED ON THE INTERIOR OF THE FRONT BASEMENT WALL WAS CONDUCTED WITH NO DETECTED LEAKS. INSIDE THE HOME, DAMAGE WAS FOUND ON THE 0.75” JURISDICTIONAL PIPING DIRECTLY BELOW THE REGULATOR, AS WELL AS AT THE JUNCTION OF JURISDICTIONAL AND NON-JURISDICTIONAL PIPING. AT THIS TIME, DUE TO THE EXTENT OF FLOODING AND SUBSEQUENT DAMAGE, WE ARE NOT ABLE TO DETERMINE THE INITIAL SOURCE OF THE GAS LEAK INSIDE OF THE BUILDING THAT LED TO THE EXPLOSION, ADDITIONALLY, THE DAMAGE TO PSE&G OWNED FACILITIES MAY HAVE BEEN AS A RESULT OF THE EXPLOSION. THEREFORE, THE APPARENT CAUSE OF THIS INCIDENT IS STILL UNDER INVESTIGATION.
2026-06-30 10:38 | NO | YES | YES | 20250050 | 41453 | 2025-08-21 02:42 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2025-07-21 03:56 | CENTRAL | YES | 2025 | 1901 CHILTON DR | BAYTOWN | HARRIS | TX | 77520 | 29.735 | -94.9447 |  |  |  | YES | [5 empty] | 2025-07-21 17:53 | 1437562 | 1437754 | NATURAL GAS |  | 0.65 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2025-07-21 15:56 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.65 | NO | 0 | 2025-07-21 15:56 |  |  |  | 2025-07-21 16:20 | 2025-07-21 16:55 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2012 |  | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 100000 | 100000 | 66 | 66 | 3964 | 3964 | 0 | 0 |  | 9.9098 | 6 | 6 | 0 | 0 | 104036 | 42247.2742318908038898969072164948453608 | 104036 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 35 | 35 | 60 | 192.619(A)(2) | 1959-04-22 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 0.2 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT INVOLVED FACILITIES DOWNSTREAM OF A RESIDENTIAL SERVICE REGULATOR. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [156 empty] | ELMER SELVERA | LEAD OPERATIONS SPECIALIST | elmer.selvera@centerpointenergy.com | 281-755-2470 |  | ELMER SELVERA | elmer.selvera@centerpointenergy.com | 281-755-2470 | JERRY GANN | DIRECTOR OPERATIONS | 713-967-7101 | jerry.gann@centerpointenergy.com | ON JULY 21, 2025, AT 3:56PM, CENTERPOINT ENERGY WAS NOTIFIED OF A HOUSEFIRE AT 1901 CHILTON DR., BAYTOWN, TX. WHEN THE RESPONDING TECHNICIAN ARRIVED ON SITE AT 4:20PM, IT WAS CONFIRMED THAT THE GAS HAD BEEN TURNED OFF BY THE RESPONDING BAYTOWN FIRE DEPARTMENT AT THE SERVICE RISER. THE TECHNICIAN WAS NOT ALLOWED TO ACCESS THE PROPERTY DUE TO AN ONGOING INVESTIGATION BY THE BAYTOWN POLICE DEPARTMENT. AT 4:55PM IT WAS REPORTED TO THE SERVICE TECHNICIAN THAT THERE WAS A CONFIRMED FATALITY INSIDE OF THE HOUSE. CENTERPOINT WAS ALLOWED ACCESS TO THE RESIDENTIAL METER AND SET. IT WAS DETERMINED THAT THE GAS METER WAS STRUCK AND BROKEN BY AN OUTSIDE FORCE. THE CAUSE OF THE FIRE HAS BEEN DETERMINED AS ARSON BY THE FIRE MARSHAL AND LOCAL AUTHORITIES. CRIMINAL CHARGES HAVE BEEN FILED AGAINST THE RESPONSIBLE PARTY.
2026-06-30 10:38 | NO | YES | NO | 20250051 | 42198 | 2025-08-22 17:30 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2025-07-25 17:45 | EASTERN | YES | 2025 | INTERSECTION OF MARSH ROAD & WILDWOOD ROAD | SHELBYVILLE | BARRY | MI | 49344 | 42.5772 | -85.5147 | YES | [8 empty] | 2025-07-25 21:11 | 1437984 | 1438006 | NATURAL GAS |  | 32 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-07-25 18:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 32 | YES | 0 | 2025-07-25 17:45 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2025-07-25 18:03 | 2025-07-25 19:00 | 2025-07-25 17:45 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1992 | UNKNOWN | [7 empty] | STEEL |  | SEAMLESS |  | 0.035 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 2401639 | 2401639 | 2261 | 2261 | 0 | 0 |  | 2.89 | 92 | 92 | 0 | 0 | 2403992 | 976201.772334319049191752577319587628866 | 2403992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 385 | 400 | 192.619(A)(2) | 1992-11-05 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER'S RESPONSE TO SCADA ALARMS WAS APPROPRIATE AND ALIGNED WITH THE ESTABLISHED PROCEDURE | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | CARMELLA KING | PRINCIPAL ENGINEERING TECHNICAL ANALYST | carmella.king@cmsenergy.com | 9892802963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 9892802963 | RANDY J. FARROW | GAS COMPLIANCE MANAGER | 5173758565 | randy.farrow@cmsenergy.com | ON FRIDAY, JULY 25, 2025, AT APPROXIMATELY 17:45, CONSUMERS ENERGY GAS CONTROL RECEIVED MULTIPLE SCADA ALARMS INDICATING A POTENTIAL FAILURE AT DISTRIBUTION REGULATOR STATION 64-301, LOCATED AT THE INTERSECTION OF MARSH ROAD AND WILDWOOD ROAD IN SHELBYVILLE, MICHIGAN (BARRY COUNTY). THE CONTROLLER PROMPTLY NOTIFIED THE ON-CALL DISTRIBUTION REGULATION SUPERVISOR, WHO DISPATCHED A GAS MECHANIC TO THE SITE. AT APPROXIMATELY 17:56, LOCAL EMERGENCY RESPONDERS ALSO NOTIFIED THE CONSUMERS ENERGY SECURITY COMMAND MONITORING CENTER. UPON ARRIVAL, ORANGEVILLE TOWNSHIP FIRE DEPARTMENT PERSONNEL OBSERVED SMOKE COMING FROM THE BUILDING. USING THERMAL DETECTION EQUIPMENT, THEY RECORDED INTERNAL TEMPERATURES REACHING UP TO 800°F. AT APPROXIMATELY 18:05, AN IGNITION OCCURRED, RESULTING IN A FIRE AND SUBSEQUENT EXPLOSION. ALTHOUGH INFORMED THAT COMPANY PERSONNEL WERE ENROUTE, THE FIRE DEPARTMENT PROCEEDED TO REMOVE THE VALVE LOCKS AND MANUALLY CLOSED THE INLET (VALVE G) AND OUTLET (VALVE H) VALVES, SUCCESSFULLY ISOLATING GAS FLOW TO THE STATION BY APPROXIMATELY 18:10. AFTER EXTINGUISHING THE FIRE, THE FIRE DEPARTMENT COOLED THE FACILITY WITH WATER TO ENSURE SAFE ACCESS FOR INSPECTION. CONSUMERS ENERGY ELECTRIC PERSONNEL THEN DE-ENERGIZED THE REMOTE TERMINAL UNIT (RTU) CABINET TO ISOLATE ELECTRICAL SERVICE. GAS MECHANICS AND A GAS SERVICE WORKER CONDUCTED A LEAK INVESTIGATION IN THE SURROUNDING AREA, PERFORMED A VISUAL INSPECTION OF THE STATION, AND SECURED IT BY LOCKING AND TAGGING THE VALVES IN ACCORDANCE WITH SAFETY PROTOCOLS. NO INJURIES OR FATALITIES WERE REPORTED AS A RESULT OF THE INCIDENT. A MULTIDISCIPLINARY TEAM HAS BEEN ASSEMBLED TO INVESTIGATE THE ROOT CAUSE AND CONTRIBUTING FACTORS. A FINAL REPORT WILL BE ISSUED UPON COMPLETION OF THE INVESTIGATION. THE INVESTIGATION CONCLUDED THAT THE REGULATOR STATION FIRE WAS CAUSED BY AN ELECTRICAL ARC FAULT ON NEARBY ELECTRIC UTILITY LINES SERVING THE ADJACENT SUBSTATION. THE REGULATOR STATION’S PROXIMITY TO THE SUBSTATION FENCE INCREASED ITS SUSCEPTIBILITY TO IGNITION DURING THE FAULT EVENT. INADEQUATE GROUNDING AND THE ABSENCE OF A COMPREHENSIVE HAZARD ASSESSMENT WERE IDENTIFIED AS CONTRIBUTING FACTORS THAT INCREASED THE FIRE RISK. CORRECTIVE ACTIONS FOR DISTRIBUTION REGULATOR STATION 64-301 HAVE BEEN IDENTIFIED AND COMPLETED. IN ADDITION, A SYSTEM WIDE RISK ASSESSMENT WAS CONDUCTED TO IDENTIFY SIMILAR POTENTIAL RISKS ACROSS THE SYSTEM. ACTIONS ARE CURRENTLY UNDERWAY TO ADDRESS IDENTIFIED DEFICIENCIES AND TO REDUCE THE LIKELIHOOD OF SIMILAR EVENTS OCCURRING IN THE FUTURE.
2026-06-30 10:38 | NO | YES | NO | 20250052 | 41295 | 2025-08-24 03:42 | ORIGINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2025-07-24 15:44 | CENTRAL | YES | 2025 | 6749 OGDEN AVE. | BERWYN | COOK | IL | 60402 | 41.8279 | -87.7925 | [5 empty] | YES |  |  |  | 2025-07-24 16:57 | 1437876 | 1438022 | NATURAL GAS |  | 120 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-07-24 15:44 | ALLOWED TO BURN OUT |  | 120 | YES | 6 | 2025-07-24 16:45 |  |  |  | 2025-07-24 16:45 | 2025-07-24 16:56 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 32 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2011 | UNKNOWN |  |  |  |  | 2 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | LEAK |  |  | OTHER | DOWN POWER LINE, ELECTRIC ARC | [5 empty] | CLASS 3 LOCATION | 237500 | 237500 | 10600 | 10600 | 9400 | 9400 | 0 | 0 |  | 5.4 | 648 | 648 | 0 | 0 | 258148 | 105088.1180078954776288659793814432989691 | 258148 | 3 | 0 | 12 | 0 | 0 | 12 | 3 | 26 | 55 | 60 | 192.619(A)(2) | 2011-04-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | YES |  |  |  | YES | SEVERE LIGHTNING STORM | [192 empty] | YES | [20 empty] | JOSE L. DELREAL | MANAGER - OPERATIONS QUALITY ASSURANCE | jdelrea@southernco.com | 630-918-4934 |  | PAMELA REID | preid@southernco.com | 224-457-0663 | PAMELA REID | MANAGER - COMPLIANCE AND QA | 224-457-0663 | preid@southernco.com | LIGHTNING STRUCK A UTILITY POLE CAUSING A HIGH-VOLTAGE POWER LINE TO FALL AND ARC THROUGH THE GROUND. THE ELECTRICAL ARC DAMAGED THE GAS MAIN RESULTING IN A RELEASE AND IGNITION. SUBSEQUENTLY, A NEARBY GAS STATION STORE EXPLODED AND A METER SET CAUGHT FIRE. THE DAMAGED GAS MAIN WAS STOPPED TO EXTINGUISH THE NATURAL GAS-FUELED FIRE. THE DAMAGED GAS MAIN WAS DISCONNECTED FROM THE GAS SYSTEM TO SECURE THE GAS RELEASE.
2026-06-30 10:38 | NO | YES | NO | 20250053 | 41702 | 2025-08-28 15:36 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2025-07-29 08:00 | CENTRAL | YES | 2025 | N MAIN ST & GRAND AVE | FORT WORTH | TARRANT | TX | 76164 | 32.7733 | -97.3439 | YES | [8 empty] | 2025-07-29 18:12 | 1438307 | 1438405 | NATURAL GAS |  | 814.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 4 | 2025-07-29 09:08 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2025-07-29 08:17 | 2025-07-29 08:17 | 2025-07-29 17:15 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 72 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2014 | 2014 |  |  |  |  | 24 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 166687 | 166687 | 0 | 0 | 0 | 0 |  | 10.664 | 8682 | 8682 | 0 | 0 | 175369 | 74755.7756923255380848247422680412371134 | 175369 | 31 | 0 | 23 | 0 | 0 | 23 | 31 | 50 | 50 | 60 | 192.619(A)(2) | 2014-04-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | MEASURED DEPTH FROM GRADE | 72 | CONTRACTOR | DRILLING | UNKNOWN/OTHER | YES | 2569939133 | TEXAS ONE CALL SYSTEM | YES | CONTRACT LOCATOR | YES | YES | 36 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | BILL BROOKS | DIRECTOR OF REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 806-787-9422 |  | BRANDON WALTON | brandon.walton@atmosenergy.com | 214-491-0443 | MARC ROTHBAUER | VP COMPLIANCE AND REGULATORY REPORTING | 469-236-8616 | marc.rothbauer@atmosenergy.com | ON JULY 29, 2025, AT APPROXIMATELY 8:00 A.M., ATMOS ENERGY RECEIVED NOTIFICATION THAT A THIRD-PARTY EXCAVATOR HAD DAMAGED A 24-INCH STEEL GAS MAIN. AN ATMOS ENERGY TECHNICIAN ARRIVED ON SITE AT 8:17 A.M. AND REQUESTED ADDITIONAL RESOURCES AT THAT TIME. THE LEAK WAS GRADED AT 9:08 A.M. THE RELEASE WAS SECURED AT APPROXIMATELY 3:45 P.M. ON JULY 29, 2025. CONFIRMED DISCOVERY OCCURRED AT 5:15 P.M. ON JULY 29, 2025, WHEN AN ESTIMATE OF THE PERMANENT REPAIRS WAS PRESENTED, WHICH EXCEEDED THE REPORTING THRESHOLD.
2026-06-30 10:38 | NO | YES | NO | 20250054 | 41329 | 2025-09-02 08:31 | ORIGINAL | 18440 | SOUTH JERSEY GAS CO | 101 SOUTH LINCOLN PLACE | ATLANTIC CITY | NJ | 08401 | 2025-08-04 09:41 | EASTERN | NO | 2025 | 20 IRON GATE RD | EVESHAM TOWNSHIP | BURLINGTON | NJ | 08053 | 39.8722 | -74.9094 |  | YES |  |  |  | YES |  |  |  | 2025-08-04 11:27 | 1438820 | 1439006 | NATURAL GAS |  | 640 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-08-04 09:41 | OPERATOR/CONTRACTOR |  | 640 | NO | 12 | 2025-08-04 09:41 |  |  |  | 2025-08-04 10:03 | 2025-08-04 10:03 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 32 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1983 | 1982 |  |  |  |  | 2 | D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | LEAK |  |  | OTHER | 3RD PARTY DAMAGE | [5 empty] | CLASS 4 LOCATION | 400000 | 400000 | 16148 | 16148 | 0 | 0 | 0 | 0 | AWAITING INSURANCE ESTIMATES FOR DAMAGE CONSTRUCTION EQUIPMENT. | 2.37 | 1517 | 1517 | 0 | 0 | 417665 | 170216.4150519755644382680412371134020619 | 417665 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 56 | 58 | 60 | 192.619(A)(2) | 1983-04-08 | PRESSURE DID NOT EXCEED MAOP | WICK |  | 6.6 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A THIRD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | 18” – 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | CURB/SIDEWALK | YES | 252090566 |  | YES | CONTRACT LOCATOR | YES | YES | 2 | LOCATING ISSUE | FACILITY MARKED INACCURATELY DUE TO INCORRECT FACILITY RECORDS/MAPS | [143 empty] | YES | [26 empty] | JEFF OGBORN | DIRECTOR UTILITY SHARED SERVICES | hjogborn@sjindustries.com | 6094027972 |  | BRIAN RITZ | britz@sjindustries.com | 609-351-7436 | JEFF OGBORN | DIRECTOR UTILITY SHARED SERVICES | 6094027972 | hjogborn@sjindustries.com | AT APPROXIMATELY 9:41AM SOUTH JERSEY GAS (SJG) DISPATCH RECEIVED A CALL ADVISING OF A STRUCK GAS FACILITY. SJG DISPATCHED A FIRST RESPONDER IMMEDIATELY. SJG FIRST RESPONDER ARRIVED AT 10:03AM. HE FOUND A THIRD-PARTY CONSTRUCTION CREW HAD STRUCK A GAS FACILITY CAUSING A FIRE. THE FIRE IGNITED THE CONTRACTOR'S BACKHOE AND DUMP TRUCK. SJG STREET CREWS WERE DISPATCHED TO ISOLATE THE SYSTEM AND MAKE SAFE. A CONTROLLED OUTAGE WAS BE CAUSED BY THE ISOLATION OF THE DAMAGE. A SEQUENCE OF VALVE CLOSURES AND SQUEEZE OFF'S WERE COMPLETED AND FLOW WAS STOPPED AND MADE SAFE AT 12:07PM. THERE IS CURRENTLY AN ACTIVE INVESTIGATION THAT IS ONGOING. COST OF DAMAGE TO EXCAVATOR, DUMP TRUCK AND AND SIDING DAMAGE TO THE HOME ARE ESTIMATES. CLAIM HAS NOT BEEN SUBMITTED TO SJG FOR ANY OF THESE AS THE INVESTIGATION IS ONGOING.
2026-06-30 10:38 | NO | YES | YES | 20250055 | 41378 | 2025-09-17 10:14 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2025-08-19 11:20 | EASTERN | YES | 2025 | 5051 NEW CENTER DRIVE | WILMINGTON | NEW HANOVER | NC | 28403 | 34.2388 | -77.8763 |  |  | YES | [6 empty] | 2025-08-19 12:35 | 1440303 | 1440425 | NATURAL GAS |  | 24.1 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES | 2025-08-19 11:28 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 24.1 | YES | 4 | 2025-08-19 11:27 |  |  |  | 2025-08-19 11:28 | 2025-08-19 11:28 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2025 | 2025 | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | YES |  |  |  | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | DESIGN METER HIT BY VEHICLE. BROKE OFF ABOVE METER STOP. | CLASS 1 LOCATION | 1000000 | 1000000 | 150000 | 150000 | 150000 | 150000 | 0 | 0 |  | 4.5 | 108 | 108 | 0 | 0 | 1300108 | 527965.5318104541979381443298969072164948 | 1300108 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 60 | 55 | 60 | 192.619(A)(2) | 1993-09-12 | PRESSURE DID NOT EXCEED MAOP | DRIP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VEHICLE ACCIDENT/FIRE | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  |  | YES |  |  | NO | UNKNOWN | PASSENGER CAR | ROADWAY | 125 | NO | [142 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | AT APPROXIMATELY 11:20 AM 911 CALLED PNG CUSTOMER CONTACT CENTER TO REPORT THAT A VEHICLE HIT AND DAMAGED OUR ASSET. THE VEHICLE THAT HIT THE PNG DESIGN METER BENT THE 2” RISER AND BROKE OFF ABOVE THE METERSTOP. UPON BEING NOTIFIED OF THE EMERGENCY, CFO WAS DISPATCHED TO INVESTIGATE AND MAKE NECESSARY REPAIRS. WITHIN MINUTES OF THE CFO TECHNICIAN ARRIVING ON SITE THE BUILDING EXPLODED AND CAUGHT ON FIRE. FIRST RESPONDERS WERE ALREADY ON SITE. REPAIRS WERE MADE. THE FIRE/EXPLOSION RESULTED IN ONE CUSTOMER OUTAGE. ONE FIREFIGHTER WAS ADMITTED TO THE HOSPITAL FOR BURNS.
2026-06-30 10:38 | NO | YES | NO | 20250057 | 41432 | 2025-10-07 09:33 | ORIGINAL | 13635 | NORTHEAST OHIO NATURAL GAS CORP | 5640 LANCASTER NEWARK RD NE | PLEASANTVILLE | OH | 43148 | 2025-09-08 13:40 | EASTERN | YES | 2025 | 3434 SR 212 | MINERAL CITY | TUSCARAWAS | OH | 44656 | 40.5224 | -81.2848 |  |  |  | YES |  |  |  | YES | 3RD PARTY OPERATOR (ENBRIDGE) CLOSED THEIR VALVE | 2025-09-08 15:05 | 1442160 | 1442317 | NATURAL GAS |  | 461 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-09-08 13:40 | ALLOWED TO BURN OUT |  | 461 | NO | 0 | 2025-09-08 14:15 | YES | OPERATOR | 2025-09-08 14:15 | 2025-09-08 14:15 | 2025-09-08 14:15 | YES | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | UNKNOWN | [7 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | 7675 | 7675 | 250000 | 250000 | 90210 | 90210 | 118250 | 118250 | TEMPORARY GAS SUPPLY PROVIDED BY MOBILE TANKER | 6 | 2766 | 2766 | 6 | 6 | 468907 | 191536.233257059544432371134020618556701 | 468907 | 33 | 0 | 713 | 1 | 0 | 713 | 33 | 650 | 650 | 656 | 192.619(A)(4) | 1899-12-31 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES | YES |  |  |  |  | UNKNOWN | 35 | SMALL TRUCK | ROADWAY | 325 | YES | [5 empty] | YES | PIPELINE FACILITY WAS ENCLOSED IN A BUILDING AND SURROUNDED BY SEVERAL LARGE TREES | [111 empty] | YES | [23 empty] | JOSHUA D. SMITH | COMPLIANCE STRATEGIC ADVISOR | joshua.d.smith@neogas.com | 3045331865 |  | JOSHUA SMITH | joshua.d.smith@neogas.com | 3045331865 | JOSHUA D. SMITH | COMPLIANCE STRATEGIC ADVISOR | 3045331865 | joshua.d.smith@neogas.com | 3RD PARTY VEHICLE OPERATOR RAN OFF ROADWAY AND STRUCK REGULATION & METERING STATION, CAUSING SIGNIFICANT DAMAGE TO THE BUILDING STRUCTURE, REGULATORS, METERS, FILTER AND OTHER EQUIPMENT. ESCAPING GAS IGNITED RESULTING IN A FIRE, DESTROYING STATION AND VEHICLE. LOCAL FIRE DEPARTMENTS, STATE POLICE, AND MEDIA WERE PRESENT. ROADWAY WAS CLOSED FOR APPROXIMATELY 2 HOURS. INLET OPERATING PRESSURE OF APPROXIMATELY 650 PSIG AND OUTLET OPERATING PRESSURE OF APPROXIMATELY 43 PSIG. ENBRIDGE, UPSTREAM SUPPLY OPERATOR, SHUT OFF THEIR INLET VALVE TO STATION. NEO SHUT OFF ADDITIONAL VALVES UPSTREAM OF STATION TO ELIMINATE FIRE HAZARD. INCIDENT RESULTED IN A 746 CUSTOMER OUTAGE AS THIS STATION IS THE SOLE FEED TO THE ATWOOD LAKE AREA ON NEO_91 SYSTEM. TEMPORARY GAS SUPPLY FROM TANKERS IS BEING UTILIZED UNTIL PERMANENT REPAIRS ARE MADE. CUSTOMER SERVICE RESTORATIONS ARE PREDOMINANTLY COMPLETE, WITH THE EXCEPTION OF SOME VACATION HOMES.
2026-06-30 10:38 | NO | YES | NO | 20250058 | 41647 | 2025-10-18 10:38 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2025-09-18 12:00 | EASTERN | YES | 2025 | 22 HABERSHAM WAY NW | ATLANTA | FULTON | GA | 30305 | 33.8344 | -84.394 | [5 empty] | YES |  |  |  | 2025-09-18 14:13 | 1443076 | 1443201 | NATURAL GAS |  | 5.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-09-18 12:17 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 5.7 | NO | 0 | 2025-09-18 12:17 |  |  |  | 2025-09-18 12:35 | 2025-09-18 13:37 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2002 | UNKNOWN |  |  |  |  | 2 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 0.1 | 0.5 | [7 empty] | CLASS 3 LOCATION | 3000000 | 3000000 | 123 | 123 | 6542 | 6542 | 0 | 0 |  | 3.39 | 19 | 19 | 0 | 0 | 3006684 | 1220900.87666300784529134020618556701031 | 3006684 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 40 | 40 | 45 | 192.619(A)(2) | 2002-01-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 9.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | WATER | YES | 250918001136 |  | NO | CONTRACT LOCATOR | YES | YES | 1 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | RALPH MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | JOE CAUBO | MANAGER COMPLIANCE AND QA | (404) 460-7894 | jfcaubo@southernco.com | A THIRD-PARTY PARTY EXCAVATOR (MEER ELECTRIC) STRUCK AND DAMAGED AN ATLANTA GAS LIGHT COMPANY (AGLC) 2-INCH PLASTIC GAS MAIN WHILE HORIZONTAL DIRECTIONALLY DRILLING TO INSTALL A NEW WATER SERVICE TO 22 HABERSHAM WAY, ATLANTA, GA. THE ESCAPING GAS TRAVELED ALONG THE BORE PATH FROM THE MAIN TO THE OUTSIDE BUILDING WALL OF THE RESIDENCE WHERE THE GAS IGNITED, RESULTING IN EXTENSIVE FIRE DAMAGE TO THE RESIDENCE. UPON ARRIVAL, AGLC PERSONNEL WORKED WITH EMERGENCY RESPONDERS TO SECURE THE AREA AND MONITOR THE SURROUNDING AREA FOR GAS. GAS WAS SHUT OFF TO THE DAMAGED AREA BY PERFORMING TWO SQUEEZE-OFF OPERATIONS ON THE TWO-WAY FEED MAIN. THE EXCAVATOR WAS PERFORMING THE EXCAVATION ACTIVITIES UNDER AN EMERGENCY LOCATE TICKET AND DID NOT POTHOLE AND SPOT THE NATURAL GAS FACILITIES PRIOR TO COMMENCING EXCAVATION ACTIVITIES. THE GAS MAIN WAS CORRECTLY MARKED AT THE POINT OF DAMAGE. AS OF 13:37 ON THE DAY OF THE INCIDENT (9/18/2025), AGLC RECOGNIZED THE POTENTIAL DAMAGE ESTIMATES LIKELY MET OR EXCEEDED THE $149,700 THRESHOLD AND THUS MET THE CRITERIA FOR BEING REPORTABLE TO THE NRC. HOWEVER, THE COMPANY DID NOT HAVE REASON TO ESTIMATE THE DAMAGES TO MEET OR EXCEED THE $1 MILLION THRESHOLD FOR CSB REPORTING. AS A RESULT, AGLC REPORTED THIS INCIDENT TO THE NRC UNDER REPORT #1443076 AND THE 48-HR FOLLOW UP FILED UNDER REPORT #1443201 BUT DID NOT REPORT IT TO THE CSB. ON OCTOBER 14, 2024, AFTER LEARNING THAT THE HOMEOWNER’S INSURANCE COMPANY RESERVED THE PROPERTY LOSS AT $3 MILLION, AGL NOTIFIED THE CSB OF THE INCIDENT.
2026-06-30 10:38 | NO | YES | NO | 20250059 | 41534 | 2025-10-31 11:31 | ORIGINAL | 14200 | OKALOOSA COUNTY GAS DISTRICT | 511 GOVERNMENT AVE | VALPARAISO | FL | 32580 | 2025-10-01 08:57 | CENTRAL | YES | 2025 | 45 SEA CASTLE ALY | INLET BEACH | WALTON | FL | 32413 | 30.284 | -86.0323 |  | YES |  |  |  | YES |  |  |  | 2025-10-01 12:28 | 1444433 | 1444734 | NATURAL GAS |  | 66.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-10-01 08:51 | OPERATOR/CONTRACTOR |  | 66.4 | NO | 0 | 2025-10-01 08:51 |  |  |  | 2025-10-01 09:05 | 2025-10-01 08:51 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 | YES | NO | [11 empty] | OTHER | GAS DISTRICT | MAIN |  | 2016 | 2016 |  |  |  |  | 2 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | MECHANICAL PUNCTURE | 0.7 | 1.5 | [7 empty] | CLASS 4 LOCATION | 125000 | 125000 | 2000 | 2000 | 8000 | 8000 | 45000 | 45000 | CAT 302CR MINI EXCAVATOR | 5.5 | 365 | 365 | 0 | 0 | 180365 | 73388.0089247464734020618556701030927835 | 180365 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 35 | 35 | 60 | 192.619(A)(2) | 2018-04-23 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SCADA-BASED SYSTEM PRIMARILY MONITORS THE COMPANY'S TRANSMISSION SYSTEM. SINCE THIS INCIDENT OCCURRED ON THE DISTRIBUTION SYSTEM, PRESSURE RECORDERS ARE NOT TIED INTO SCADA. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | YES | NO | 18” – 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | ELECTRIC | YES | 268506463 |  | Unknown | FACILITY OWNER | YES | YES | 3 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | CHRISTOPHER HIESTAND | VICE PRESIDENT OF OPERATIONS | christopherhiestand@okaloosagas.com | 850-974-9661 |  | CHRISTOPHER HIESTAND | christopherhiestand@okaloosagas.com | 850-974-9661 | CHRISTOPHER HIESTAND | VICE PRESIDENT OF OPERATIONS | 850-974-9661 | christopherhiestand@okaloosagas.com | A THIRD-PARTY CONTRACTOR WAS INSTALLING ELECTRICAL CONDUIT FOR A NEW RESIDENCE. THE CONTRACTOR HAD LOCATED AND IDENTIFIED THE GAS MAIN, BUT FAILED TO DETERMINE THE CLEARANCE NECESSARY TO AVOID STRIKING THE GAS MAIN. AS THE CONTRACTOR WAS CONTINUING TO REMOVE COVER, THE TEETH OF THE EXCAVATOR BUCKET STRUCK AND SHEARED OFF A SERVICE TEE FOR THE RESIDENCE. THIS STRIKE LED TO THE UNCONTROLLED RELEASE OF GAS AND IGNITED. THE CONTRACTOR'S EXCAVATOR WAS DESTROYED BY THE FIRE, AND SIGNIFICANT DAMAGE OCCURRED TO THE NEW RESIDENCE BEING BUILT, ALONG WITH DAMAGE TO OTHER UTILITIES IN THE AREA.
2026-06-30 10:38 | NO | YES | NO | 20250060 | 42275 | 2025-11-07 12:57 | SUPPLEMENTAL FINAL | 3200 | DEKALB - CHEROKEE COUNTIES GAS DISTRICT | 1405 GAULT AVENUE S/ P.O. BOX 376 | FORT PAYNE | AL | 35967 | 2025-10-18 15:44 | CENTRAL | YES | 2025 | NEAR INTERSECTION OF CR 51 & CR 212 | COLLINSVILLE | DEKALB | AL | 35961 | 34.3271 | -85.8462 | [5 empty] | YES |  |  |  | 2025-10-20 09:33 | 1445885 | NA | NATURAL GAS |  | 6.05 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-10-18 15:44 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 6.05 | NO | 0 | 2025-10-18 15:44 | YES | OPERATOR | 2025-10-18 16:05 | 2025-10-18 15:55 | 2025-10-18 15:56 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 8 | NO | NO | [11 empty] | OTHER | GAS DISTRICT | MAIN |  | 2009 | [5 empty] | 2 | ASTM D2513 | JM EAGLE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | OTHER | [8 empty] | MAIN WAS DAMAGED BY A MILLING MACHINE OPERATED BY WIREGRASS CONSTRUCTION COMPANY, INC. | CLASS 1 LOCATION | 0 | 0 | 10606 | 10606 | 6457 | 6457 | 1028634 | 1028634 | DAMAGES CLAIMED BY WIREGRASS CONSTRUCTION COMPANY, INC | 3.79 | 23 | 23 | 0 | 0 | 1045720 | 424634.1123457800378419381443298969072165 | 1045720 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 30 | 30 | 53 | 192.619(A)(2) | 2003-10-14 | PRESSURE DID NOT EXCEED MAOP | DRIP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO | YES | COUNTY ROAD | [8 empty] | NO | NO | < 18” |  | CONTRACTOR | MILLING EQUIPMENT | ROAD WORK | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 8 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | MICHAEL OWENS | COMPLIANCE OFFICER | mowens@dcgas.org | 256-845-3731 |  | HEATH JONES | hjones@dcgas.org | 256-845-3731 | JAYSON HIGDON | GENERAL MANAGER | 256-845-3731 | jhigdon@dcgas.org | ON THE 18TH OF OCTOBER 2025 AT 3:44PM DEKALB CHEROKEE GAS (DC GAS) WAS NOTIFIED OF A GAS LEAK AT THE INTERSECTION OF DEKALB COUNTY ROAD 51 AND DEKALB COUNTY ROAD 212. CALLER STATED THAT A MILLING MACHINE HAD STRUCK A GAS LINE WHILE PREPARING THE INTERSECTION FOR PAVING AND THE MILLING MACHINE HAD IGNITED. UPON DC GAS PERSONNEL ARRIVING AT THE SCENE AT 3:55PM, DC GAS PERSONNEL, IN COORDINATION WITH EMERGENCY PERSONNEL, ASSESSED THE SITUATION AND BEGAN TO ISOLATE THE THREAT BY UNCOVERING THE GAS MAIN 75 FEET AWAY FROM THE MILLING MACHINE OPERATED BY WIREGRASS CONSTRUCTION COMPANY, INC. THAT HAD CAUGHT FIRE. DC GAS PERSONNEL SQUEEZED OFF THE 2" PE GAS MAIN. EMERGENCY CREWS THEN EXTINGUISHED THE FIRE, AND A WRECKER CREW REMOVED THE MILLING MACHINE OF WIREGRASS CONSTRUCTION COMPANY, INC. FROM THE SCENE. WIREGRASS CONSTRUCTION COMPANY, INC. WAS OPERATING THE MILLING MACHINE OUTSIDE OF THE FOOTPRINT OF THE EXISTING ROAD ON UNIMPROVED GROUND WHERE THE 2" PE GAS MAIN HAD BEEN INSTALLED. THE LAYOUT OF THE INTERSECTION WAS EXPANDED BY WIREGRASS CONSTRUCTION COMPANY, INC. OUTSIDE OF THE FOOTPRINT OF THE EXISTING ROAD INTO UNIMPROVED GROUND WHEN THE GAS LINE WAS STRUCK CAUSING DAMAGE TO THE MILLING MACHINE OPERATED BY WIREGRASS CONSTRUCTION COMPANY, INC. NO LINE LOCATES WERE CALLED INTO 811 PRIOR TO WORK BEING PERFORMED BY WIREGRASS CONSTRUCTION COMPANY, INC. AT THIS LOCATION. ONCE THE AREA WHERE THE INCIDENT OCCURRED WAS CLEARED OF OBSTRUCTIONS, REPAIRS TO THE GAS LINE BY DC GAS PERSONNEL BEGAN. THE 2" MAIN WAS CLEARED OF ALL FOREIGN SUBSTANCES FROM THE MILLING MACHINE FIRE, AND GAS WAS REINTRODUCED TO THE REPAIRED 2" GAS MAIN AND SERVICE WAS RESTORED TO THE CUSTOMER AFFECTED BY THIS OUTAGE.
2026-06-30 10:38 | NO | YES | YES | 20250062 | 41589 | 2025-11-14 11:50 | ORIGINAL | 31470 | VECTREN ENERGY DELIVERY OF OHIO | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2025-10-19 06:45 | EASTERN | YES | 2025 | 608 FLORENCE AVE | BELLEFONTAINE | LOGAN | OH | 43311 | 40.3716 | -83.7684 |  |  |  | YES |  |  |  | YES | RETIRED SERVICE AT THE MAIN | 2025-10-19 08:58 | 1445814 | 1445972 | NATURAL GAS |  | 0.01 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 2025-10-19 07:06 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.01 | NO | 2 | 2025-10-19 08:07 |  |  |  | 2025-10-19 07:11 | 2025-10-19 08:07 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | OTHER | OWNED BY CENTERPOINT ENERGY | OUTSIDE METER/REGULATOR SET |  | 2020 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | YES | UNABLE TO DETERMINE | NO |  |  |  | OTHER | THE METER WAS INVOLVED | [9 empty] | OTHER | [8 empty] | IT IS POSSIBLE THAT THE METER RELEASED GAS PRIOR TO OUR ARRIVAL. | CLASS 2 LOCATION | 129200 | 129200 | 200 | 200 | 1600 | 1600 | 300 | 300 | FUEL, OVERTIME WAGES, MATERIALS | 0 | 0 | 0 | 0 | 0 | 131300 | 53315.6348778043276 | 131300 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 45 | 45 | 52 | 192.619(A)(1) | 1978-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 74 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS IS A METER SET | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | BRENT PRICE | GAS COMPLIANCE SPECIALIST | brent.price@centerpointenergy.com | (937)-371-6117 |  |  |  |  | BRENT PRICE | GAS COMPLIANCE SPECIALIST | (937)-371-6117 | brent.price@centerpointenergy.com | CENTERPOINT ENERGY WAS CALLED TO 608 FLORENCE AVE IN BELLEFONTAINE FOR A FIRE AT THE RESIDENCE. METER SET WAS SHUT OFF UPON ARRIVAL. THE FIRE DEPARTMENT BELIEVES THE FIRE STARTED INSIDE THE FRONT OF THE HOME AWAY FROM THE METER SET. IT IS BELIEVED THAT THE FIRE WAS A SECONDARY CAUSE FOR DAMAGE TO THE METER SET AND A POSSIBLE RELEASE OF GAS.
2026-06-30 10:38 | NO | YES | YES | 20250063 | 41664 | 2025-11-21 15:57 | SUPPLEMENTAL FINAL | 6243 | HAWAII GAS | 515 KAMAKEE STREET (P.O. BOX 3000) | HONOLULU | HI | 96802-3000 | 2025-10-24 13:30 | HAWAII-ALEUTIAN | NO | 2025 | FORT SHAFTER HALE ‘IKENA COMMUNITY ACTIVITY CENTER - 711 MORTON DRIVE | HONOLULU | HONOLULU | HI | 96819 | 21.3485 | -157.8853 | [7 empty] | YES | PLUG FITTING | 2025-10-24 17:25 | 1446329 | 1446567 | SYNTHETIC GAS |  | 0.5 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2025-10-24 13:30 | OPERATOR/CONTRACTOR |  | 0.5 | NO | 50 | 2025-10-24 13:30 | YES | OPERATOR | 2025-10-24 13:40 | 2025-10-24 13:33 | 2025-10-24 13:30 | YES | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | BYPASS TEE UPSTREAM OF METER SET ASSEMBLY SERVICE VALVE | UNKNOWN | UNKNOWN | [7 empty] | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | CATCHING LIVE GAS METER BYPASS OPERATION | CLASS 4 LOCATION | 10000 | 10000 | 2500 | 2500 | 2500 | 2500 | 0 | 0 |  | 20 | 10 | 10 | 0 | 0 | 15010 | 6099.039403522687216494845360824742268041 | 15010 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 12 | 12 | 17 | 192.619(A)(3) | 1999-03-31 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | WHILE ATTEMPTING TO PLUG TEE DURING LIVE GAS CATCHING OPERATION, NEARBY GAS WATER HEATER CAUSED IGNITION OF GAS. METER RISER DID NOT HAVE ISOLATION VALVES IN PLACE TO TIE IN BYPASS. AN SOP FOR THIS SPECIFIC OPERATION WAS NOT AVAILABLE AT THE TIME OF INCIDENT. | YES |  |  |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [46 empty] | YES |  | YES | CHRIS HALL | IMP ENGINEER | chall@hawaiigas.com | (808) 388-7847 |  | CHRISTOPHER HALL | chall@hawaiigas.com | (808) 388-7847 | DEBRA OTA | EXECUTIVE DIRECTOR ENTERPRISE OPERATIONS | (808) 935-2337 | dota@hawaiigas.com | ON FRIDAY 10/24/25, HAWAII GAS'S TRANSMISSION & DISTRIBUTION (T&D) DEPARTMENT RELOCATED A SECTION OF SYNTHETIC NATURAL GAS (SNG) COATED STEEL MAIN ON THE FORT SHAFTER MILITARY BASE. FORT SHAFTER REQUESTED THIS RELOCATION TO ALLOW FOR CONSTRUCTION OF A PARKING STRUCTURE. DURING THE RELOCATION EFFORTS, A PORTABLE PROPANE-AIR UNIT (PAU) WAS USED TO SUPPLY GAS TO THE HALE ‘IKENA COMMUNITY ACTIVITY CENTER TO AVOID SERVICE INTERRUPTION. THE PAU WAS TIED IN TO THE UPSTREAM RISER OF THE METER SET ASSEMBLY (MSA). AT APPROXIMATELY 1:19 PM, THE HAWAII GAS T&D CREW COMPLETED THE MAIN RELOCATION WORK. AT APPROXIMATELY 1:30 PM, A HAWAII GAS PRESSURE CONTROL TECHNICIAN WAS REMOVING THE PAU CONNECTION FROM THE BYPASS TEE ON THE HIGH-PRESSURE RISER SIDE OF THE MSA. THE PAU CONNECTION INCLUDED A TEMPORARY VALVE AND OTHER FITTINGS, WHICH WOULD BE REMOVED AND REPLACED BY A PLUG (ORIGINAL SETUP). ALMOST IMMEDIATELY AFTER REMOVING THE TEMPORARY PAU CONNECTION, THE ESCAPING GAS (LIKELY A MIXTURE OR SNG, PROPANE, AND AIR) CAUGHT FIRE, BURNING THE EMPLOYEE’S RIGHT FACE AND NECK. IT IS BELIEVED THE SOURCE OF IGNITION WAS A NEARBY BOILER. ROOT CAUSE(S): · HAZARDS WERE NOT (RE)CHECKED. THERE WAS NO STANDARD OPERATING PROCEDURE (SOP) FOR RUNNING THE PORTABLE PROPANE-AIR UNIT. THE PAU HAD BEEN USED TO FEED THE HALE ‘IKENA COMMUNITY ACTIVITY CENTER SEVERAL TIMES BEFORE WITHOUT INCIDENT. CONTRIBUTING FACTOR(S): · THE EMPLOYEE “CAUGHT LIVE GAS” TO INSTALL AND REMOVE THE TEMPORARY PAU CONNECTION, WHICH INCLUDED A STAINLESS STEEL BALL VALVE AND OTHER FITTINGS, FROM THE BYPASS TEE ON THE HIGH-PRESSURE RISER. PERMANENT VALVES ARE NOT NORMALLY INSTALLED ON THE BYPASS TEE. A PERMANENT VALVE WOULD HAVE ELIMINATED THE NEED TO “CATCH LIVE GAS”. · ALTHOUGH HAWAII GAS HAS A PREVENTION OF ACCIDENTAL IGNITION SOP (DISTRIBUTION STANDARD D-216 “PREVENTION OF ACCIDENTAL IGNITION”), IT IS WRITTEN PRIMARILY FOR WORK IN AND AROUND TRENCHES, VAULTS, AND CONFINED SPACES. THERE IS NO FORMAL SYSTEM TO RECORD CHECKING FOR SOURCES OF IGNITION BEFORE “CATCHING LIVE GAS”. CURRENTLY, "CATCHING LIVE GAS" MAY NOT REQUIRE A HOT WORK PERMIT, DEPENDING ON OPERATIONAL CONDITIONS. · THERE IS NO FORMAL SYSTEM TO IDENTIFY HAZARDS FROM CHANGING CONDITIONS IN THE FIELD (E.G. FLAMMABLE MATERIAL BEING STACKED AGAINST A MSA, INSTALLATION OF ELECTRICAL ENCLOSURES NEAR A GAS PRESSURE REGULATOR VENT, ETC.). · THE PRESSURE CONTROL TECHNICIAN WASN’T WEARING A BALACLAVA, WHICH COULD HAVE PREVENTED OR REDUCED INJURIES. A BALACLAVA IS NOT A REQUIRED PPE FOR PRESSURE CONTROL EMPLOYEES AND ITS USE IS CONSIDERED OUTSIDE OF STANDARD OPERATING PROCEDURES. CORRECTIVE ACTION(S): · CREATE AND IMPLEMENT AN SOP FOR RUNNING THE PORTABLE PAU, INCLUDING A REQUIREMENT FOR CHECKING FOR SOURCES OF IGNITION. CONSIDER CREATING A SYSTEM TO HELP ENSURE THE SOP IS FOLLOWED, WHICH MAY INCLUDE TRAINING AND ONGOING FOLLOW-UP OBSERVATIONS. (DUE 12/31/25) · ESTABLISH A STANDARD PRACTICE TO INSTALL A PERMANENT LOCK-WING PLUG VALVE AND PLUG FOR REGULARLY USED PAU INJECTION LOCATIONS. PROVIDE TRAINING AS APPLICABLE. (DUE 12/31/25) · CONSIDER ADDING "CATCHING LIVE GAS" TO THE T&D HOT WORK PERMITTING SYSTEM. CONSIDER DOCUMENTING WORK PLANNING AND/OR HAZARDOUS ID DISCUSSIONS. (DUE 12/31/25) · DETERMINE IF THERE IS AN OPPORTUNITY TO LEVERAGE OTHER BUSINESS UNITS (WHO SEE THE MSA MORE OFTEN) TO IDENTIFY UNSAFE CONDITIONS AND GENERATE A HAZARDOUS ID. PROVIDE TRAINING AS APPLICABLE. (DUE 12/31/25) · CONSIDER WAYS TO ENSURE PPE (E.G. BALACLAVA) MATCH THE HAZARDS FOR PRESSURE CONTROL WORK AND "LIVE GAS" OPERATIONS. PROVIDE TRAINING AS APPLICABLE. (DUE 12/31/25) HAWAII GAS IS CONFIDENT THE LESSONS LEARNED AND MITIGATIVE ACTIONS LISTED ABOVE WILL HELP TO FURTHER REDUCE ACCIDENTAL IGNITION RELATED INCIDENTS GOING FORWARD. PLEASE CONTACT HAWAII GAS FOR ADDITIONAL NARRATIVE DETAIL SHOULD YOU REQUIRE ANY ADDITIONAL INFORMATION.
2026-06-30 10:38 | NO | YES | NO | 20250064 | 42170 | 2025-11-30 09:17 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2025-11-03 15:16 | EASTERN | NO | 2025 | 586 E. TOWN ST. | COLUMBUS | FRANKLIN | OH | 43215 | 39.9608 | -82.9844 | [5 empty] | YES |  |  |  | 2025-11-03 16:17 | 1447000 | 1447228 | NATURAL GAS |  | 19.28 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-11-03 15:16 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 7 | YES | 100 | 2025-11-03 15:16 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2025-11-03 14:40 | 2025-11-03 14:51 | 2025-11-03 15:16 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | YES | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2000 | 2000 | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | YES | 1 | ASTM D2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.99 |  | 2406 | MECHANICAL PUNCTURE | 0.4 | 0.4 | [7 empty] | CLASS 3 LOCATION | 2000000 | 2000000 | 2000 | 2000 | 11044 | 11044 | 0 | 0 |  | 5.04 | 97 | 97 | 1 | 1 | 2013142 | 817495.7999391186690096494845360824742268 | 2013142 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 42 | 43 | 50 | 192.619(A)(4) | 1991-04-29 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.4 |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EVENT DID NOT EXCEED MAOP, NOR DID THE DAMAGE CAUSE A PRESSURE LOSS THAT WOULD BE SEEN IN THE CONTROL ROOM. | [12 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2025-02-04 | NO |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [6 empty] | NO | NO | < 18” |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  |  | UNKNOWN/OTHER | NO | YES | 18 | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | ROB R. SMITH | MANAGER OF OPERATION COMPLIANCE AND RISK MGMT. | rrsmith@nisource.com | 6144605491 |  | ROB R. SMITH | rrsmith@nisource.com | 6144605491 | ROB R. SMITH | MANAGER OF OPERATION COMPLIANCE AND RISK MGMT. | 6144605491 | rrsmith@nisource.com | ON NOVEMBER 3, 2025, COLUMBIA GAS OF OHIO, INC. (COLUMBIA) RESPONDED TO AN EMERGENCY ODOR CALL AT 586 EAST TOWN ST., COLUMBUS, OHIO AT THE REQUEST OF THE COLUMBUS FIRE DEPARTMENT. COLUMBIA’S FIRST RESPONDER ARRIVED AT THE SITE AND FOUND GAS LEAKING FROM A HOLE APPROXIMATELY ONE INCH IN DIAMETER IN THE GROUND, AS THE RESULT OF A TENT STAKE REMOVAL. THE FIRST RESPONDER ENTERED THE BUILDING, DETECTED PARTS PER MILLION GAS IN FREE AIR AND ASKED FOR THE FIRE DEPARTMENT’S ASSISTANCE TO EVACUATE THE AREA. THE FIRST RESPONDER THEN CONFIRMED THE CURB BOX LOCATION ON HIS VEHICLE COMPUTER AND WHILE IN THE PROCESS OF LOOKING FOR THE CURB BOX, THE REAR OF THE BUILDING EXPLODED. THERE WERE NO INJURIES. ADDITIONAL COLUMBIA RESOURCES RESPONDED AND USED A SQUEEZE-OFF JACK TO SQUEEZE THE MAIN TO SHUT OFF THE AFFECTED BUILDING. COLUMBIA REVIEWED 811 TICKETS AND CUSTOMER SERVICE RECORDS FOR THE LOCATION AND CONDUCTED INTERVIEWS WITH THE TENT COMPANY ONSITE WHEN THE INCIDENT OCCURRED. COLUMBIA HAS DETERMINED THAT THE INCIDENT OCCURRED AS THE RESULT OF A TENT STAKE PIERCING THE CUSTOMER-OWNED SERVICE LINE AT THE PROPERTY AND A SUBSEQUENT RELEASE OF GAS WHEN THE STAKE WAS REMOVED BY THE TENT COMPANY ON THE DATE OF THE INCIDENT. THROUGH ITS INVESTIGATION, COLUMBIA IS UNABLE TO DETERMINE WHEN THE SERVICE LINE DAMAGE OCCURRED (I.E., WHEN THE TENT STAKE PIERCED THE CUSTOMER-OWNED SERVICE LINE) OR IF THERE WAS A VALID ONE-CALL TICKET FOR THE TENT STAKE INSTALLATION. COLUMBIA ATTENDED A JOINT LABORATORY EXAM TO INSPECT PHYSICAL EVIDENCE FROM THIS INCIDENT WITH OTHER INTERESTED PARTIES, INCLUDING THE PUBLIC UTILITIES COMMISSION OF OHIO. THE LABORATORY EXAM YIELDED NO ADDITIONAL INSIGHT AS TO THE CAUSE OF THIS INCIDENT. COLUMBIA HAS CONCLUDED ITS INVESTIGATION INTO THIS INCIDENT. PLEASE CONSIDER THIS REPORT FINAL AND CLOSED.
2026-06-30 10:38 | NO | YES | NO | 20250065 | 41961 | 2025-12-04 14:09 | SUPPLEMENTAL FINAL | 11824 | LOUISVILLE GAS & ELECTRIC CO | 820 WEST BROADWAY, PO BOX 32030 | LOUISVILLE | KY | 40202 | 2025-11-04 17:15 | EASTERN | NO | 2025 | 4550 MELTON AVE | LOUISVILLE | JEFFERSON | KY | 40213 | 38.1455 | -85.7332 | YES | [6 empty] | YES | CRITICAL VALVE - ISOLATION VALVE ON DISTRICT REGULATOR STATION WAS SHUT OFF. | 2025-11-13 11:32 | 1447823 | 1447899 | NATURAL GAS |  | 16.9 | 2.7 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-11-04 17:15 | YES | OPERATOR | 2025-11-04 17:25 | 2025-11-04 18:11 | 2025-11-13 10:40 | NO | PUBLIC PROPERTY | ABOVEGROUND | OTHER | UNKNOWN - WIDESPREAD DAMAGE IN AREA |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | WIDESPREAD DAMAGE IN AREA | UNKNOWN | UNKNOWN | [7 empty] | OTHER | WIDESPREAD DAMAGE IN AREA. | [9 empty] | OTHER | [8 empty] | WIDESPREAD DAMAGE IN AREA CAUSED BY AIRPLANE CRASH. | CLASS 3 LOCATION | 0 | 0 | 2100000 | 2100000 | 113906 | 113906 | 0 | 0 |  | 4.58 | 77 | 77 | 12 | 12 | 2213995 | 899050.4277941195473388041237113402061855 | 2213995 | 92 | 2 | 0 | 0 | 0 | 0 | 72 | 15.3 | 15.5 | 20 | 192.619(A)(2) | 1986-06-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | COMMERCIAL AIRCRAFT CRASHED, CAUSING WIDESPREAD DAMAGE INCLUDING TO COMPANY'S DISTRIBUTION SYSTEM IN THE AREA. | [154 empty] | PETER CLYDE | SR MANAGER - GAS T AND D INTEGRITY AND COMPLIANCE | peter.clyde@lge-ku.com | 502-364-8715 |  | PETER CLYDE | peter.clyde@lge-ku.com | 502-364-8715 | PETER CLYDE | SR MANAGER - GAS T AND D INTEGRITY AND COMPLIANCE | 502-364-8715 | peter.clyde@lge-ku.com | ON 11/04/2025, A COMMERCIAL AIRCRAFT OPERATED BY UPS CRASHED AFTER TAKEOFF, CAUSING WIDESPREAD DAMAGE TO THE AREA. LOCATION INFORMATION PROVIDED IN THIS REPORT IS APPROXIMATE BASED ON AREA IMPACTED BY THE CRASH. THE FACILITY DAMAGED AND OTHER INFORMATION PROVIDED IN THIS REPORT WAS DESCRIBED TO THE BEST OF THE COMPANY'S ABILITY DUE TO THE NATURE OF THE INCIDENT AND THE INFORMATION AVAILABLE TO THE COMPANY. THE NTSB AND KY DIVISION OF EMERGENCY MANAGEMENT TOOK CONTROL OF THE SITE AND RESTRICTED ACCESS TO COMPANY PERSONNEL. ONCE COMPANY PERSONNEL WERE ALLOWED TO ACCESS THE SITE AND ASSESSED THE DAMAGE TO COMPANY'S DISTRIBUTION SYSTEM, IT WAS DETERMINED THAT REPAIR COSTS WOULD EXCEED THE INCIDENT REPORTING THRESHOLD AND THE NOTIFICATION TO THE NRC WAS SUBMITTED.
2026-06-30 10:38 | NO | YES | NO | 20250066 | 41703 | 2025-12-05 13:30 | SUPPLEMENTAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2025-12-02 14:20 | MOUNTAIN | NO | 2025 | 920 GLEN HEATHER CT | DACONO | WELD COUNTY | CO | 80514 | 40.0813 | -104.9308 | [5 empty] | YES |  |  |  | 2025-12-02 18:28 | 1449322 | 1449502 | NATURAL GAS |  | 104.26 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2025-12-02 14:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 104.26 | YES | 12 | 2025-12-02 14:20 | YES | OPERATOR | 2025-12-02 15:00 | 2025-12-02 14:20 | 2025-12-02 14:55 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 0.2 | 2 | [7 empty] | CLASS 3 LOCATION | 250000 | 250000 | 25000 | 25000 | 25000 | 25000 | 0 | 0 |  | 2.7105 | 283 | 283 | 0 | 0 | 300283 | 122048.3860085980742268041237113402061856 | 300283 | 0 | 0 | 11 | 0 | 0 | 12 | 0 | 30 | 30 | 60 | 192.619(A)(2) | 1994-06-30 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.7 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LINE WAS DAMAGED BY BORE COMPANY | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [5 empty] | NO | YES | 18” – 36” |  | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | A532101864 |  | NO | CONTRACT LOCATOR | YES | YES | 10 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [143 empty] | YES | [26 empty] | JOSHUA DOUGHTY | PIPELINE SAFETY PROFESSIONAL | joshua.doughty@blackhillsenergy.com | 303-515-0088 |  | KAMRON WEISSHAAR | kamron.weissharr@blackhillsenergy.com | 719-342-0151 | JOSHUA DOUGHTY | PIPELINE SAFETY PROFESSIONAL | 303-515-0088 | joshua.doughty@blackhillsenergy.com | ON DECEMBER 2, 2025, J&R TELCOM WAS PERFORMING A BORE TO INSTALL A NEW FIBER LINE ON GLEN HEATHER CT. DURING THE OPERATION, THE CREW STRUCK A 1-INCH POLYETHYLENE GAS SERVICE LINE SUPPLYING 917 GLEN HEATHER CT WHILE CONDUCTING A PERPENDICULAR BORE ACROSS THE SERVICE LINE. GAS MIGRATED TO 920 GLEN HEATHER CT, AND AT APPROXIMATELY 14:55, THE GAS IGNITED, RESULTING IN AN EXPLOSION AND FIRE THAT CAUSED A TOTAL LOSS OF THE HOME AT 920 GLEN HEATHER CT. THE INCIDENT RESULTED FROM THE THIRD-PARTY CONTRACTOR’S FAILURE TO MAINTAIN APPROPRIATE CLEARANCES AFTER VERIFYING THE LOCATE MARKS. THE DRILL WAS POSITIONED OUTSIDE THE POTHOLE AND NOT VISIBLE WHEN CROSSING THE SERVICE LINE. THE DAMAGE OCCURRED APPROXIMATELY 18–24 INCHES OUTSIDE OF THE POTHOLE. LOCATE MARKS WERE ACCURATE AND CONFIRMED BY THE POTHOLE, AND GAS FACILITIES WERE ACCURATELY LOCATED BY THE OPERATOR’S CONTRACTOR. IT IS UNCLEAR HOW LONG AFTER THE DAMAGE OCCURRED BEFORE THE BORING COMPANY CONTACTED BHE. BHE PERSONNEL WERE ON SITE AT THE TIME OF THE EXPLOSION. AT THIS TIME, ROOT CAUSE ANALYSIS AND POTENTIAL CHANGES ARE STILL UNDER REVIEW.
2026-06-30 10:38 | NO | YES | YES | 20250067 | 41708 | 2025-12-16 11:42 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2025-11-16 15:56 | PACIFIC | NO | 2025 | 4222 SIERRA VISTA DR | CHINO HILLS | SAN BERNARDINO | CA | 91709 | 33.9706 | -117.7124 | [5 empty] | YES |  |  |  | 2025-11-16 21:01 | 1448100 | 1448293 | NATURAL GAS |  | 127.52 | 0.07 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES | 2025-11-16 15:56 | OPERATOR/CONTRACTOR |  | 127.52 | YES | 11 | 2025-11-16 15:56 |  |  |  | 2025-11-16 16:09 | 2025-11-16 21:01 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 40 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1983 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.29 |  | UNKNOWN | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 15000 | 15000 | 60000 | 60000 | 0 | 0 |  | 6 | 765 | 765 | 0 | 0 | 75765 | 31077.5166052423020618556701030927835052 | 75765 | 0 | 0 | 11 | 2 | 0 | 11 | 0 | 45 | 45 | 60 | 192.619(A)(2) | 1983-06-01 | PRESSURE DID NOT EXCEED MAOP | NONE |  | 2.2 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | CRACK ON THE COUPLING |  |  |  |  | YES | [9 empty] | YES |  |  |  | OTHER | CRACK ON THE COUPLING | NO | [86 empty] | KRISTIE JACOBO | PIPELINE SAFETY ASSURANCE ADVISOR | kjacobo@sdge.com | 619-695-4030 |  | KRISTIE JACOBO | kjacobo@sdge.com | 619-695-4030 | KRISTIE JACOBO | PIPELINE SAFETY ASSURANCE ADVISOR | 619-695-4030 | kjacobo@sdge.com | SOCALGAS CREWS RESPONDED TO A STRUCTURE FIRE AND EXPLOSION LOCATED AT 4222 SIERRA VISTA DR, CHINO HILLS. GAS HAS BEEN CONTROLLED AS OF 11/16/25 AT 10:31PM. THE INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO THE RELEASE OF NATURAL GAS LEADING TO POTENTIAL INJURIES AND COSTS ASSOCIATED WITH THE INCIDENT POTENTIALLY EXCEEDING $149,700. THE INCIDENT IS CURRENTLY STILL UNDER INVESTIGATION TO DETERMINE THE ROOT CAUSE.
2026-06-30 10:38 | NO | YES | YES | 20250068 | 42366 | 2025-12-19 15:34 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | 3600 MIDTOWN DR. | TAMPA | FL | 33607 | 2025-12-04 09:46 | EASTERN | NO | 2025 | 101 S EUSTIS STREET | EUSTIS | LAKE COUNTY | FL | 32726 | 28.8511 | -81.6819 | [5 empty] | YES |  |  |  | 2025-12-04 14:12 | 1449482 | 1449596/1449804 | NATURAL GAS |  | 59.5 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2025-12-04 10:57 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 1 | 2025-12-04 09:46 |  |  |  | 2025-12-04 10:05 | 2025-12-04 10:05 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 38 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2011 | [5 empty] | 2 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 148299 | 148299 | 21132 | 21132 | 3381 | 3381 | 1 | 1 | 1 | 6.22 | 370 | 370 | 0 | 0 | 173183 | 70473.7302300850282863092783505154639175 | 173183 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 50 | 50 | 60 | 192.619(A)(2) | 2011-10-10 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CAUSED BY THIRD-PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 318502664 | N/A | YES | FACILITY OWNER | YES | YES | 26 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | IYANNA JONES | COMPLIANCE ANALYST | iejones@tecoenergy.com | 407-420-6617 |  | RICHARD GULLETT | rgullett@tecoenergy.com | 352-401-3417 | NARINDER GREWAL | MANAGER PIPELINE SAFETY COMPLIANCE | 813-327-3717 | ngrewal@tecoenergy.com | ON THURSDAY, DECEMBER 4, 2025, PEOPLES GAS SYSTEM, INC. (PGS) WAS NOTIFIED OF A RUPTURED GAS LINE IN EUSTIS. PGS DOES NOT KNOW THE PRECISE TIME OF THE RUPTURE. HOWEVER, THE EUSTIS FIRE DEPARTMENT RECEIVED THE REPORT AT 9:32 A.M. THE FIRE DEPARTMENT CALLED PGS AT 9:43 A.M. PGS ARRIVED ON SCENE AT 10:05 A.M. AND SQUEEZED OFF THE MAIN TO STOP GAS FLOW AT 10:48 A.M. THE EXPLOSION OCCURRED NINE MINUTES LATER, AT 10:57 A.M. ONE PERSON WAS INJURED AND TRANSPORTED TO AN AREA HOSPITAL. SHE LATER PASSED AWAY. THE INVESTIGATION SHOWED THAT THE PIPELINE WAS DAMAGED BY AN EXCAVATOR HORIZONTAL DIRECTIONAL DRILLING CONDUIT FOR ANOTHER UTILITY WITH NO CONNECTION TO PGS. THE DAMAGE OCCURRED UNDER CONCRETE ADJACENT TO THE BUILDING THAT EXPLODED. WHEN THE DAMAGE TO THE GAS MAIN OCCURRED, THE EXCAVATOR WAS DRILLING MORE-OR-LESS PARALLEL TO THE GAS MAIN AND WITHIN THE TOLERANCE ZONE. PEOPLES GAS ACCURATELY MARKED THE FACILITIES ON NOVEMBER 19, 2025, WHICH MARKS REMAINED IN PLACE ON DECEMBER 4. THE INVESTIGATION SHOWED THAT THE DAMAGED MAIN RESIDED AT A HORIZONTAL DISTANCE OF APPROXIMATELY 15-18 INCHES FROM THE “ZERO LINE” OF THE MARKS, WITHIN THE 24-INCH TOLERANCE ZONE. (WE PROVIDE A RANGE BECAUSE THE DRILL PUNCTURED 10 HOLES IN THE MAIN, WHICH HOLES SPANNED AN APPROXIMATE 4-FOOT DISTANCE ALONG THE PIPE. THE POINTS OF DAMAGE ON THE PIPE RANGED FROM APPROXIMATELY 15 TO 18 INCHES FROM THE “ZERO LINE” OF THE MARKS.) PEOPLES GAS’ RESPONDERS INVESTIGATED TO DETERMINE WHETHER THE EXCAVATOR POTHOLED TO EXPOSE THE GAS MAIN BUT FOUND NO EVIDENCE THAT THE EXCAVATOR DID SO. THE INVESTIGATION IS ONGOING, BUT THE CAUSE OF THE INCIDENT APPEARS TO BE THE EXCAVATOR’S FAILING TO MAINTAIN APPROPRIATE CLEARANCE FROM THE MARKS, FAILING TO USE INCREASED CAUTION WHILE DRILLING WITHIN THE TOLERANCE ZONE, AND FAILING TO EXPOSE THE GAS MAIN BEFORE DRILLING IN THE TOLERANCE ZONE. AS A RESULT OF THE RUPTURE, NATURAL GAS ESCAPED THE SYSTEM AND MIGRATED INTO THE BUILDING. WE CONTINUE TO INVESTIGATE HOW GAS ENTERED THE BUILDING. ADDITIONAL NOTES: (1) THE FIRE DEPARTMENT EVACUATED NEARBY BUILDINGS. PEOPLES GAS DOES NOT KNOW THE NUMBER OF BUILDINGS EVACUATED. BECAUSE OF THIS UNKNOWN, WE HAVE IDENTIFIED “1” IN RESPONSE TO QUESTION 22, ABOVE; (2) WITH RESPECT TO PART D QUESTION 2E, ABOVE, THE LAKE COUNTY PROPERTY APPRAISER VALUES THE BUILDING AT $148,299 BEFORE THE EXPLOSION. WE UNDERSTAND THAT THE BUILDING CONTAINED A BUSINESS WITH MERCHANDISE AND A RESIDENCE. PGS DOES NOT KNOW WHETHER THE BUILDING SUFFERED A CATASTROPHIC TOTAL LOSS, AND PGS HAS NO ESTIMATE FOR THE VALUE OF ITS CONTENTS. PGS CONTINUES TO COLLECT TIME SHEETS AND CONTRACTOR INVOICES TO DETERMINE THE VALUE OF THE DAMAGE TO GAS FACILITIES; (3) WITH RESPECT TO PART A QUESTION 21C, PEOPLES GAS CANNOT ESTIMATE THE VOLUME OF GAS CONSUMED IN THE EXPLOSION.
2026-06-30 10:38 | NO | NO | NO | 20250069 | 42379 | 2025-12-30 15:39 | SUPPLEMENTAL FINAL | 31632 | NORTHWESTERN CORPORATION | 3010 W. 69TH ST. | SIOUX FALLS | SD | 57108 | 2025-12-03 08:57 | CENTRAL | NO | 2025 | 13653 389TH AVE | ABERDEEN | BROWN | SD | 57350 | 45.4081 | -98.454 |  |  | YES | [6 empty] | 2025-12-03 17:48 | 1449410 | 1449575 | NATURAL GAS |  | 4567 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2025-12-03 09:11 |  |  |  | 2025-12-03 09:26 | 2025-12-03 17:42 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | FARM TAP METER/REGULATOR SET |  | 1996 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.19 | [6 empty] | LEAK |  |  | OTHER | VEHICLE IMPACT | [5 empty] | CLASS 1 LOCATION | 2000 | 2000 | 4508 | 4508 | 24686 | 24686 | 0 | 0 |  | 5.39 | 24616 | 24616 | 0 | 0 | 55810 | 32714.7078693389762117113402061855670103 | 55810 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 610 | 610 | 710 | 192.619(A)(2) | 1996-10-10 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 5.6 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CAUSED BY VEHICLE IMPACT | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | NO | [5 empty] | NO | 30 | PASSENGER CAR | ROADWAY | 35 | YES | YES | [141 empty] | CASSANDRA RUSSELL | GAS SYSTEM INTEGRITY DATA ANALYST | cassandra.russell@northwestern.com | 6053537615 |  | MICHAEL BAUMGARN | micahel.baumgarn@northwestern.com | 6052264173 | MELISSA BARUTH | GAS SYSTEM INTEGRITY SUPERINTENDENT | 6053537462 | melissa.baruth@northwestern.com | AT APPROXIMATELY 08:57 ON DECEMBER 3, 2025, SOUTH OF ABERDEEN SD, A VEHICLE SLID OFF AN ICY, GRAVEL ROAD STRIKING A 1" STEEL FARM TAP WITH A 4" STEEL BOLLARD BARRICADE IN THE RIGHT OF WAY. DRIVER WAS NOT INJURED. THE NIGHT BEFORE THE INCIDENT THERE WAS SNOW AND FREEZING RAIN WHICH AFFECTED ROAD CONDITIONS. AT 09:11, BROWN COUNTY 911 DISPATCH CALLED NORTHWESTERN ENERGY TO REPORT HIT LINE AND FIRST RESPONDER WAS ON SCENE AT APPROXIMATELY 09:26. NORTHWESTERN ENERGY FIRST RESPONDER IDENTIFIED THIS WAS THE MAIN PIPELINE INTO ABERDEEN, SD AND COMPANY LEADERSHIP WAS NOTIFIED IMMEDIATELY. MULTIPLE TEAMS COORDINATED TO ASSESS SYSTEM INTEGRITY, MANAGE GAS LOAD TO THE CITY OF ABERDEEN, AND ENSURE PUBLIC SAFETY. ABERDEEN RURAL FIRE DEPARTMENT (ARFD) TURNED OFF THE ABOVE GROUND VALVE AT THE FARM TAP AT APPROXIMATELY 09:30 WHICH MINIMIZED THE BLOWING GAS; HOWEVER, AN UNDERGROUND LEAK WAS STILL PRESENT AND RELEASING GAS (INITIALLY ~610PSIG). THE BROWN COUNTY SHERIFF DEPARTMENT BLOCKED THE ROAD AT THE INTERSECTION NORTH AND SOUTH OF THE ACCIDENT. THE ARFD VERIFIED NO ONE WAS HOME AT THE WEST RESIDENCE AND EVACUATED THE TWO RESIDENTS AT THE EAST RESIDENCE. MITIGATION STEPS INCLUDED MONITORING AMBIENT AIR, BARHOLING FOR GAS MIGRATION, AND PLANNING SEGMENT ISOLATION TO CONTROL THE PLUME OF GAS FOR SAFE APPROACH TO THE FARM TAP CURB VALVE. TO SUSTAIN THE GAS LOAD FOR THE CITY OF ABERDEEN DURING FRIGID WINTER WEATHER CONDITIONS, FOUR LARGE INDUSTRIAL CUSTOMERS WERE CURTAILED AND ALTERNATE SUPPLY INTERCONNECT SUPPORT FROM NORTHERN NATURAL GAS WAS ARRANGED. SEVERAL ATTEMPTS OF ISOLATION WERE ORGANIZED AND COMPLETED; HOWEVER, GAS LOAD DEMANDS WERE A FACTOR IN EXECUTION DUE TO FRIGID WINTER WEATHER CONDITIONS. AT 18:33, WITH DIMINISHED GAS LOAD, THE DAMAGED FARM TAP WAS ISOLATED, GAS FLOW STOPPED, AND SYSTEM PRESSURE RESTORED. CONTINGENCY PLANS FOR HEATING TO THE TWO CUSTOMERS AFFECTED BY THE FARM TAP SHUT OFF AND REPAIR LOGISTICS WERE IMPLEMENTED. FINAL REPAIR WAS DEFERRED TO NEXT DAY WITH OVERNIGHT MONITORING IN PLACE.
2026-06-30 10:38 | NO | YES | NO | 20260001 | 41781 | 2026-01-02 09:04 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2025-12-10 02:55 | CENTRAL | NO | 2025 | COUNTY RD 42 & INTERLACHEN DR NE | ALEXANDRIA | DOUGLAS | MN | 55308 | 45.9427 | -95.3556 | [5 empty] | YES |  |  |  | 2025-12-10 04:06 | 1450020 | 1450164 | NATURAL GAS |  | 3450 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-12-04 02:47 |  |  |  | 2025-12-04 04:06 | 2025-12-10 14:55 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2015 | UNKNOWN | [7 empty] | OTHER | TWO 2" FLANGES OPEN TO ATMOSPHERE | [9 empty] | OTHER | [8 empty] | VEHICLE STRUCK DISTRICT REGULATOR STATION. TWO 2" FLANGE CONNECTIONS OPEN TO ATMOSPHERE | CLASS 3 LOCATION | 0 | 0 | 60000 | 60000 | 130000 | 130000 | 0 | 0 |  | 4.48 | 15456 | 15456 | 0 | 0 | 205456 | 89739.2138879196738144329896907216494845 | 205456 | 43 | 2 | 481 | 0 | 0 | 481 | 45 | 70 | 70 | 76 | 192.619(A)(2) | 1997-10-09 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 10 | YES | YES | [141 empty] | KYLE MARTY | SENIOR OPERATIONS SPECIALIST | kyle.marty@centerpointenergy.com | 612-655-9214 | 612.321.0000 | KYLE MARTY | kyle.marty@centerpointenergy.com | 612-655-9214 | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 320-708-9474 | dean.headlee@centerpointenergy.com | A VEHICLE LEFT THE ROADWAY OF CR 42 IN ALEXANDRIA, MN AND STRUCK A REGULATOR STATION CAUSING THE RELEASE OF NATURAL GAS. THIS INCIDENT WAS REPORTED ON 12/4/2025 BY 911 AT 2:47 AM. THIS RESULTED IN THE SHUTDOWN OF OUR DISTRICT REGULATOR STATION. THE OUTAGE CREATED INVOLVED 526 CUSTOMERS WITHOUT GAS. SUPPLEMENTAL UPDATE 1/7/2026- THERE WERE 4 6" CONCRETE FILLED BOLLARDS INSTALLED BEFORE THE INCIDENT OCCURRED. IN TYPICAL CIRCUMSTANCES THESE BOLLARDS WOULD HAVE PREVENTED ANY DAMAGE TO THE REGULATOR STATION. BOLLARDS CURRENTLY MEET CENTERPOINT ENERGY'S INSTALLATION REQUIREMENTS.
2026-06-30 10:38 | NO | YES | YES | 20260002 | 42136 | 2026-01-09 11:14 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2025-12-12 09:16 | PACIFIC | NO | 2025 | 2300 CALIFORNIA ST | PLACENTIA | ORANGE | CA | 92870 | 33.9042 | -117.8464 | [7 empty] | YES | 4-INCH TOP HALF VALVE | 2025-12-12 15:01 | 1450239 | 1450362 | NATURAL GAS |  | 1.4 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2025-12-12 09:16 | YES | OPERATOR | 2025-12-12 09:16 | 2025-12-12 08:30 | 2025-12-12 18:30 | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 34 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1963 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | DEAVER MANUFACTURING | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | RELEASE THROUGH 4” TOP HALF VALVE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 200 | 200 | 0 | 0 |  | 6 | 8 | 8 | 0 | 0 | 208 | 87.72739823253617319587628865979381443299 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 44 | 60 | 192.621 M | 1963-05-21 | PRESSURE DID NOT EXCEED MAOP | NONE |  | 6.8 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 6 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | PRESSURE VERIFICATION WAS NOT FULLY COMPLETED PRIOR TO THE REMOVAL OF A 2-INCH TOP HALF PLUG FROM A 4-INCH TOP HALF VALVE, DURING MEDIUM-PRESSURE CONTROL WORK. SEE NARRATIVE SUMMARY FOR MORE DETAILS. |  |  | YES |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | JERRY BOLIVAR | PIPELINE SAFETY ASSURANCE ADVISOR | bjerry@socalgas.com | 951-287-9514 |  | JERRY BOLIVAR | bjerry@socalgas.com | 951-287-9514 | JERRY BOLIVAR | PIPELINE SAFETY ASSURANCE ADVISOR | 951-287-9514 | bjerry@socalgas.com | ON DECEMBER 12, 2025, A SOCALGAS CREW WAS REMOVING AN OVERNIGHT PLUG DURING ROUTINE ABANDONMENT OPERATIONS. DURING THIS ACTIVITY, A RELEASE OF NATURAL GAS OCCURRED, AND AN EMPLOYEE WAS INJURED BY DEBRIS ASSOCIATED WITH THE RELEASE. THE EMPLOYEE WAS HOSPITALIZED, ADMITTED, AND DISCHARGED THE FOLLOWING DAY. NO PROPERTY DAMAGE OCCURRED. THE INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO THE GAS RELEASE AND EMPLOYEE HOSPITALIZATION. SOCALGAS PLACES THE HIGHEST PRIORITY ON PUBLIC AND EMPLOYEE SAFETY AND IS COMMITTED TO LEARNING FROM INCIDENTS THAT MAY OCCUR AS A RESULT OF ITS WORK ACTIVITIES. FOLLOWING THE INCIDENT, SOCALGAS CONDUCTED AN INTERNAL INVESTIGATION TO DETERMINE THE CAUSE, ASSESS CONTRIBUTING FACTORS, AND IDENTIFY NECESSARY CORRECTIVE ACTIONS. MECHANICAL INSPECTIONS OF THE COMPONENTS INVOLVED WERE COMPLETED, AND NO DEFICIENCIES WERE IDENTIFIED WITH THE VALVE. THE INVESTIGATION IDENTIFIED INCOMPLETE PRESSURE VERIFICATION AND OPPORTUNITIES TO STRENGTHEN PROCEDURAL AND COMMUNICATION PRACTICES THAT MAY HAVE ALLOWED RESIDUAL PRESSURE TO REMAIN PRESENT PRIOR TO PLUG REMOVAL. AS PART OF ITS CORRECTIVE ACTIONS, SOCALGAS HAS INITIATED UPDATES TO PROCEDURES AND STANDARDS, INCLUDING FORMAL DOCUMENTATION AND COMMUNICATION REQUIREMENTS FOR OVERNIGHT WORK. IN ADDITION, SOCALGAS WILL ISSUE INFORMATION BULLETINS REINFORCING ZERO-PRESSURE VERIFICATION AND LINE OF FIRE AWARENESS. ENHANCED EXPECTATIONS FOR TAILGATE SAFETY BRIEFINGS WILL BE IMPLEMENTED, AND A REVIEW OF THE STOP-THE-JOB POLICY WILL BE CONDUCTED WITH THE INVOLVED CREW AND SUPERVISORY PERSONNEL.
2026-06-30 10:38 | NO | YES | YES | 20260003 | 41810 | 2026-01-12 18:11 | ORIGINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2025-12-11 12:50 | PACIFIC | NO | 2025 | 857/867 E. LEWELLING BLVD. | HAYWARD | ALAMEDA | CA | 94541 | 37.6876 | -122.1078 | [5 empty] | YES |  |  |  | 2025-12-11 12:53 | 1450128 | 1450295 | NATURAL GAS |  | 77 | 0.02 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES | 2025-12-11 09:38 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 3 | YES | 0 | 2025-12-11 09:38 | YES | OPERATOR | 2025-12-11 07:46 | 2025-12-11 07:50 | 2025-12-11 12:50 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 28 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1942 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | DIG IN INCIDENT | [5 empty] | CLASS 3 LOCATION | 149700 | 149700 | 535000 | 535000 | 10000 | 10000 | 0 | 0 |  | 4.98 | 383 | 383 | 0 | 0 | 695083 | 282401.581678240170791752577319587628866 | 695083 | 3 | 0 | 7 | 3 | 6 | 7 | 3 | 50 | 50 | 58 | 192.619(A)(3) | 1978-04-13 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 33 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DIG-IN INCIDENT. | [12 empty] | YES | 7 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | 18” – 36” |  | CONTRACTOR | GRADER/SCRAPER | GRADING | YES | 2024121700698 | USA NORTH 811 | YES | FACILITY OWNER | YES | YES | 126 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | rosa.duenas@pge.com | 510-298-7063 |  | BRIAN STOUT | brian.stout@pge.com | 925-548-4084 | BRIAN STOUT | GAS REGULATORY COMPLIANCE MANAGER | 925-548-4084 | brian.stout@pge.com | ON THURSDAY, DECEMBER 11, 2025, AT APPROXIMATELY 0938 HOURS, PG&E WAS NOTIFIED OF AN EXPLOSION AT 857/867 E. LEWELLING BLVD., HAYWARD, CA. A PG&E CREW WAS ON SITE MAKING REPAIRS TO A DIG-IN ON 3/4” STEEL SERVICE LINE WHEN THE EXPLOSION TOOK PLACE. A TOTAL OF 6 INJURIES WERE REPORTED. FIRE DEPARTMENT, POLICE DEPARTMENT, AND AMBULANCE WERE ON SITE. THE AREA WAS BLOCKED OFF, AND TRAFFIC REROUTED. THIS INCIDENT WAS REPORTED TO THE DOT (INCIDENT REPORT #1450128/1450295) AND CPUC ONCE ESTIMATED DAMAGE WAS CONFIRMED TO BE AT LEAST $149,700. A NATIONAL TRANSPORTATION SAFETY BOARD (NTSB) INVESTIGATION OF THE INCIDENT IS ONGOING. PG&E, PHMSA, OEIS AND THE CPUC ARE PARTIES TO THE INVESTIGATION, AND ADDITIONAL INFORMATION WILL BE PROVIDED ONCE THE NTSB COMPLETES ITS INVESTIGATION.
2026-06-30 10:38 | NO | YES | YES | 20260004 | 41850 | 2026-01-22 18:30 | ORIGINAL | 15462 | PECO ENERGY CO | 2301 MARKET STREET, S9-1 | PHILADELPHIA | PA | 19103 | 2025-12-23 14:15 | EASTERN | NO | 2025 | 905 TOWER RD | BRISTOL | BUCKS | PA | 19007 | 40.1072 | -74.8705 | [7 empty] | YES | SHUT OFF AT SERVICE TEE, AND CUT SERVICE AT MAIN | 2025-12-23 16:02 | 1451212 | 1451300, 1451419 | NATURAL GAS |  | 200 | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2025-12-23 14:15 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 200 | YES | 180 | 2025-12-23 14:18 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2025-12-23 14:19 | 2025-12-23 14:42 | 2025-12-23 14:18 | NO | PUBLIC PROPERTY | ABOVEGROUND | OTHER | BASEMENT |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | 2002 METER, 1968 ASSOCIATED PIPING AND APPURTENANCES | UNKNOWN | UNKNOWN | [7 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 15000 | 15000 | 533246 | 533246 | 0 | 0 | TOTAL COSTS ARE CURRENTLY UNDER INVESTIGATION. | 3.85 | 770 | 770 | 0 | 0 | 549016 | 223247.7041043978144621030927835051546392 | 549016 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 56.5 | 56.5 | 99 | 192.619(C) | 1968-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 6 |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EVENT WAS NOT ASSOCIATED WITH ANY OVERPRESSURE EVENT OR ANY OTHER ABNORMALITY ON THE SYSTEM THAT WOULD HAVE BEEN IDENTIFIED THROUGH THE SCADA SYSTEM. | [12 empty] | YES | 2 | 0 | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | ROBERT EDLING |  | robert.edling@exeloncorp.com | [5 empty] | CHANTEE ANGUS |  | 2159836404 | chantee.angus@exeloncorp.com | ON DECEMBER 23, 2025, AT APPROXIMATELY 14:15 HOURS, AN EXPLOSION OCCURRED AT 905 TOWER RD, BRISTOL, PA. 3 FATALITIES AND AN ESTIMATED 20 INJURIES OCCURRED AS A RESULT OF THE INCIDENT. THIS INCIDENT IS UNDER NTSB INVESTIGATION, AND THE CAUSE OF THE INCIDENT HAS NOT YET BEEN DETERMINED. THIS IS THE INITIAL REPORT. PECO WILL SUPPLEMENT AS ADDITIONAL INFORMATION BECOMES AVAILABLE, SUBJECT TO NTSB RESTRICTIONS. THE NTSB INVESTIGATION IS ONGOING. NOTE: SOME FIELDS WERE ENTERED AS "0" IF THEY WERE UNKNOWN AT THE TIME THE REPORT WAS WRITTEN (PART A - 10C, 10D, 10E, PART D - 2A, 4, 5). THESE VALUES WILL BE UPDATED AS APPROPRIATE AS INFORMATION BECOMES AVAILABLE.
2026-06-30 10:38 | NO | YES | NO | 20260005 | 41870 | 2026-01-29 10:51 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2026-01-05 10:53 | EASTERN | YES | 2026 | WAXPOOL ROAD AND PACIFIC BLVD | ASHBURN | LOUDOUN COUNTY | VA | 20166 | 39.0078 | -77.4377 | [5 empty] | YES |  |  |  | 2026-01-05 16:24 | 1452055 | 1452170 | NATURAL GAS |  | 6760 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 100 | 2026-01-05 10:51 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2026-01-05 11:23 | 2026-01-05 11:23 | 2026-01-05 11:23 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 96 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2023 | 2020 |  |  |  |  | 8 | ASTM D2513 | DURA-LINE POLYPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.639 |  | 2708 | MECHANICAL PUNCTURE | 3 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 650 | 637.2269669715066 | 104000 | 101956.314715441056 | 0 | 0 |  | 2.82 | 19063 | 19063 | 0 | 0 | 123713 | 57184.635923756026954123711340206185567 | 121656.5416824125626 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 55 | 55 | 60 | 192.619(A)(2) | 2023-10-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 9 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | AUGER | UNKNOWN/OTHER | YES | a534603102 | N/A | NO | CONTRACT LOCATOR | NO | YES | 8 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | TICKET WAS CODED 90, WHICH MEANS NO ACCESS. CONTRACTOR CONTINUED TO EXCAVATE ON THE CODE 90 TICKET. IN VIRGINIA, CODE 90 TICKET REQUIRES THE EXCAVATOR TO CALL AND REQUEST ANOTHER TICKET, THIS EXCAVATOR DID NOT REQUEST A NEW TICKET. | [169 empty] | MARK AIESI | DOT PIPELINE SUPERVISOR | mark.aiesi@washgas.com | 5714054623 |  |  |  |  | STACEY FORD | VP EHS UTILITIES | 832-592-0316 | stacey.ford@washgas.com | ON JANUARY 5, 2026, AT APPROXIMATELY 10:53, GEOTHERMAL TECHNICAL, AN EXCAVATOR USING A 6” AUGER, STRUCK AN 8" MAIN LOCATED AT PACIFIC BLVD AND WAXPOOL ROAD, ASHBURN, VIRGINIA. WASHINGTON GAS WAS NOTIFIED AT 10:53 VIA THE THIRD-PARTY EXCAVATOR OF THE DAMAGE. THE RESULTING DAMAGE, WHICH WAS A MECHANICAL PUNCTURE OF THE MAIN, CAUSED A GAS LEAK. THE FIRST WASHINGTON GAS CREW ARRIVED AT 11:24. THE FIRE DEPARTMENT NOTIFIED WASHINGTON GAS THEY EVACUATED 10 BUSINESSES IN THE SHOPPING CENTER OUT OF PRECAUTION. WASHINGTON GAS STOPPED THE FLOW OF GAS BY SQUEEZING OFF THE MAIN AT 04:30 ON JANUARY 6, 2026. CREWS HAVE RESTORED GAS SERVICE TO THE AREA. THERE WERE NO INJURIES FROM THIS INCIDENT.
2026-06-30 10:38 | NO | YES | NO | 20260007 | 41930 | 2026-02-12 15:11 | ORIGINAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2026-01-14 15:03 | EASTERN | YES | 2026 | 128 WOODHAVEN DRIVE | GREENCASTLE | PUTNAM | IN | 46135 | 39.6297 | -86.8486 | [5 empty] | YES |  |  |  | 2026-01-14 18:07 | 1452732 | 1452899 | NATURAL GAS |  | 271.85 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-01-14 15:29 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 45.3 | YES | 15 | 2026-01-14 15:11 | YES | OPERATOR | 2026-01-14 15:11 | 2026-01-14 15:39 | 2026-01-14 17:56 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 24 | YES | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1992 | 1992 | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1 | ASTM D3350 | DUPONT | PLASTIC |  |  |  |  | OTHER | ALDYL-A | 11.5 |  |  |  | MECHANICAL PUNCTURE | 1 | 0.2 | [7 empty] | CLASS 3 LOCATION | 275000 | 269596.0244879451 | 18885 | 18513.89426347215714 | 0 | 0 | 0 | 0 |  | 3.437 | 934 | 934 | 0 | 0 | 294819 | 117750.4993980863928556185567010309278351 | 289043.91875141725714 | 0 | 0 | 1 | 3 | 0 | 3 | 0 | 53 | 54 | 60 | 192.619(A)(2) | 1990-06-15 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 3.8 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | [7 empty] | YES |  |  | NO | NO | 18” – 36” |  | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 26010600055 |  | Unknown | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY MARKED INACCURATELY DUE TO LOCATOR ERROR | [170 empty] | RANDA POWERS | LEAD OPERATIONS SPECIALIST | randa.powers@centerpointenergy.com | 317-997-3939 |  | RANDA POWERS | randa.powers@centerpointenergy.com | 317-997-3939 | JERRY GANN | DIRECTOR GAS COMPLIANCE | 713-967-7101 | jerry.gann@centerpointenergy.com | ON JANUARY 14, 2026, AT APPROXIMATELY 15:11, CENTERPOINT ENERGY (CNP) RECEIVED A NOTIFICATION THAT A FIBER INSTALLATION CREW HIT A GAS LINE WITH A BORING MACHINE AT 128 WOODHAVEN DRIVE, GREENCASTLE, INDIANA. CNP DISPATCHED AN EMERGENCY TICKET AT 15:13, AND THE PRIMARY CNP RESPONDER ARRIVED ON-SITE AT 15:39. BASED ON INFORMATION FROM THE FIRE DEPARTMENT AND OTHERS ON SITE, IT IS ESTIMATED THAT THE DAMAGE OCCURRED AT APPROXIMATELY 15:00; HOWEVER, IMMEDIATELY PRIOR TO THE CNP TECHNICIAN’S ARRIVAL, AN IGNITION OCCURRED WITHIN THE RESIDENCE. UPON ARRIVAL, THE TECHNICIAN FOUND THE STRUCTURE FULLY ENGULFED AND THE FIRE DEPARTMENT IN ACTIVE FIRE SUPPRESSION MODE. CNP IMMEDIATELY ENACTED ITS EMERGENCY PROTOCOLS, INCLUDING THE SHUTTING OFF OF THE METER AT THE PRIMARY SITE VIA THE LOCK WING VALVE AND SHUTTING OFF THE METERS AT TWO ADJACENT PROPERTIES AS A PRECAUTION. THE ELECTRIC UTILITY ALSO REMOVED THE ELECTRIC METERS. FOR BROADER COMMUNITY SAFETY, THE ELECTRIC UTILITY SUBSEQUENTLY DE-ENERGIZED 105 HOMES IN THE VICINITY. THE INCIDENT RESULTED IN A TOTAL LOSS OF THE STRUCTURE. THREE INDIVIDUALS—TWO RESIDENTS AND ONE FIREFIGHTER—WERE INSIDE THE HOME AT THE TIME OF THE EXPLOSION; ALL THREE WERE TREATED FOR NON-LIFE-THREATENING INJURIES AND RELEASED FROM MEDICAL CARE THAT EVENING. THE REPORT FROM THE FIRE DEPARTMENT INDICATES THAT IT WAS INITIALLY DISPATCHED TO A REPORTED GAS LINE STRIKE BY THE THIRD-PARTY FIBER OPTIC CREW AND UPON ARRIVAL, THE FIRE DEPARTMENT OBSERVED A BORING MACHINE AT THE FRONT OF THE HOUSE AND WAS ADVISED BY THE BORING CREW THAT THEY HAD STRUCK A GAS LINE. BASED UPON THE REPORT FROM THE FIRE DEPARTMENT, A GAS DETECTOR WAS UTILIZED, AND THE ONLY MEASURABLE LEL READING OCCURRED WHEN THE DETECTOR WAS PLACED DIRECTLY INTO THE HOLE WHERE THE BORING MACHINE HAD BEEN OPERATING. THE FIRE DEPARTMENT’S REPORT STATES THAT THE HOMEOWNER RETURNED HOME AND WAS ADVISED BY THE FIRE DEPARTMENT THAT A GAS LINE HAD BEEN STRUCK AND THAT THEY WERE MONITORING THE AIR. THE REPORT INDICATES THE HOMEOWNER ASKED THAT THE FIRE DEPARTMENT ENTER THE HOME (WHERE HER SON WAS ALREADY LOCATED) WITH HER. THE FIRE DEPARTMENT REPORT STATES THAT “[P]RIOR TO ENTRY, THE GAS DETECTOR SHOWED NO ALARMS AND ALL READINGS WERE WITHIN NORMAL LIMITS. [A FIREFIGHTER] ENTERED THE RESIDENCE WITH THE GAS DETECTOR. THE HOMEOWNER AND HER SON WERE INSIDE THE RESIDENCE. BASED ON THE INFORMATION AVAILABLE AT THAT TIME AND NORMAL DETECTOR READINGS, I DID NOT DEEM EVACUATION NECESSARY.” ACCORDING TO THE FIRE DEPARTMENT REPORT, SHORTLY THEREAFTER, WITH ONE FIREFIGHTER, THE HOMEOWNER, AND HER SON INSIDE THE RESIDENCE, THE IGNITION OCCURRED INSIDE THE RESIDENCE. SUBSEQUENT EXCAVATION BY CNP CREWS CONFIRMED THAT THE 1-INCH SERVICE LINE HAD BEEN STRUCK BY THE THIRD-PARTY FIBER OPTIC CREW UTILIZING A BORING MACHINE. THIS SERVICE LINE WAS MISMARKED BY THE CONTRACTOR LOCATING COMPANY. SUBSEQUENT INVESTIGATION INDICATED THE LOCATE WAS 5-6 FEET OFF THE ACTUAL LOCATION OF THE SERVICE LINE. AFTER THE DAMAGE LOCATION WAS UNCOVERED, A CORRUGATED DRAIN TILE WAS VISIBLE, LOCATED APPROXIMATELY 12 INCHES FROM THE DAMAGED SERVICE LINE BELOW GROUND. GIVEN THAT THE RESIDENCE DRAINAGE SYSTEM UTILIZED IDENTICAL MATERIALS (ATTACHED TO THEIR GUTTERING), CURRENT ANALYSIS SUGGESTS THIS CONDUIT SERVED AS THE PRIMARY PATH FOR GAS MIGRATION INTO/AROUND THE STRUCTURE. CNP CREWS RETIRED THE SERVICE BY CAPPING THE SERVICE LINE AT THE MAIN AND BACKFILLING THE EXCAVATION SITES TO RESTORE THE AREA TO A SAFE CONDITION.
2026-06-30 10:38 | YES | NO | NO | 20260009 | 41950 | 2026-02-18 13:23 | ORIGINAL FINAL | 2128 | CASCADE NATURAL GAS CORP | 8113 W. GRANDRIDGE BLVD | KENNEWICK | WA | 99336 | 2026-01-21 11:48 | PACIFIC | NO | 2026 | 308 E SEATTLE AVE | MOXEE | YAKIMA COUNTY | WA | 98936 | 45.5528 | -120.3831 | [5 empty] | YES |  |  |  | 2026-01-21 13:53 | 1453152 | 1453257 | NATURAL GAS |  | 12.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-01-21 11:40 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 6 | YES | 570 | 2026-01-21 12:12 |  |  |  | 2026-01-21 12:12 | 2026-01-21 13:26 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 | YES | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1994 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.625 | D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 3408 | MECHANICAL PUNCTURE | 3 | 3 | [7 empty] | CLASS 3 LOCATION | 325000 | 318613.4834857533 | 496 | 486.253193258257344 | 16002 | 15687.547577658536328 | 0 | 0 |  | 4.715 | 57 | 57 | 0 | 0 | 341555 | 135990.0373731792338920206185567010309278 | 334844.284256670093672 | 0 | 0 | 1 | 0 | 0 | 10 | 6 | 54 | 54 | 60 | 192.619(A)(2) | 1994-11-08 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 9.4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | SAMANTHA J CALDWELL |  | samantha.caldwell@mdu.com | 2085092140 |  |  |  |  | SAMANTHA J CALDWELL |  | 2085092140 | samantha.caldwell@mdu.com | ON JANUARY 21, 2026, CNG RESPONDED TO A STRUCTURE FIRE/EXPLOSION AT 308 E SEATTLE AVE IN MOXEE, WA. CNG SERVICE MECHANIC ARRIVED ONSITE AND DISCOVERED NATURAL GAS IN THE SEWER. CNG PERSONNEL SECURED THE GAS PIPELINE BY SQUEEZING OFF THE 2” MAIN. UPON INVESTIGATION, IT WAS DETERMINED THAT A 5/8” PE NATURAL GAS SERVICE LINE WAS INSTALLED IN 1994 THROUGH A SEWER MAIN AND WAS SEVERED DURING THE REAMING OF THE SEWER MAIN BY A THIRD PARTY THE DAY OF THE INCIDENT.
2026-06-30 10:38 | NO | YES | YES | 20260010 | 42000 | 2026-03-02 13:59 | ORIGINAL | 32198 | MINNESOTA ENERGY RESOURCES CORPORATION | 2685 145TH STREET WEST | ROSEMOUNT | MN | 55068 | 2026-01-31 18:20 | CENTRAL | YES | 2026 | 5064 JENNIFER CIRCLE | HERMANTOWN | ST LOUIS | MN | 55811 | 46.8338 | -92.2135 |  |  |  | YES |  | YES |  |  |  | 2026-01-31 21:31 | 1453838 | 1453955 | NATURAL GAS |  | 0.65 | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 2026-01-31 18:20 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.65 | YES | 0 | 2026-01-31 18:47 |  |  |  | 2026-01-31 19:48 | 2026-01-31 19:48 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | CUSTOMER OWNED FACILITY | UNKNOWN | UNKNOWN | [7 empty] | OTHER | CUSTOMER BOILER | [9 empty] | OTHER | [8 empty] | CUSTOMER PIPING OR EQUIPMENT. UNKNOWN AT THIS TIME. | CLASS 3 LOCATION | 2108100 | 2066674.1062655893284 | 1500 | 1470.523769934246 | 5500 | 5391.920489758902 | 0 | 0 |  | 6.24 | 4 | 4 | 0 | 0 | 2115104 | 841982.8284371201149865979381443298969072 | 2073540.5505252824764 | 0 | 0 | 6 | 0 | 0 | 1 | 0 | 53 | 55 | 60 | 192.619(A)(2) | 1992-09-30 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | LINDSAY K LYLE | ENGINEERING MANAGER | lindsay.lyle@minnesotaenergyresources.com | 651-322-8909 |  | TRAVIS SOUTHWARD | travis.southward@minnesotaenergyresources.com | 320-438-3000 | LINDSAY K LYLE | ENGINEERING MANAGER | 651-322-8909 | lindsay.lyle@minnesotaenergyresources.com | REPORTS OF EXPLOSION AT 5064 JENNIFER CIRCLE. 911 CALL MADE AND REPORTED BY NEARBY RESIDENCE, 5096 JENNIFER CIRCLE, HERMANTOWN. FIRE ON STRUCTURE WHEN ARRIVED, GAS WAS SHUT OFF BY SQUEEZING SERVICE LINE. 6 UNIT STRUCTURE WHERE THERE IS A COMMON UTILITY ROOM FOR BOILER THAT PROVIDES HEAT TO ALL 6 UNITS. INVESTIGATION UNDER STATE FIRE MARSHALL STILL ON GOING AT THIS TIME.
2026-06-30 10:38 | NO | YES | NO | 20260011 | 42004 | 2026-03-03 00:38 | ORIGINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2026-02-01 21:11 | EASTERN | NO | 2026 | 6411 GLADYS MAY LANE | ALEXANDRIA | FAIRFAX | VA | 22310 | 38.7771 | -77.1508 | [5 empty] | YES |  |  |  | 2026-02-01 01:30 | 1453891 | 1454038 | NATURAL GAS |  | 20 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-02-01 21:11 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 20 | NO | 0 | 2026-02-01 21:11 | YES | OPERATOR | 2026-02-01 21:11 | 2026-02-01 19:24 | 2026-02-01 21:11 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1995 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 3 LOCATION | 1454510 | 1425927.68573804009964 | 0 | 0 | 3500 | 3431.222129846574 | 8467 | 8300.616506688840588 | CONTRACTING CREWS | 4.84 | 97 | 97 | 0 | 0 | 1466574 | 583854.554304284858467 | 1437756.524374575514228 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 22 | 20 | 25 | 192.619(A)(2) | 1995-01-12 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 5.6 |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | YES | 4 | 0 | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | ARTHUR M GROFF | SUPERVISOR PIPELINE SAFETY AND COMPLIANCE | agroff@washgas.com | 5713187993 |  | ARTHUR M GROFF | agroff@washgas.com | 5713187993 | JENNIFER POND | SR MANAGER PIPELINE SAFETY REGULATORY COMPLIANCE | 8102422381 | jennifer.pond@washgas.com | ON FEBRUARY 1, 2026, A WASHINGTON GAS SERVICE TECHNICIAN WAS DISPATCHED TO 6411 GLADYS MAY LANE, ALEXANDRIA, VIRGINIA, TO INVESTIGATE A REPORTED GAS ODOR INSIDE A RESIDENCE. THE TECHNICIAN ARRIVED IN THE EVENING HOURS AND CONDUCTED AN INITIAL ASSESSMENT INSIDE AND OUTSIDE OF THE HOME. GAS READINGS WERE IDENTIFIED, AND EXTERIOR CORROSION WAS OBSERVED ON THE SERVICE RISER AT THE REAR OF THE PROPERTY. BASED ON THE FINDINGS, THE TECHNICIAN NOTIFIED DISPATCH AND REQUESTED ASSISTANCE FROM A BELOW-GROUND CREW TO ADDRESS A GRADE 1 LEAK IDENTIFIED AT THE BUILDING WALL. THE BELOW-GROUND CREW WAS DISPATCHED AND ARRIVED ON SITE LATER THAT EVENING. WHILE THE CREW WAS PRESENT IN THE AREA PERFORMING RESPONSE ACTIVITIES ASSOCIATED WITH THE IDENTIFIED LEAK, A SUDDEN IGNITION OCCURRED NEAR THE REAR OF THE ADJACENT PROPERTY AT 6413 GLADYS MAY LANE. AT THE TIME OF THE IGNITION, NO ACTIVE EXCAVATION WAS OCCURRING. THE CREW OBSERVED FLAMES AND IMMEDIATELY INITIATED EMERGENCY RESPONSE ACTIONS, INCLUDING NOTIFYING DISPATCH AND REQUESTING ASSISTANCE FROM LOCAL FIRE AND RESCUE AUTHORITIES. WASHINGTON GAS PERSONNEL COORDINATED WITH EMERGENCY RESPONDERS AND SECURED THE AREA. THE INCIDENT REMAINS UNDER INVESTIGATION, AND THE COMPANY CONTINUES TO COOPERATE FULLY WITH ALL REGULATORY AUTHORITIES.
2026-06-30 10:38 | NO | YES | YES | 20260012 | 42007 | 2026-03-03 16:27 | ORIGINAL | 16667 | ENERGY NORTH NATURAL GAS INC | 15 BUTTRICK RD | LONDONDERRY | NH | 03053 | 2026-02-02 14:30 | EASTERN | NO | 2026 | 440 AMHERST STREET | NASHUA | HILLSBOUROUGH COUNTY | NH | 03063 | 42.7589 | -71.4882 |  |  | YES | [6 empty] | 2026-02-02 21:21 | 1453978 | 1454039 | NATURAL GAS |  | 20 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 3 | 0 | 0 | 3 | YES | 2026-02-02 14:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 15 | YES | 40 | 2026-02-02 14:21 |  |  |  | 2026-02-02 14:44 | 2026-02-02 14:44 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1979 |  | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | YES |  |  |  | OTHER | METER | [9 empty] | OTHER | [8 empty] | UNDER INVESTIGATION BY NTSB | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 23492 | 23030.362935530204688 | 0 | 0 | PROPERTY DAMAGE AND OTHER COSTS UNDER INVESTIGATION.0 | 16.47 | 329 | 329 | 0 | 0 | 23821 | 9619.650063463880954680412371134020618557 | 23359.362935530204688 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 53 | 53 | 60 | 192.619(A)(4) | 1979-08-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT DID NOT INVOLVE SCADA OPERATIONS, REMOTE VALVE MANIPULATION, ALARM MANAGEMENT, OR ANY CONTROLLER ACTIONS, AND THEREFORE NO CONTROL ROOM INVESTIGATION WAS WARRANTED. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | LEO CODY | PROGRAM MANAGER REGULATORY COMPLIANCE | leo.codyiii@libertyutilities.com | 6033276980 |  |  |  |  | ANTHONY STRABONE | PRESIDENT | (603) 327-9367 | anthony.strabone@libertyutilities.com | ON FEBRUARY 2, 2026, LIBERTY UTILITIES WAS NOTIFIED BY THE NASHUA FIRE DEPARTMENT OF AN INSIDE ODOR AT 440 AMHERST STREET, NASHUA, NEW HAMPSHIRE. LIBERTY UTILITIES RESPONDED AND CLOSED THE STREET VALVE FOR THE SERVICE LINE TO THE BUILDING THEREBY TERMINATING NATURAL GAS SERVICE TO THE STRUCTURE. THIS INCIDENT IS UNDER NTSB INVESTIGATION.
2026-06-30 10:38 | NO | NO | NO | 20260014 | 42038 | 2026-03-12 11:39 | ORIGINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2026-02-15 21:54 | EASTERN | NO | 2026 | 14389 QUAIL POND COURT | CENTREVILLE | FAIRFAX | VA | 20120 | 30.8574 | -77.4452 | YES | [8 empty] | 2026-02-15 23:10 | 1455006 | 1455099 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 1 | 2026-02-15 21:54 | YES | OPERATOR | 2026-02-15 21:54 | 2026-02-15 21:54 | 2026-02-15 21:54 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | PENDING NTSB INVESTIGATION | UNKNOWN | UNKNOWN | [7 empty] | OTHER | PENDING NTSB INVESTIGATION | [9 empty] | OTHER | [8 empty] | PENDING NTSB INVESTIGATION | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PENDING NTSB INVESTIGATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192.619(A)(1) | 2026-02-15 | PRESSURE DID NOT EXCEED MAOP | OTHER | PENDING NTSB INVESTIGATION | 2.2 |  | NO |  |  |  |  | OTHER | OPERATOR CREW |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | RICHARD FITZPATRICK | DOT PIPELINE SAFETY COMPLIANCE SUPERVISOR | richardfitzpatrick@washgas.com | 7036397825 |  | RICHARD FITZPATRICK | richardfitzpatrick@washgas.com | 7036397825 | JENNIFER POND | SENIOR MANAGER PIPELINE SAFETY REGULATORY COMP | 7036397825 | jennifer.pond@washgas.com | WASHINGTON GAS IS FULLY COOPERATING WITH THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB), WHICH HAS ASSUMED THE LEAD FOR THIS INVESTIGATION. WASHINGTON GAS WILL SUBMIT A SUPPLEMENTAL FILING, AS NECESSARY, UPON COMPLETION OF THE NTSB’S INVESTIGATION. ALL REQUIRED FIELDS IN THIS SUBMISSION HAVE BEEN COMPLETED TO THE BEST OF OUR KNOWLEDGE AT THIS STAGE; HOWEVER, CERTAIN INFORMATION MAY BE SUBJECT TO REVISION PENDING THE OUTCOME OF THE ONGOING INVESTIGATION. THIS FILING IS BEING SUBMITTED TO SATISFY THE 30-DAY REPORTING REQUIREMENT.
2026-06-30 10:38 | NO | YES | NO | 20260015 | 42158 | 2026-03-20 12:54 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2026-02-18 05:24 | EASTERN | NO | 2026 | 101 HUMBOLDT ST | BROOKLYN | KINGS | NY | 11206 | 40.705 | -73.9412 | YES | [8 empty] | 2026-02-18 10:06 | 1455215 | 1455415 | NATURAL GAS |  | 537 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-02-18 05:24 | ALLOWED TO BURN OUT |  | 537 | NO | 53 | 2026-02-18 05:24 | YES | OPERATOR | 2026-02-18 05:24 | 2026-02-18 05:24 | 2026-02-18 09:59 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 20 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2006 | 2005 | MULTI-FAMILY RESIDENTIAL | NO |  | YES | 2 | ASTM D2513 | US POLY | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1.5 | 2 |  | CLASS 4 LOCATION | 50000 | 49017.4589978082 | 25000 | 24508.7294989041 | 150000 | 147052.3769934246 | 0 | 0 |  | 10.23 | 5494 | 5494 | 0 | 0 | 230494 | 94042.5547047817997422680412371134020619 | 226072.5654901369 | 0 | 0 | 6446 | 0 | 0 | 173 | 0 | 13 | 13 | 15 | 192.621 M | 2006-02-23 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS INFRASTRUCTURE DAMAGE FROM ADJACENT ELECTRIC UTILITY | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | ALEC DAY | DIRECTOR - FEDERAL AND INDUSTRY ENGAGEMENT | alexander.day@nationalgrid.com | (781)844-1421 |  | ALEC DAY | alexander.day@nationalgrid.com | (781)844-1421 | ALEC DAY | DIRECTOR - FEDERAL AND INDUSTRY ENGAGEMENT | (781)844-1421 | alexander.day@nationalgrid.com | THE LOCAL ELECTRIC UTILITY SUFFERED AN UNDERGROUND CABLE FAILURE. AS A RESULT OF THAT EVENT, OPERATOR PERSONNEL WERE CALLED TO THE SCENE AT 03:49 TO ASSIST FDNY WITH CO READS IN AN ADJACENT MULTI-UNIT NEW YORK CITY HOUSING AUTHORITY RESIDENTIAL BUILDING. OPERATOR PERSONNEL REMAINED ON SITE. DUE TO THE ONGOING ELECTRIC CABLE FAILURE, THE 2-INCH 15PSIG PLASTIC SERVICE LINE FOR THE MULTI-UNIT RESIDENTIAL BUILDING, WHICH FEEDS OFF OF A 20-INCH 15PSIG CAST IRON MAIN, WAS IMPACTED BY ARCING ELECTRICITY. THIS IMPACTED FACILITY BEGAN TO LEAK, WHICH SUBSEQUENTLY IGNITED DUE TO THE ARCING ELECTRICITY AT 05:24. FDNY AND OPERATOR PERSONNEL WERE STILL ON SITE FROM EARLIER THAT MORNING AND WHILE FDNY WORKED TO CONTAIN THE FLAMES AND PROTECT NEARBY LIFE AND PROPERTY, OPERATOR PERSONNEL WORKED TO IDENTIFY AND THEN OPERATE THE MAIN VALVES NEEDED TO ISOLATE THE IMPACTED SERVICE. THE FIRE CONTINUED TO BURN THROUGH THE REMAINING LINE PACK UNTIL IT COULD BE EXTINGUISHED AT APPROXIMATELY 09:02.
2026-06-30 10:38 | NO | YES | NO | 20260016 | 42077 | 2026-03-24 16:32 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2026-02-24 12:48 | EASTERN | NO | 2026 | 3400 ATLANTA ROAD | SMYRNA | COBB | GA | 30080 | 33.8702 | -84.495 | [6 empty] | YES |  |  | 2026-02-25 15:15 | 1455815 | 1455992 | NATURAL GAS |  | 66.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2026-02-24 12:48 |  |  |  | 2026-02-24 12:57 | 2026-02-25 15:10 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1996 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 0.1 | 0.1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 75515 | 74031.06832438972446 | 119309 | 116964.480311389970676 | 60420 | 59232.69745295142888 | TDW TAPPING & STOPPING - PAXON BYPASS MATERIAL – PAVING -HYDRO-X | 3.67 | 243 | 243 | 0 | 0 | 255487 | 101805.5066420861668848247422680412371134 | 250471.246088731124016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 278 | 300 | 192.619(A)(2) | 1994-06-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 10.8 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE DAMAGE MEASURED ABOUT 1/8”, AND THE ASSOCIATED RELEASED VOLUME WAS MINIMAL, SO IT DID NOT REACH THE ALARM THRESHOLDS FOR THE CONTROL ROOM. FIELD OPERATIONS PERSONNEL NOTIFIED THE CONTROL ROOM ABOUT THE INCIDENT; HOWEVER, THE CONTROL ROOM’S ACTIONS WERE NOT A FACTOR IN THIS EVENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 260112001008 |  | NO | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | RALPH T MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | 4045843733 | (404) 584-4710 |  |  |  | JOE CAUBO | MANAGER COMPLIANCE AND QA | 4044607894 | jfcaubo@southernco.com | A THIRD-PARTY PARTY EXCAVATOR (SHOOK CONSTRUCTION, A SUBCONTRACTOR FOR CABLE EAST LLC) STRUCK AND DAMAGED AN ATLANTA GAS LIGHT COMPANY (AGLC) 12-INCH STEEL GAS MAIN WHILE HORIZONTAL DIRECTIONALLY DRILLING PARALLEL TO AGLC’S GAS MAIN TO INSTALL TELECOMMUNICATION LINES. THE BORE AUGER STRUCK THE SIDE OF THE GAS MAIN CREATING A GOUGE AND A 1/8-INCH HOLE AT ONE POINT ALONG THE 12-INCH STEEL GAS MAIN. DUE TO THE BORE ROD RESTING AGAINST THE 12-INCH STEEL GAS MAIN AND THE LENGTH OF THE GOUGE ALONG THE PIPE MADE IT DIFFICULT TO GET A COMPLETE SHUTOFF WITH A LEAK CLAMP. INITIALLY THE DAMAGE DID NOT MEET ANY OF THE CRITERIA FOR BEING REPORTABLE BUT WAS EVENTUALLY CALLED IN AT 15:15 ON 2/25/2026 WHEN COMPANY PERSONNEL DETERMINED THE TOTAL COST OF REPAIR, EMERGENCY RESPONSE, AND RESTORATION OF THE DAMAGE TO AGL FACILITIES WOULD AT SOME POINT CROSS OVER THE $149,700 PROPERTY DAMAGE THRESHOLD. UPON ARRIVAL, AGLC PERSONNEL WORKED WITH EMERGENCY RESPONDERS TO SECURE THE AREA AND MONITOR THE SURROUNDING AREA FOR GAS. GAS WAS SHUT OFF TO THE DAMAGED AREA BY PERFORMING A 4-INCH BYPASS AND TWO STOPPLE FITTING OPERATIONS ON THE TWO-WAY FEED MAIN. THE EXCAVATOR WAS PERFORMING THE EXCAVATION ACTIVITIES UNDER A LARGE PROJECT TICKET AND DID NOT POTHOLE AND SPOT THE NATURAL GAS FACILITIES ALONG THE BORE PATH AS APPROPRIATE FOR A PARALLEL BORE PRIOR TO COMMENCING EXCAVATION ACTIVITIES. THE GAS MAIN WAS CORRECTLY MARKED AT THE POINT OF DAMAGE. AGLC REPORTED THIS INCIDENT TO THE NRC UNDER REPORT #1455815 AND THE 48-HR FOLLOW UP FILED UNDER REPORT #1455992. 12-INCH MAIN IN QUESTION WAS TESTED TO ESTABLISH ITS MAOP AT 300PSIG ON 6/17/1994, HOWEVER, NATURAL GAS WAS INITIATED INTO THE PIPELINE ON 3/19/1996 WHEN THE OVERALL PROJECT WAS COMPLETE.
2026-06-30 10:38 | NO | YES | YES | 20260017 | 42425 | 2026-03-25 12:15 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2026-02-27 10:27 | EASTERN | NO | 2026 | POWDER MILL ROAD AND CHERRY HILL ROAD | BELTSVILLE | PRINCE GEORGE'S | MD | 20783 | 39.0399 | -76.9477 | YES | [8 empty] | 2026-02-27 23:58 | 1456026 | 1456108 | NATURAL GAS |  | 2928 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2026-02-27 22:00 | OPERATOR/CONTRACTOR |  | 2928 | YES | 0 | 2026-02-27 10:37 |  |  |  | 2026-02-27 11:15 | 2026-02-27 11:15 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 156 | NO | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1980 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES | 4 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2306 | MECHANICAL PUNCTURE | 2.6 | 3.3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 547 | 536.251001436021708 | 160739 | 157580.346836973845196 | 0 | 0 |  | 2.99 | 8755 | 8755 | 0 | 0 | 170041 | 71335.1346135714741472371134020618556701 | 166871.597838409866904 | 70 | 2 | 437 | 0 | 1 | 496 | 70 | 50 | 50 | 55 | 192.619(A)(2) | 1980-07-29 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY DAMAGE | [12 empty] | YES | 14 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | COUNTY ROAD | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 26084563 | N/A | NO | CONTRACT LOCATOR | NO | YES | 161 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | MARK AIESI |  | mark.aiesi@washgas.com | 5714054623 |  |  |  |  | STACEY FORD | VP EHS UTILITIES | 8325920316 | stacey.ford@washgas.com | ON FEBRUARY 27, 2026, AT APPROXIMATELY 10:27, A THIRD-PARTY CONTRACTOR CONDUCTING EXCAVATION ACTIVITIES STRUCK A 4-INCH SERVICE LINE LOCATED AT POWDER MILL ROAD AND CHERRY HILL ROAD IN BELTSVILLE, MARYLAND. WASHINGTON GAS WAS NOTIFIED OF THE INCIDENT AT 10:37 VIA FIREBOARD. THE EXCAVATION DAMAGE RESULTED IN A BLOWING GAS LEAK. THE INVESTIGATION DETERMINED THAT, ALTHOUGH A LOCATE TICKET HAD BEEN ISSUED AND CLOSED AS COMPLETE, THE AFFECTED SERVICE LINE WAS NOT MARKED IN THE FIELD BY THE LOCATE CONTRACTOR. THIS REPRESENTS A FAILURE IN LOCATE EXECUTION AND IS NOT ATTRIBUTED TO MAPPING INACCURACIES, INCORRECT RECORDS, OR DEFICIENCIES IN MAP REVIEW. WASHINGTON GAS PERSONNEL RESPONDED TO THE SCENE AND INITIATED REPAIR OPERATIONS. DURING THESE ACTIVITIES, AN IGNITION OCCURRED AT APPROXIMATELY 22:00. THE IGNITION WAS CAUSED BY A DIESEL EXCAVATOR ENGINE RUNAWAY RESULTING FROM INGESTION OF A NATURAL GAS-AIR MIXTURE. THE ENGINE SUBSEQUENTLY EMITTED FLAME FROM THE EXHAUST, WHICH IGNITED THE SURROUNDING FLAMMABLE ATMOSPHERE. CONTRIBUTING FACTORS INCLUDED THE OPERATION OF NON-INTRINSICALLY SAFE EQUIPMENT IN A FLAMMABLE ENVIRONMENT, CONTRARY TO ESTABLISHED PROCEDURES PROHIBITING SUCH ACTIVITY. AS A RESULT OF THE IGNITION, ONE WASHINGTON GAS EMPLOYEE SUSTAINED BURN INJURIES AND WAS TRANSPORTED TO THE HOSPITAL. THE EMPLOYEE WAS LOCATED WITHIN THE EXCAVATOR AT THE TIME OF THE IGNITION. WASHINGTON GAS CREWS ISOLATED THE AFFECTED SECTION OF PIPELINE AND STOPPED THE FLOW OF GAS AT APPROXIMATELY 00:45 ON FEBRUARY 28, 2026. THIS ACTION RESULTED IN A SERVICE OUTAGE IMPACTING 564 CUSTOMERS. CREWS SUBSEQUENTLY RESTORED SERVICE TO ALL AFFECTED CUSTOMERS. THE INVESTIGATION CONCLUDED THAT APPLICABLE PROCEDURES AND STANDARDS WERE ADEQUATE AND CLEARLY DEFINED THE REQUIRED CONTROLS FOR THIS TYPE OF OPERATION. THE EVENT WAS ATTRIBUTED TO A FAILURE TO FOLLOW AND ENFORCE ESTABLISHED REQUIREMENTS RATHER THAN DEFICIENCIES IN THE PROCEDURES THEMSELVES. ROOT CAUSES IDENTIFIED INCLUDED PROCEDURAL NONCOMPLIANCE AND WEAKNESSES IN SUPERVISORY OVERSIGHT. IN RESPONSE TO THE INCIDENT, WASHINGTON GAS HAS IMPLEMENTED CORRECTIVE ACTIONS TO ADDRESS PROCEDURAL COMPLIANCE AND SUPERVISORY OVERSIGHT, WITH THE OBJECTIVE OF REDUCING THE LIKELIHOOD OF RECURRENCE.
2026-06-30 10:38 | NO | YES | YES | 20260018 | 42089 | 2026-03-26 15:35 | ORIGINAL | 40196 | EVERSOURCE GAS OF MASSACHUSETTS | 157 CORDAVILLE RD | SOUTHBOROUGH | MA | 01772 | 2026-02-25 09:57 | EASTERN | NO | 2026 | 78 PLAIN ST | TAUNTON | BRISTOL | MA | 02780 | 41.8825 | -71.0826 |  |  | YES | [6 empty] | 2026-02-25 11:40 | 1455792 | 1455961 | OTHER GAS | UNDETERMINED, PENDING INVESTIGATION | 0 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | NO | [5 empty] | 0 | 2026-02-25 09:57 |  |  |  | 2026-02-25 10:25 | 2026-02-25 09:57 | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | UNDETERMINED, PENDING INVESTIGATION |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | NO LEAKS DETECTED ON SERVICE OR MAIN IN THE VICINITY | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | CURRENTLY UNDER INVESTIGATION | CLASS 3 LOCATION | 547200 | 536447.0712720129408 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 547200 | 217829.5215781118112 | 536447.0712720129408 | 0 | 0 | 6 | 0 | 0 | 3 | 0 | 87 | 90 | 98 | 192.619(A)(1) | 1983-06-27 | PRESSURE DID NOT EXCEED MAOP | OTHER | GAS DISTRIBUTION SYSTEM IS FED BY AN INJECTION PUMP |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT ISOLATED TO A SINGLE FOUR-FAMILY RESIDENCE | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | OGHENETEGA OGBAN | MANAGER GAS POLICY AND COMPLIANCE | oghenetega.ogban@eversource.com | 5088367135 |  | OGHENETEGA OGBAN | oghenetega.ogban@eversource.com | 5088367135 | OGHENETEGA OGBAN | MANAGER GAS POLICY AND COMPLIANCE | 5088367135 | oghenetega.ogban@eversource.com | TAUNTON PD CALLED TO REPORT A HOUSE FIRE AND POSSIBLE EXPLOSION AT THIS ADDRESS. EGMA TECHNICIANS, AND SUPERVISORS WERE DISPATCHED TO INVESTIGATE AND MAKE SAFE. UPON ARRIVAL, EVERSOURCE FOUND THE HOUSE IN FLAMES. FIRST RESPONDERS EVACUATED THE PREMISES PRIOR TO ARRIVAL. GAS SERVICE TO PREMISES WAS ISOLATED AT THE CURB VALVE PENDING FURTHER INVESTIGATION. NO LEAKS WERE DETECTED ON THE SERVICE OR ON THE MAIN IN THE VICINITY OF THE PROPERTY. THE COMPANY HAS NOT BEEN INFORMED BY DPU, FIRE DEPARTMENT, OR THE STATE FIRE MARSHAL OF THEIR FINDINGS OF THE CAUSE OF THE EVENT. PART A.11. IT IS UNDETERMINED WHETHER A FAILURE OCCURRED, THE COMPANY WAS INFORMED OF THE EVENT BY THE TAUNTON, MA POLICE DEPARTMENT. PART A.21. NO LEAKS WERE DETECTED ON THE SERVICE OR ON THE MAIN IN THE VICINITY OF THE PROPERTY PART A.22. THE COMPANY CANNOT CONFIRM THE NUMBER OF GENERAL PUBLIC EVACUATED. PART D.2.A THE PUBLIC AND NON-OPERATOR PRIVATE PROPERTY DAMAGE IS BASED ON THE TAUNTON ASSESSOR DATABASE FOR 2026 ASSESSMENTS. PART D.2.C. ESTIMATED COST IS UNKNOWN AT THIS TIME. PART E.6 THE POINT OF FAILURE IS UNKNOWN AND NO DETECTABLE LEAKS WERE NOTED ON THE SERVICE OR MAIN IN THE VICINITY OF THE PROPERTY.
2026-06-30 10:38 | NO | YES | NO | 20260019 | 42094 | 2026-03-26 19:06 | ORIGINAL | 4060 | ENBRIDGE GAS OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2026-02-27 12:33 | EASTERN | NO | 2026 | 5914 CABLE AVE | CLEVELAND | CUYAHOGA | OH | 44127 | 41.4682 | -81.6466 |  |  | YES | [6 empty] | 2026-02-27 16:46 | 1456012 |  | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-02-27 12:16 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | NO | 0 | 2026-02-27 12:16 |  |  |  | 2026-02-27 12:23 | 2026-02-27 12:23 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | OTHER | METER AND METER MANIFOLD | [9 empty] | OTHER | [8 empty] | CAUSED BY FIRE | CLASS 3 LOCATION | 345300 | 338514.5718388634292 | 2500 | 2450.87294989041 | 3762 | 3688.073614995088968 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 351562 | 139949.894490212252502 | 344653.518403748928168 | 0 | 0 | 3 | 0 | 0 | 4 | 0 | 0.42 | 0.42 | 1 | 192.619(A)(2) | 1961-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.6 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | B DEREK GOINS | SUPERVISOR PIPELINE SAFETY AND COMPLIANCE | derek.goins@enbridge.com | 3304147251 |  | B DEREK GOINS | derek.goins@enbridge.com | 3304147251 | B DEREK GOINS | COMPLIANCE SUPERVISOR | 3304147251 | derek.goins@enbridge.com | ON 2-27-26 AT APPROX. 12:14 P.M., ENBRIDGE GAS OHIO RECEIVED A CALL ABOUT A POSSIBLE EXPLOSION AT 5914 CABLE AVE CLEVELAND, OHIO. ENBRIDGE GAS ARRIVED ONSITE ABOUT 12:54 P.M. AND FOUND AN ACTIVE FIRE. GAS SERVICE WAS SHUT OFF AT THE CURB BOX, AND GAS WAS ALSO SHUT OFF TO NEIGHBORING STRUCTURES AT 5916 AND 5910 CABLE AVE. SERVICE LINES AT 5910, 5914, AND 5916 CABLE AVENUE WERE CUT AND PLUGGED. 5910, 5914, AND 5916 CABLE AVE SUSTAINED FIRE DAMAGE, AND 5917 CABLE AVENUE APPEARS TO HAVE SUSTAINED HEAT DAMAGE. ENBRIDGE GAS WAS UNABLE TO BAR HOLE THE PERIMETER OF 5914 CABLE DUE TO THE ACTIVE FIRE. BAR HOLE TESTING WAS DONE ON BOTH SIDES OF CABLE AVE IN FRONT OF 5916, 5914, AND 5910 CABLE WITH 0% NATURAL GAS DETECTED. CGI TESTING OF MAINLINES, SEWERS AND DRAINS ON BOTH SIDES OF CABLE AVE IN FRONT OF 5916, 5914, AND 5910 CABLE ALSO DETECTED NO LEAKS. ON 2-27-26, ENBRIDGE GAS LEAK TESTED THE STEEL SERVICE LINE AT 5910 CABLE. PRESSURE DROPPED FROM 10OZ. TO 2OZ. WITHIN 5 MIN OVER 19 FT OF 1.5” PIPE. THE PLASTIC SERVICE LINE AT 5916 CABLE HELD PRESSURE DURING A 10-MIN LEAK TEST. PRESSURE READINGS WERE TAKEN AT THE NEARBY REGULATOR STATION, AND THE INLET PRESSURE FOR THE STATION WAS 84.57PSIG AND THE LOW-PRESSURE OUTLET WAS 6.84OZ. ODORANT TESTING AT 5928 CABLE INDICATED ODOR WAS READILY DETECTIBLE AT 0.62%. ON 2-27-26, 2-28-26, AND 3-2-26, ENBRIDGE GAS CONDUCTED LEAK DETECTION SURVEYS ALONG CABLE AVE AND FOUND NO LEAKS. A JOINT SITE EXAMINATION ON 3-9-26 WAS LIMITED BY DEBRIS AT 5914 CABLE, WHICH PREVENTED SERVICE LINE TESTING AND ACCESS TO THE INSIDE METER. ENBRIDGE GAS RE-TESTED THE SERVICE LINE AT 5910 CABLE AT 7.5OZ. AND OBSERVED A PRESSURE DROP TO 5OZ. AFTER 5 MIN. A FLOW TEST INDICATED AN IN-SITU LEAK FLOW RATE OF LESS THAN 0.05 SCFH. THE SERVICE LINE AND OUTSIDE GAS METER AT 5910 CABLE WERE REMOVED AND PRESERVED. DURING A JOINT SITE EXAMINATION ON 3-13-26, CONTRACTORS FOR THE HOMEOWNER’S INSURER REMOVED DEBRIS FROM 5914 CABLE. THE ENCLOSED FRONT PORCH AREA AT 5914 CABLE WAS EXCAVATED AND THE STEEL SERVICE LINE BENEATH THE ENCLOSED PORCH WAS PARTIALLY EXCAVATED. ENBRIDGE GAS CUT APPROX. 1 FT OF SERVICE LINE TO PREPARE FOR LEAK TESTING TOWARDS THE STREET. THE UPSTREAM PORTION OF THE SERVICE LINE WAS LOOSE AND APPROX. 3 FT WAS REMOVED BY HAND. CORROSION, WALL THINNING, AND A FRACTURE IN THE SERVICE LINE WERE OBSERVED. A LEAK TEST FROM THE CUT CLOSEST TO THE METER TO THE CLOSED LOCK STOP HELD PRESSURE, WHILE A TEST FROM THE CUT TOWARD THE MAIN AT 10OZ. SHOWED A 3.1OZ. PRESSURE DROP AFTER 5 MINS. THE GAS METER, SERVICE LINE SECTIONS, FOUR APPLIANCES (FURNACE, WATER HEATER, A DRYER AND RANGE) AND ASSOCIATED HOUSE LINE PIPING FROM 5914 CABLE WERE REMOVED AND PRESERVED. ENBRIDGE GAS ANTICIPATES THAT A JOINT LABORATORY INSPECTION AND TESTING WILL BE SCHEDULED REGARDING ALL RECOVERED ARTIFACTS. AT THIS TIME ENBRIDGE GAS HAS MADE NO DETERMINATION THAT A RELEASE OF GAS FROM A JURISDICTIONAL FACILITY CONTRIBUTED TO OR CAUSED THE INCIDENT. THIS INVESTIGATION REMAINS ONGOING AND SUPPLEMENTAL NOTIFICATIONS WILL BE PROVIDED AS APPROPRIATE.
2026-06-30 10:38 | NO | NO | NO | 20260020 | 42348 | 2026-03-30 20:33 | SUPPLEMENTAL FINAL | 4060 | ENBRIDGE GAS OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2026-03-01 22:11 | EASTERN | NO | 2026 | 443 GARFIELD ST | YOUNGSTOWN | MAHONING | OH | 44502 | 41.0885 | -80.6683 |  |  |  | YES | [5 empty] | 2026-03-01 23:26 | 1456138 |  | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-03-01 22:11 | OTHER | HOUSE EXPLODED AND EXTINGUISHED. | 0 | YES | 0 | 2026-03-01 22:11 |  |  |  | 2026-03-01 22:19 | 2026-03-01 22:19 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | OTHER | [8 empty] | FIRE | CLASS 3 LOCATION | 94000 | 92152.822915879416 | 2500 | 2450.87294989041 | 3990 | 3911.59322802509436 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 100490 | 40003.08593454761679 | 98515.28909379492036 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0.45 | 0.45 | 1 | 192.619(A)(2) | 1968-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [137 empty] | YES | [18 empty] | B DEREK GOINS | SUPERVISOR PIPELINE SAFETY AND COMPLIANCE | derek.goins@enbridge.com | 3304147251 |  | B DEREK GOINS | derek.goins@enbridge.com | 3304147251 | B DEREK GOINS | SUPERVISOR PIPELINE SAFETY AND COMPLIANCE | 3304147251 | derek.goins@enbridge.com | AT APPROX. 22:00 ON 3-1-26, ENBRIDGE GAS RECEIVED A CALL THAT THERE WAS A FIRE/EXPLOSION AT 443 GARFIELD ST., YOUNGSTOWN, OH. AROUND 22:11 ENBRIDGE GAS WAS DISPATCHED TO THE SCENE AND ARRIVED AROUND 22:19. UPON ARRIVAL, THE FIRE WAS ALREADY EXTINGUISHED AS A RESULT OF THE EXPLOSION. THE OUTSIDE GAS METER HAD BEEN SHUT OFF ON 11-19-25 AND SEALED WITH A BULLET LOCK ON 12-1-25. ON 3-1-26, THE GAS METER WAS INACCESSIBLE DUE TO FALLEN DEBRIS. BAR HOLE TESTING WAS PERFORMED FOR 100 FEET IN EACH DIRECTION AT 10 FOOT INTERVALS IN FRONT OF 443 GARFIELD WITH 0% GAS READINGS RECORDED. NO INDICATION OF GAS WAS DETECTED ON THE MAIN OR SERVICE LINES AT 433, 438, 440, 442, 443, AND 450. ENBRIDGE GAS CUT AND ABANDONED THE 1 1/4" PLASTIC SERVICE LINE TO STOP THE FLOW OF GAS. ON 3-2-26 DEBRIS WAS REMOVED FROM THE METER LOCATION. THE LOCKSTOP WAS FOUND IN THE ON POSITION, WITH FRESH WRENCH MARKS ON THE LOCKSTOP OBSERVED. THE BULLET LOCK PREVIOUSLY INSTALLED ON THE METER WAS MISSING. DAMAGE WAS OBSERVED ON THE NIPPLE UPSTREAM OF THE METER. AN ADDITIONAL LEAK DETECTION SURVEY WAS CONDUCTED ON BOTH SIDES OF GARFIELD ST. ODOR READINGS TAKEN FROM A MAINLINE TAP WERE READILY DETECTIBLE AT 0.38%. PRESSURE READINGS AT A NEARBY REGULATOR STATION MEASURED 82.9 PSI INLET PRESSURE AND 7.24OZ. OUTLET PRESSURE. AN INDIVIDUAL ON SITE IDENTIFYING HERSELF AS THE PROPERTY MANAGER STATED THE PROPERTY WAS IN FORECLOSURE, CONFIRMED THAT BASEMENT APPLIANCES HAD BEEN REMOVED, AND INDICATED AN INSURANCE CLAIM WAS PENDING. OPEN HOUSELINE GAS PIPING WAS OBSERVED IN THE BASEMEN WITH NO APPLIANCES PRESENT. METER DATA INDICATED GAS SERVICE WAS OFF BUT HAD BEEN TURNED BACK ON AT APPROX. 19:00 ON 3-1-26. THE EXPLOSION BLEW OUT THE WINDOWS OF THE NEIGHBORING HOME AT 439 GARFIELD ST. ENBRIDGE GAS HAS DETERMINED THE APPARENT CAUSE OF THE INCIDENT TO BE INTENTIONAL DAMAGE; SPECIFICALLY, VANDALISM, ARSON, AND UNAUTHORIZED USE. THE IGNITION SOURCE WAS NOT IDENTIFIED.
2026-06-30 10:38 | NO | YES | NO | 20260021 | 42444 | 2026-04-01 16:35 | SUPPLEMENTAL | 38906 | LIBERTY UTILITIES (MIDSTATES NATURAL GAS) CORP. D/B/A LIBERTY UTILITIES | 2751 NORTH HIGH STREET | JACKSON | MO | 63755 | 2026-03-05 04:25 | CENTRAL | NO | 2026 | HWY 72 | JACKSON | CAPE GIRARDEAU | MO | 63755 | 37.4066 | -89.7448 | YES | [8 empty] | 2026-03-05 04:56 | 1456425 | 1456575 | NATURAL GAS |  | 3666.6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2026-03-04 22:24 | NO |  |  | 2026-03-04 23:50 | 2026-03-05 04:25 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | UNDER FLOOD WATER | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1953 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.156 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 4 | 4 |  | CLASS 2 LOCATION | 19500 | 19116.809009145198 | 1261259 | 1236474.226362331450476 | 0 | 0 | 0 | 0 |  | 5.0096 | 18368 | 18368 | 0 | 0 | 1299127 | 524804.3886101598353467319587628865979381 | 1273959.035371476648476 | 627 | 16 | 6320 | 0 | 0 | 6320 | 643 | 425 | 425 | 485 | 192.619(A)(4) | 2011-06-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | “THERE WAS NO CAUSE TO INVESTIGATE THE CONTROL ROOM OPERATOR BECAUSE THERE WERE NO REMOTE CONTROLLING ACTIONS THAT COULD HAVE BEEN PERFORMED TO EITHER PREVENT OR CONTROL THE INCIDENT. CONTROLLERS MADE TIMELY AND APPROPRIATE NOTIFICATIONS AS REQUIRED BY PROCEDURE.” | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  |  |  | YES | HEAVY FLOODING CAUSING DRAINING DITCH TO WASH OUT LEADING INTO BYRDS CREEK. | [178 empty] | YES | [34 empty] | RONALD SNIDER | DIRECTOR OF OPERATIONS | ronald.snider@libertyutilities.com | 573-225-7834 |  | RONALD SNIDER | ronald.snider@libertyutilities.com | 573-225-7834 | RONALD SNIDER | DIRECTOR OF OPERATIONS | 573-225-7834 | ronald.snider@libertyutilities.com | JACKSON, MISSOURI, RECEIVED APPROXIMATELY 4.7 INCHES OF RAINFALL OVER A 72-HOUR PERIOD, RESULTING IN SIGNIFICANT RUNOFF. THE VOLUME OF WATER OVERWHELMED A DRAINAGE DITCH OFF HIGHWAY 72, WHICH FEEDS INTO BYRDS CREEK, CAUSING A WASHOUT.
2026-06-30 10:38 | NO | YES | NO | 20260022 | 42116 | 2026-04-01 20:30 | ORIGINAL FINAL | 11032 | SPIRE MISSOURI INC. EAST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2026-03-03 13:27 | CENTRAL | NO | 2026 | 1 WHITE HAVEN CT | IMPERIAL | JEFFERSON | MO | 63052 | 38.3973 | -90.3997 | [5 empty] | YES |  |  |  | 2026-03-03 15:14 | 1456283 | 1456461 | NATURAL GAS |  | 44.48 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-03-03 13:27 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 44.48 | YES | 5 | 2026-03-03 12:17 |  |  |  | 2026-03-03 12:34 | 2026-03-03 14:20 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 62 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1987 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 12 | 2 | [7 empty] | CLASS 3 LOCATION | 249000 | 244106.945809084836 | 56995 | 55875.00151160156718 | 500 | 490.174589978082 | 12240 | 11999.47396266344736 | RESTORATION COSTS RELATED TO THE EXCAVATION ACTIVITIES ON 5 WHITE HAVEN CT. | 6.7976 | 302 | 302 | 0 | 0 | 319037 | 127128.0723597423511231443298969072164948 | 312773.59587332793254 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 39.71 | 40 | 60 | 192.619(A)(4) | 1987-04-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 8 | 0 | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [5 empty] | NO | NO | MEASURED DEPTH FROM GRADE | 62 | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 260551882 |  | Unknown | CONTRACT LOCATOR | NO | YES | 10 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ERIN MILKERT | MANAGER DISTRIBUTION INTEGRITY | erin.milkert@spireenergy.com | 314-349-2932 |  | ERIN MILKERT | erin.milkert@spireenergy.com | 314-349-2932 | RANDY WILSON | DIRECTOR - PIPELINE AND SYSTEM INTEGRITY | 205-337-1337 | randy.wilson@spireenergy.com | WHILE DIRECTIONAL BORING, A THIRD-PARTY EXCAVATOR, BLACKWELL CONTRACTING, COMPLETELY SEVERED A 2- INCH PLASTIC MAIN LOCATED AT 5 WHITE HAVEN CT. THE LOCATE TICKET HAD NOT BEEN MARKED AS COMPLETE IN THE 811 REPORTING SYSTEM, AND THE CONTRACTOR BORED WITHOUT CONFIRMING THE REQUIRED POSITIVE RESPONSE OF “MARKED” OR “CLEARED” FOR THE LOCATE REQUEST, OR SUBMITTING AN “INCORRECT LOCATE” TICKET TO THE 811 REPORTING SYSTEM. AFTER THE DAMAGE, BLACKWELL CONTRACTORS NOTIFIED LOCAL FIRST RESPONDERS, WHO PROMPTLY NOTIFIED SPIRE AND BEGAN EVACUATING NEARBY HOMES. AS SPIRE PERSONNEL WERE WORKING TO STOP THE GAS LEAK, GAS THAT HAD MIGRATED INTO A NEARBY HOME AT 1 WHITE HAVEN CT. IGNITED RESULTING IN AN EXPLOSION, LEAVING THE HOUSE SEVERELY DAMAGED. THERE WERE NO INJURIES OR FATALITIES DUE TO THIS INCIDENT.
2026-06-30 10:38 | NO | YES | YES | 20260023 | 42279 | 2026-04-02 17:44 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2026-03-02 14:37 | CENTRAL | NO | 2026 | 307 SUNSET BLVD | CROCKETT | HOUSTON | TX | 75835 | 31.3056 | -95.4611 | [6 empty] | YES |  |  | 2026-03-02 16:16 | 1456205 | 1456370 | NATURAL GAS |  | 21.11 | 0 | NO | [5 empty] | 0 | YES | 0 | 2 | 0 | 0 | 0 | 2 | YES | 2026-03-02 14:37 | OPERATOR/CONTRACTOR |  | 21.11 | NO | 3 | 2026-03-02 14:50 |  |  |  | 2026-03-02 14:57 | 2026-03-02 15:45 | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1925 | UNKNOWN |  |  |  |  | 2.375 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.154 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 7509 | 7361.441992290835476 | 1168 | 1145.047842188799552 | 0 | 0 |  | 3.38 | 71 | 71 | 0 | 0 | 8748 | 3511.967210713355904113402061855670103093 | 8577.489834479635028 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 38 | 38 | 60 | 192.619(A)(2) | 1925-01-01 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 0.5 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR DID NOT IDENTIFY THE CONTROLLER OR ACTIONS OF THE CONTROL ROOM WAS A CONTRIBUTING FACTOR. | [12 empty] | NO |  |  | YES | 6 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | UNQUALIFIED INDIVIDUAL WAS IN THE PROCESS OF REMOVING STOPPLE EQUIPMENT. |  |  | YES |  |  | OTHER MAINTENANCE | YES | NO, BUT THEY WERE PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | ELMER SELVERA | MANAGER COMPLIANCE TX | elmer.selvera@centerpointenergy.com | 281-755-2470 |  | ELMER SELVERA | elmer.selvera@centerpointenergy.com | 281-755-2470 | JERRY GANN | DIRECTOR COMPLIANCE | 713-967-7101 | jerry.gann@centerpointenergy.com | LAUREN SAMUELS LLC, A CONTRACTOR FOR CENTERPOINT ENERGY, WAS PERFORMING MAINTENANCE ACTIVITIES ON CENTERPOINT ENERGY FACILITIES. WHILE CONDUCTING A LEAK REPAIR ON A 2-INCH STEEL PIPELINE OPERATING AT A MAXIMUM ALLOWABLE OPERATING PRESSURE (MAOP) OF 60 PSIG, THE CONTRACTOR WAS PERFORMING WELDING, BYPASS, AND TAPPING AND STOPPING PROCEDURES WHEN A GAS IGNITION OCCURRED. THE IGNITION RESULTED IN BURN INJURIES TO TWO CONTRACTOR EMPLOYEES, BOTH OF WHOM REQUIRED OVERNIGHT HOSPITALIZATION. THE INVESTIGATION DETERMINED THAT CENTERPOINT ENERGY PROCEDURES WERE NOT FOLLOWED. SPECIFICALLY, THE INSTALLATION AND REMOVAL OF THE STOPPLE TOOL WERE PERFORMED BY AN INDIVIDUAL WHO WAS NOT QUALIFIED UNDER THE OPERATOR QUALIFICATION (OQ) PROGRAM. THIS ACTIVITY FALLS OUTSIDE PERMITTED SPAN OF CONTROL ALLOWANCES AND REQUIRES DIRECT PERFORMANCE BY A QUALIFIED INDIVIDUAL. LAUREN SAMUELS LLC HAS NOT BEEN ABLE TO CONTACT THE INDIVIDUAL PERFORMING THE TASK TO DETERMINE EXACTLY WHAT OCCURRED, BUT OTHER INFORMATION OBTAINED DURING THE INVESTIGATION INDICATES THE INDIVIDUAL WAS REMOVING THE STOPPLE AND BYPASS EQUIPMENT WHILE WELDING ACTIVITIES WERE SIMULTANEOUSLY UNDERWAY.
2026-06-30 10:38 | NO | NO | NO | 20260024 | 42453 | 2026-04-06 08:57 | SUPPLEMENTAL FINAL | 22435 | WEST TEXAS GAS UTILITY, LLC. | 508 W WALL ST SUITE 500 | MIDLAND | TX | 79701 | 2025-12-29 05:40 | CENTRAL | YES | 2025 | INTERSECTION OF CR CC & CR16 | CACTUS | SHERMAN | TX | 79013 | 36.0987 | -101.9004 |  | YES | [7 empty] | 2026-01-02 11:45 | 1451817 |  | NATURAL GAS |  | 5374 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2025-12-29 05:40 | NO |  |  | 2025-12-29 06:15 | 2026-01-02 11:30 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | OPP | CLASS 1 LOCATION | 0 | 0 | 13500 | 13500 | 0 | 0 | 4000 | 4000 | WAGES & EXPENSES | 3.38 | 18164 | 18164 | 0 | 0 | 35664 | 21899.4050773056780412371134020618556701 | 35664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 190 | 200 | 192.619(A)(4) | 1989-01-01 | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | INJECTION PUMP |  |  | YES | YES | NO | NO | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | CODY DRAPER | SAFETY AND SYSTEM INTEGRITY MANAGER | cdraper@wtg-energy.com | 4694084598 |  | CHARLIE GRIGGS | cgriggs@wtg-energy.com | 8062444513 | CODY DRAPER | SAFETY AND SYSTEM INTEGRITY MANAGER | 4694084598 | cdraper@wtg-energy.com | DECEMBER 28, 2025 - CIG REGULATION FAILURE OVER PRESSURIZED THE SYSTEM. DETERMINED THROUGH INVESTIGATION ON DECEMBER 29, 2025. VERIFIED THROUGH SCADA. DECEMBER 29, 2025 - TECHNICIAN, BRENT REHKOPF, RECEIVED PHONE CALL REGARDING RELIEF RELEASING GAS ON THE NORTH RESIDUE. DECEMBER 29, 2025 - TECHNICIAN ARRIVED ON-SITE TO INVESTIGATE. DECEMBER 29, 2025 - TECHNICIAN, BRENT, DETERMINED THAT THE CIG 3 WORKER/MONITOR WAS IN FAILURE AND ISOLATED THE INLET VALVE AND ENSURED SYSTEM WENT BACK TO CORRECT OPERATING PRESSURE. DECEMBER 31, 2025 - LEAK SURVEY COMPLETED ON THE NORTH AND EAST RESIDUE SYSTEMS WITH NO LEAKS FOUND. JANUARY 2, 2026 - SCADA DEPARTMENT WAS ABLE TO PROVIDE ALL DOCUMENTATION NEEDED TO DETERMINE THAT WE EXCEEDED THE RELEASE THRESHOLD WHICH LED TO US DETERMINING THAT THIS SHOULD BE CONSIDERED AN INCIDENT. JANUARY 2, 2026 - ONE HOUR NOTIFICATIONS WERE MADE TO PHMSA AND THE TEXAS RAILROAD COMMISSION. JANUARY 22, 2026 - EXISTING WORKER/MONITOR AT CIG 3 WAS REPLACED WITH NEW EQUIPMENT TO PROPERLY PROTECT OUR 600 MAOP ON THE TRANSMISSION LINE GOING TO THE NORTH RESIDUE. JANUARY 22, 2026 - DUEL WORKER/MONITOR REGULATOR RUNS PUT IN ON CR CC & CR 16 TO PROPERLY PROTECT THE 200 MAOP WHERE THE TRANSMISSION SUPPLIES GAS TO THE NORTH RESIDUE. FEBRUARY 6, 2026 - RELIEF INSTALLED AT THE ENERGY TRANSFER SUPPLY POINT TO BETTER PROTECT OUR MAOP OF THE NORTH AND EAST RESIDUE. THE MAOP WAS NOT EXCEEDED ON THE 600 PSI SYSTEM WHERE THE REGULATOR FAILED. THE PRESSURE ONLY REACHED 380 PSI. THERE WAS NOT AN OVERPRESSURE EVENT THAT OCCURRED. THIS EVENT IS REPORTABLE DUE TO THE AMOUNT OF GAS RELEASED. DUE TO A THUNDERSTORM, THE COMMUNICATION CONTROL BOX FOR THE REGULATOR WAS EFFECTED WHICH LED TO SCADA MALFUNCTION NOT ALLOWING THE PROPER COMMUNICATIONS BETWEEN THE SCADA DEPARTMENT AND THE FIELD. THIS LEAD TO THE RELEASE EVENT OF THE WEST RESIDUE DISTRIBUTION PIPELINE.
2026-06-30 10:38 | NO | NO | NO | 20260025 | 42137 | 2026-04-08 08:14 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2026-03-09 21:17 | EASTERN | YES | 2026 | 1093 FRANK RD. | COLUMBUS | FRANKLIN | OH | 43223 | 39.9161 | -83.0357 | [6 empty] | YES |  |  | 2026-03-09 21:26 | 1456802 | 1456944 | NATURAL GAS |  | 7576 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 25 | 2026-03-09 13:50 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2026-03-09 14:10 | 2026-03-09 14:04 | 2026-03-09 21:17 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 3 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1973 | UNKNOWN |  |  |  |  | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.175 | [6 empty] | OTHER | [8 empty] | 2 INCH BULL PLUG | CLASS 3 LOCATION | 0 | 0 | 12000 | 11764.190159473968 | 8250 | 8087.880734638353 | 0 | 0 |  | 5.04 | 38183 | 38183 | 1 | 1 | 58434 | 39159.4346656984032139175257731958762887 | 58036.070894112321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 165 | 174 | 192.619(A)(2) | 2004-02-15 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A THIRD-PARTY DAMAGE CAUSED THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | OTHER | [8 empty] | NO | NO | 18” – 36” |  | CONTRACTOR | BULLDOZER | ROAD WORK | YES | A604300132V0 | OHIO 811 | Unknown | CONTRACT LOCATOR | NO | NO |  | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | ROB R. SMITH | MANAGER OF OPERATION COMPLIANCE AND RISK MGMT. | rrsmith@nisource.com | 6144605491 |  | ROB R. SMITH | rrsmith@nisource.com | 6144605491 | ROB R. SMITH | MANAGER OF OPERATION COMPLIANCE AND RISK MGMT. | 6144605491 | rrsmith@nisource.com | COLUMBIA GAS OF OHIO INC. (COLUMBIA) RESPONDED TO A DISTRIBUTION MAIN LINE DAMAGE ON MARCH 9, 2026, AT 1093 FRANK RD. COLUMBUS, OHIO. THE OPERATOR FOUND THAT A BULLDOZER HAD STRUCK A PROPERLY MARKED MAINLINE AND HAD OPERATED A MECHANIZED EQUIPMENT WITHIN THE TOLERANCE ZONE, A VIOLATION OF STATE ONE-CALL LAW. COLUMBIA REPORTED THE INCIDENT TO THE PUCO AND THE NRC AS REQUIRED DUE TO 7.5 MILLION CUBIC FEET OF GAS LOSS. COLUMBIA PROTECTED LIFE AND PROPERTY UNTIL THE RELEASE WAS MADE SAFE. PLEASE CONSIDER THIS A FINAL REPORT.
2026-06-30 10:38 | NO | YES | NO | 20260026 | 42148 | 2026-04-10 08:49 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2026-03-12 16:45 | EASTERN | YES | 2026 | BROWN ROAD & GIDDINGS ROAD | LAKE ORION | OAKLAND | MI | 48359 | 42.7085 | -83.2635 | [6 empty] | YES |  |  | 2026-03-13 08:25 | 1457076 | 1457185 | NATURAL GAS |  | 4686 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2026-03-12 16:45 | YES | OPERATOR | 2026-03-12 16:58 | 2026-03-12 16:45 | 2026-03-13 07:31 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 72 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1981 | UNKNOWN |  |  |  |  | 4 | API-5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 2 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 109587 | 107433.525583856144268 | 681 | 667.617791550147684 | 0 | 0 |  | 2.91 | 13636 | 13636 | 0 | 0 | 123904 | 55001.123023327711840371134020618556701 | 121737.143375406291952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 245 | 274 | 192.619(A)(2) | 1981-05-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | COUNTY ROAD | [8 empty] | NO | NO | > 36” |  | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 2026031004718 |  | NO | FACILITY OWNER | NO | NO |  | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | CARMELLA KING | PRINCIPAL ENGINEERING TECHNICAL ANALYST | carmella.king@cmsenergy.com | 9892802963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 9892802963 | RANDY J. FARROW | SENIOR MANAGER ENGINEERING | 5173758565 | randy.farrow@cmsenergy.com | ON MARCH 12, 2026, AT APPROXIMATELY 16:45, A CONSUMERS ENERGY GAS DISTRIBUTION CREW WAS PERFORMING EXCAVATION ACTIVITIES AT THE INTERSECTION OF BROWN ROAD AND GIDDINGS ROAD IN LAKE ORION, MICHIGAN (OAKLAND COUNTY). DURING REMOVAL OF A SHORING BOX, THE EXCAVATOR BUCKET CONTACTED A RETIRED SERVICE TEE CONNECTED TO A 4-INCH STEEL HIGH PRESSURE PIPELINE, RESULTING IN AN UNINTENTIONAL RELEASE OF NATURAL GAS. THE GAS RELEASE WAS SAFELY ISOLATED USING EXISTING MUELLER PRESSURE CONTROL FITTINGS. THE AFFECTED PIPELINE SEGMENT WAS REPAIRED BY INSTALLING A PLIDCO BOLTED SPLIT SLEEVE AND WELDED ENCAPSULATION. NO LOSS OF SERVICE TO CUSTOMERS OCCURRED AS A RESULT OF THE INCIDENT. LOCAL POLICE AND FIRE DEPARTMENTS RESPONDED TO THE AREA AND ASSISTED WITH TRAFFIC CONTROL AND PUBLIC SAFETY. THERE WERE NO FATALITIES OR INJURIES ASSOCIATED WITH THIS INCIDENT. A ROOT CAUSE ANALYSIS DETERMINED THE INCIDENT WAS CAUSED BY EXCAVATION DAMAGE RESULTING FROM FAILURE TO MAINTAIN UTILITY MARKINGS. SOIL DISTURBANCE ASSOCIATED WITH THE PRIOR INSTALLATION OF THE SHORING BOX, COMBINED WITH WORK PERFORMED OVER MULTIPLE DAYS BY DIFFERENT PERSONNEL WITHOUT SUFFICIENT COMMUNICATION OR REVIEW OF UNDERGROUND FACILITY INFORMATION, CONTRIBUTED TO THE EVENT. CORRECTIVE MEASURES HAVE BEEN IDENTIFIED, INCLUDING REVISIONS TO APPLICABLE PROCEDURES AND COMMUNICATION OF LESSONS LEARNED TO IMPACTED EMPLOYEES.
2026-06-30 10:38 | NO | YES | NO | 20260027 | 42154 | 2026-04-13 08:10 | ORIGINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2026-03-14 12:19 | EASTERN | YES | 2026 | 86 MAGAZINE STREET | NEWARK | ESSEX | NJ | 07105 | 40.7266 | -74.1473 |  |  | YES |  | YES | YES |  |  |  | 2026-03-14 15:12 | 1457211 | 1457345 | NATURAL GAS |  | 73.85 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-03-14 12:19 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.3 | YES | 28 | 2026-03-14 12:19 |  |  |  | 2026-03-14 12:29 | 2026-03-14 12:19 | NO | PUBLIC PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2024 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | YES | UNABLE TO DETERMINE | YES | 1.25 | UNKNOWN | ENDOT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | PINHOLE | [6 empty] | CLASS 4 LOCATION | 750000 | 735261.884967123 | 3924 | 3846.890182147987536 | 19873 | 19482.479253268847172 | 0 | 0 |  | 1.07 | 79 | 79 | 0 | 0 | 773876 | 308097.6558285872211973092783505154639175 | 758670.254402539834708 | 0 | 0 | 1 | 3 | 0 | 3 | 0 | 13 | 13 | 15 | 192.619(A)(2) | 2024-10-29 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 5.2 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | NO | 18” – 36” |  | CONTRACTOR | HAND TOOLS | SEWER (SANITARY/STORM) | YES | 260730034 | 2.6069e+26 | NO | FACILITY OWNER | YES | YES | 24 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [143 empty] | YES | [26 empty] | HENRY VARUM | PRINCIPAL REGULATORY SPECIALIST | henry.varum@pseg.com | 732-343-3421 |  | HENRY VARUM | henry.varum@pseg.com | 732-343-3421 | CHRISTOPHER LAROSSA | SENIOR MGR REG POLICY AND PROCEDURE | 973-896-7617 | christopher.larossa@pseg.com | ON 3/4/2026 AT APPROXIMATELY 12:19 HRS PSEG WAS NOTIFIED OF A GAS IGNITION AND HOUSE EXPLOSION AT 86 MAGAZINE STREET NEWARK, NJ. PSEG ARRIVED ON SCENE AT 12:29 PM. FIRE AND POLICE WERE ONSITE. GAS WAS SHUT OFF AND AREA WAS MADE SAFE AT 14:16 HRS. 2 ADJACENT HOMES WERE EVACUATED, AND THREE PEOPLE WERE TRANSPORTED TO THE HOSPITAL FOR EVALUATION. ALL THREE PEOPLE WERE RELEASED THE SAME DAY WITH MINOR INJURIES. BARHOLE SURVEYS AND LEAK SURVEYS WERE COMPLETED WITH NO ADDITIONAL LEAKS FOUND. ACCESS TO THE BASEMENT IS PENDING A STRUCTURAL REVIEW AND SHORING OF THE HOME TO ENSURE THE SAFETY OF ALL PERSONNEL CONDUCTING THE INVESTIGATION. THE ROOT CAUSE OF THE INCIDENT IS STILL UNDER INVESTIGATION, PENDING LABORATORY TESTING. PRELIMINARY EVIDENCE AND EVENTS SHOW THAT A CONTRACTOR WORKING UNDER AN EMERGENCY MARKOUT WAS PERFORMING SEWER REPAIRS AND DAMAGED A FULLY EXPOSED 1.25" PLASTIC SERVICE THAT WAS SLEEVED THROUGH 2" STEEL. THE DAMAGE AND GAS RELEASE OCCURRED AFTER THE CONTRACTOR USED AN ELECTRIC DRILL TO DRILL A HOLE THROUGH THE STEEL GAS SERVICE. ADDITIONAL DAMAGE TO THE GAS SERVICE CONSISTENT WITH THE USE OF MECHANIZED EQUIPMENT WAS OBSERVED ON THE SERVICE IN QUESTION. EMERGENCY MARKOUT TICKET REQUESTS, PICTURES AND THE INITIAL DAMAGE INVESTIGATION CONFIRM THAT THE UNDERGROUND FACILITY WAS ACCURATELY MARKED. THIS INVESTIGATION IS ONGOING, PENDING FINAL LABORATORY TESTING OF THE GAS SERVICE AND METER SET.
2026-06-30 10:38 | NO | YES | NO | 20260028 | 42173 | 2026-04-15 17:55 | ORIGINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 3500 BLAKE ST | DENVER | CO | 80205 | 2026-03-16 17:17 | MOUNTAIN | YES | 2026 | 11446 W 17TH PLACE | LAKEWOOD | JEFFERSON | CO | 80215 | 39.7448 | -105.1272 | [5 empty] | YES |  |  |  | 2026-03-16 21:25 | 1457400 | 1457580 | NATURAL GAS |  | 9.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-03-16 17:17 | OTHER | GAS EXPLODED, NO FLAME AS A RESULT | 0 | YES | 4 | 2026-03-16 17:58 |  |  |  | 2026-03-16 17:58 | 2026-03-16 21:06 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | UNKNOWN |  |  |  |  | 1 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | LARGER THAN PINHOLE LEAK | [5 empty] | CLASS 3 LOCATION | 170000 | 166659.36059254788 | 29142 | 28569.335802282531288 | 13800 | 13528.8186833950632 | 0 | 0 |  | 1.385 | 13 | 13 | 0 | 0 | 212955 | 84778.5956403540738634432989690721649485 | 208770.515078225474488 | 0 | 0 | 4 | 0 | 1 | 4 | 0 | 12 | 13 | 15 | 192.619(A)(2) | 1969-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 12 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS UNRELATED TO CONTROL ROOM ACTIVITIES | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1969 | NO | YES | YES |  |  | 2026 |  |  |  |  | YES | COAL TAR |  | NO | [19 empty] | 2022-08-27 | NO | [201 empty] | YES | [25 empty] | NATHAN GONZALES | PRINCIPAL ENGINEER GAS COMPLIANCE | nathan.a.gonzales@xcelenergy.com | 303-285-8407 |  | NATHAN GONZALES | nathan.a.gonzales@xcelenergy.com | 303-285-8407 | CHRISTOPHER AKINS | DIRECTOR GAS GOVERNANCE | 303-571-3298 | christopher.a.akins@xcelenergy.com | ON MARCH 16, 2026, AT APPROXIMATELY 17:17 MST, AN EXPLOSION OCCURRED IN THE BASEMENT OF A RESIDENTIAL BUILDING ADJACENT TO A 1" NATURAL GAS DISTRIBUTION MAINLINE. EXCAVATION OF THE MAINLINE NEAR THE STRUCTURE, WHERE GAS READINGS WERE DETECTED, REVEALED THROUGH-WALL EXTERNAL CORROSION WITH ACTIVE GAS LEAKAGE. ADDITIONALLY, THE PIPE COATING IN THIS AREA WAS FOUND TO BE DAMAGED, AND FOREIGN UTILITIES WERE OBSERVED IN DIRECT PROXIMITY TO THE COMPROMISED COATING. THESE OBSERVATIONS SUPPORT A HYPOTHESIS THAT LATENT THIRD-PARTY DAMAGE MAY HAVE CONTRIBUTED TO ACCELERATED EXTERNAL CORROSION. IT IS BELIEVED THAT NATURAL GAS MIGRATED UNDERGROUND AND ENTERED THE STRUCTURE’S FOUNDATION, RESULTING IN THE FORMATION OF AN EXPLOSIVE ATMOSPHERE WITHIN THE BUILDING.
2026-06-30 10:38 | NO | YES | YES | 20260029 | 42177 | 2026-04-17 10:07 | ORIGINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2026-03-19 19:21 | CENTRAL | YES | 2026 | 620 MOSELEY STREET | LAKE DALLAS | DENTON | TX | 75065 | 33.1236 | -97.0203 | [5 empty] | YES |  |  |  | 2026-03-19 21:11 | 1457699 | 1457838 | NATURAL GAS |  | 1 | 1 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2026-03-19 19:21 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 30 | 2026-03-19 20:07 |  |  |  | 2026-03-19 20:07 | 2026-03-19 20:20 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 33 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1970 | 1970 |  |  |  |  | 1.25 | ASTM D2513 | NIPAK | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3306 | OTHER | [8 empty] | SEE NARRATIVE. | CLASS 3 LOCATION | 67500 | 66173.56964704107 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11.27 | 11 | 11 | 11 | 11 | 67522 | 26888.3354835994883762886597938144329896 | 66195.56964704107 | 1 | 0 | 346 | 0 | 0 | 346 | 1 | 48 | 48 | 60 | 192.619(A)(2) | 1970-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM OPERATING PERFORMANCE WAS WITHIN TYPICAL PRESSURE RANGES. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | BILL BROOKS | REGULATORY AND COMPLIANCE DIRECTOR | bill.brooks@atmosenergy.com | 806-787-9422 |  |  |  |  | MARC ROTHBAUER | COMPLIANCE AND REGULATORY REPORTING VP | 469-236-8616 | marc.rothbauer@atmosenergy.com | ON MARCH 19, 2026, AT APPROXIMATELY 7:21 P.M., ATMOS ENERGY RECEIVED A NOTIFICATION OF A STRUCTURE FIRE AND AN EXPLOSION AT 620 MOSELEY IN LAKE DALLAS. THE FIRST ATMOS ENERGY TECHNICIAN ARRIVED ON THE SCENE AT 8:07 P.M. ADDITIONAL COMPANY RESOURCES WERE REQUESTED PRIOR TO THE FIRST EMPLOYEE’S ARRIVAL ON SITE. ATMOS ENERGY PERSONNEL, WORKING WITH FIRST RESPONDERS, ESTABLISHED A SAFETY PERIMETER TO CONTROL THE SCENE AND INITIATED ON-SITE LEAK INVESTIGATION. AT APPROXIMATELY 8:20 P.M., IT WAS DETERMINED THAT SUB-SURFACE GAS HAD BEEN DETECTED IN THE VICINITY. AT 10:16 P.M., THE GAS SYSTEM IN THE VICINITY WAS ISOLATED, AND SERVICE WAS SHUT OFF WHICH IMPACTED 347 METERS IN THE AREA. DURING PRESSURE TESTING OF THE ASSETS TAKEN OUT OF SERVICE, IT WAS CONFIRMED THAT A SECTION OF PIPE PROVIDING SERVICE NEAR THE INCIDENT SITE DID NOT PASS A PRESSURE TEST. SERVICE RESTORATION TO CUSTOMERS IMPACTED BY THE OUTAGE BEGAN ON MARCH 21, 2026, UNDER THE OVERSIGHT OF REPRESENTATIVES OF THE RRC ON-SITE. A LEAK WAS FOUND IN THE 1.25” POLY MAIN NEAR THE INCIDENT SITE DURING THE POST-EVENT INVESTIGATION WORK. THE INVESTIGATION OF THIS EVENT REMAINS ONGOING. THE LAKE CITIES FIRE DEPARTMENT REPORTED THAT THERE WAS 1 HOSPITALIZATION AT THE AFFECTED RESIDENCE. THE VOLUME OF GAS RELEASED (PART A, 7, 8, 21C) IS STILL UNKNOWN AT THIS TIME. A VALUE OF 1 WAS ENTERED AS IT IS THE LOWEST VALUE THAT WILL VALIDATE IN THE FIELD. THE NUMBER OF THE GENERAL PUBLIC EVACUATED (PART A, 22) WAS 30 HOMES. THE VALUE OF 30 WAS USED, AS THE NUMBER OF PEOPLE IS UNKNOWN. THE COST ESTIMATES IN PART D HAVE NOT BEEN FINALIZED.
2026-06-30 10:38 | NO | YES | YES | 20260030 | 42180 | 2026-04-17 18:25 | ORIGINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 3500 BLAKE ST | DENVER | CO | 80205 | 2026-03-19 11:45 | MOUNTAIN | YES | 2026 | 510 BRYANT STREET | DENVER | DENVER | CO | 80204 | 39.7241 | -105.0183 | [5 empty] | YES |  |  |  | 2026-03-19 17:56 | 1457691 | 1457761 | NATURAL GAS |  | 6.61 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2026-03-19 11:45 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 6.61 | YES | 2 | 2026-03-19 12:43 |  |  |  | 2026-03-19 12:00 | 2026-03-19 17:45 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1976 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 150000 | 147052.3769934246 | 10000 | 9803.49179956164 | 10000 | 9803.49179956164 | 0 | 0 |  | 1.325 | 9 | 9 | 0 | 0 | 170009 | 67680.9751240252864948453608247422680412 | 166668.36059254788 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 132 | 140 | 150 | 192.619(A)(2) | 1976-01-23 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 10 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS UNRELATED TO CONTROL ROOM ACTIVITIES | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1976 | NO | YES | YES |  |  | 2025 |  |  |  |  | NO | COAL TAR |  | UNKNOWN | [19 empty] | 2025-07-22 | NO | [201 empty] | YES | [25 empty] | NATHAN GONZALES | PRINCIPAL ENGINEER GAS COMPLIANCE | nathan.a.gonzales@xcelenergy.com | 303-285-8407 |  | NATHAN GONZALES | nathan.a.gonzales@xcelenergy.com | 303-285-8407 | CHRISTOPHER AKINS | DIRECTOR GAS GOVERNANCE | 303-571-3298 | christopher.a.akins@xcelenergy.com | ON MARCH 19TH, 2026 AT APPROXIMATELY 11:45 AM MST, AN EXPLOSION OCCURRED WITHIN A COMMERCIAL BUILDING. FOLLOWING THE EXPLOSION, THE ADJACENT NATURAL GAS SERVICE LINE WAS EXCAVATED, AND THROUGH-WALL CORROSION WAS IDENTIFIED, WHICH PERMITTED THE RELEASE OF NATURAL GAS. ADDITIONALLY, A PREVIOUSLY REPAIRED SEWER LINE WAS OBSERVED APPROXIMATELY 18 INCHES DIRECTLY ABOVE THE CORRODED SECTION OF THE SERVICE LINE, SUPPORTING A HYPOTHESIS THAT EXCAVATION ACTIVITIES DURING THE SEWER LINE REPAIR DAMAGED THE PROTECTIVE COATING ON THE SERVICE LINE AND ACCELERATED THE GROWTH OF THE EXTERNAL CORROSION. IT IS BELIEVED THAT THE ESCAPING GAS THEN MIGRATED INTO THE STRUCTURE, RESULTING IN THE CREATION OF AN EXPLOSIVE ATMOSPHERE.
2026-06-30 10:38 | NO | YES | NO | 20260031 | 42189 | 2026-04-21 11:50 | ORIGINAL | 15845 | PRESQUE ISLE ELECTRIC & GAS COOPERATIVE | 3149 MAIN ST /P.O. BOX 308 | ONAWAY | MI | 49765 | 2026-03-21 12:15 | EASTERN | YES | 2026 | 13255 CAULKINS LK RD | JOHANNESBURG | OTSEGO | MI | 49751 | 44.8991 | -84.4078 | [5 empty] | YES |  |  |  | 2026-03-26 12:20 | 1458260 | 1458574 | NATURAL GAS |  | 30 | 30 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-03-21 12:15 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 25 | YES | 1 | 2026-03-21 12:15 |  |  |  | 2026-03-21 14:03 | 2026-03-21 14:03 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | COOPERATIVE |  | SERVICE RISER |  | 2011 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | OTHER | ANODELESS RISER | UNKNOWN | [6 empty] | OTHER | [8 empty] | RISER BROKE OFF. | CLASS 2 LOCATION | 150000 | 147052.3769934246 | 300 | 294.1047539868492 | 5050 | 4950.7633587786282 | 0 | 0 |  | 5.255 | 158 | 158 | 158 | 158 | 155666 | 62099.1301543469278912371134020618556702 | 152613.2451061900774 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 94 | 94 | 100 | 192.619(A)(1) | 2004-08-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 33 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | DAMAGE FROM SNOW/ICE | [56 empty] | SNOW/ICE IMPACT OR ACCUMULATION | [5 empty] | YES |  |  |  | YES | BLIZZARD | [213 empty] | GREG KARSTEN | DIRECTOR OF NATURAL GAS OPERATIONS | gkarsten@pieg.com | 9893062616 |  | GREG KARSTEN | gkarsten@pieg.com | 9893062616 | GREG KARSTEN | DIRECTOR OF NATURAL GAS OF OPERATIONS | 9893062616 | gkarsten@pieg.com | ON 3/21/26 AT 12:34, PIE&G ON CALL SUPERVISOR RECEIVED A CALL FROM OUR AFTER HOURS DISPATCH TO RESPOND TO A STRUCTURE FIRE ON CAULKINS LK RD. OUR SOUTH GAS STANDBY TECHNICIAN WAS IN THE FIELD WORKING ON OTHER CALLS, SO SUPERVISOR CALLED THE NEXT AVAILABLE TECH TO RESPOND. TECH ARRIVED ON SCENE AT 14:03 AND FOUND HOUSE FULLY INVOLVED IN THE FIRE AND MOSTLY CONSUMED. TECH NOTED GAS BURNING IN THE AREA OF THE RISER. FIRE AT RISER WENT OUT, LEAVING GAS BLOWING INTO THE REMAINS OF THE BURNING HOUSE. TECH WAS NOT ABLE TO APPROACH HOUSE DUE TO CONCERN OF SECONDARY IGNITION OF GAS. TECH RESPONDED BY LOCATING SERVICE LINE AND CAPPING THE LINE NEAR THE ROAD, ELIMINATING GAS FLOW TO THE RISER AT THE HOUSE. DUE TO SMOKE AND CONGESTION OF EMERGENCY RESPONDERS AT THE SCENE, THE TECH COMPLETE THE PAPERWORK FOR STRUCTURE FIRE RESPONSE AND LEFT THE SCENE WITH NO FURTHER INVESTIGATION. ON 3/25/26 AND EMAIL WAS SENT TO THE DIRECTOR OF GAS OPERATIONS BY MPSC STAFF INQUIRING ABOUT AN EXPLOSION ON PIE&G SYSTEM THAT WAS NOT REPORTED. DIRECTOR RESPONDED THAT WE HAD RESPONDED TO A STRUCTURE FIRE BUT HAD NO KNOWLEDGE OF AN EXPLOSION. MPSC REITERATED THAT THERE HAD BEEN AN EXPLOSION ACCORDING TO FIRE DEPT. PIE&G CONTACTED THE RESPONDING TECH AND ASKED IF THERE WAS A POSSIBILITY THAT THE HOUSE EXPLODED. TECH RESPONDED THERE WAS NOT, AS THE WALLS TO THE HOME HAD COLLAPSED INTO THE HOME, NOT OUT OF THE HOME AS WOULD BE NORMAL IN AN EXPLOSION. TECH WAS DISPATCHED TO GO BACK TO THE SCENE AND INVESTIGATE FURTHER. TECH NOTED THERE WAS MORE DEBRIS IN THE YARD THAN HAD BEEN VISIBLE DURING THE INITIAL RESPONSE DUE TO THE CONGESTION FROM THE RESPONDERS AND THE SMOKE AT THE SCENE. INSURANCE INVESTIGATOR WAS ON SCENE AND WAS RULING THE INCIDENT AN EXPLOSION. TECH INTERVIEWED NEIGHBORS WHO STATED THAT THERE WAS A MUFFLED NOISE AND WHEN THEY LOOKED OUT, THERE WAS SOME INSULATION/DEBRIS AIRBORNE IN THE YARD. TECH DISCOVERED THE RISER WAS SNAPPED OFF BELOW THE METER VALVE, AND THAT THERE WAS REMAINING CHUNKS OF ICE ON THE GROUND IN THE AREA OF THE RISER. AN ADDITIONAL CREW WAS DISPATCHED TO THE SCENE TO CONDUCT A PRESSURE TEST OF THE SERVICE LINE FROM THE POINT IT HAD BEEN CAPPED TO THE RISER. AIR TESTED AT 137# FOR 14 MINUTES, TEST PASSED. INFORMATION WAS BROUGHT BACK TO PIE&G HEADQUARTERS FOR REVIEW. ON 3/26/26 GAS PERSONNEL MET TO REVIEW ADDITIONAL INFORMATION REGARDING THE INCIDENT. MPSC STAFF CONTACTED PIE&G TO QUESTION WHY NO REPORT HAD BEEN FILED. AFTER ADDITIONAL INFORMATION HAD BEEN REVIEWED, PIE&G DID DETERMINE THAT THERE HAD BEEN AN EXPLOSION, AND MADE TELEPHONIC REPORTS TO THE MPSC & NRC ACCORDINGLY. ON 3/30/26 MPSC AGAIN CONTACTED PIE&G AND STATED THAT WE HAD NOT FILED A 48 HOUR UPDATE TO THE REPORT. PIE&G CONDUCTED AN INTERNET SEARCH OF 191.5 WHICH DID NOT INCLUDE THE 48 HOUR PROVISION, NOR WAS THAT INFORMATION RELAYED TO PIE&G DURING THE INITIAL REPORT. PIE&G CALLED IN A 48 HOUR UPDATE TO THE NRC LINE WITH NO FURTHER INFORMATION. 3/25/26-4/17/26 PIE&G PERSONNEL GATHERED ALL INFORMATION RELATED TO THE INCIDENT TO FINALIZE THE INVESTIGATION AND COMPLETE THE FINAL REPORT.
2026-06-30 10:38 | NO | YES | NO | 20260032 | 42207 | 2026-04-23 19:37 | ORIGINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2026-03-15 04:08 | PACIFIC | YES | 2026 | 1687 E HORSEHAVEN AVE | POST FALLS | KOOTENAI | ID | 83854 | 47.7277 | -116.9223 |  |  |  | YES | [5 empty] | 2026-03-25 11:10 | 1458178 | 1458376; 1458395 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-03-15 04:08 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | NO | 0 | 2026-03-25 09:30 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2026-03-15 05:35 | 2026-03-15 06:05 | 2026-03-25 09:30 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2021 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | YES |  |  |  | OTHER | REGULATOR | [9 empty] | OTHER | [8 empty] | ACCORDING TO IDAHO DEPARTMENT OF INSURANCE NEWS RELEASE, THE REGULATOR FAILED IN THE OPEN POSITION CAUSING OVERPRESSURE IN THE BUILDING AND A RESULTING FIRE. | CLASS 3 LOCATION | 750000 | 735261.884967123 | 0 | 0 | 500 | 490.174589978082 | 0 | 0 |  | 3.31 | 3 | 3 | 0 | 0 | 750503 | 298761.6829633932576649484536082474226804 | 735755.059557101082 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 53 | 55 | 60 | 192.619(A)(2) | 1981-12-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 6 |  | YES | YES | YES | NO | NO | OTHER | MEDIA |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | JOSH FORT | PRINCIPAL GAS COMPLIANCE ENGINEER | josh.fort@avistacorp.com | 509-495-2656 |  | RANDY BAREITHER | randy.bareither@avistacorp.com | 509-495-8716 | CARIE MOURIN | MANAGER GAS PIPELINE INTEGRITY AND COMPLIANCE | 509-495-2224 | carie.mourin@avistacorp.com | ON THE MORNING OF 3/15/25 AT APPROXIMATELY 05:35 LOCAL TIME, AVISTA WAS NOTIFIED OF A FIRE AT THE RIVER CHURCH, 1687 E. HORSEHAVEN AVE. IN POST FALLS, IDAHO. A GAS FIRST RESPONDER WAS DISPATCHED AND ARRIVED AT 06:05. UPON ARRIVAL, THE FIRST RESPONDER CHECKED IN WITH THE INCIDENT COMMANDER AND THEN PROCEEDED TO VISIT THE GAS METER/REGULATOR. THE FIRST RESPONDER FOUND THE METER SERVICE (INLET) VALVE ALREADY IN THE OFF POSITION. HE THEN PROCEEDED TO LOCK OFF THE METER AND THEN PERFORM A COMBUSTIBLE GAS INDICATOR (CGI) SWEEP OF THE AREA ALONG THE SERVICE ROUTE TO THE MAIN. NO INDICATION OF GAS WAS FOUND. UPON CHECKING IN WITH FIRE PERSONNEL ON THE SCENE, THE GAS FIRST RESPONDER WAS NOTIFIED THAT FIRE PERSONNEL DID NOT SUSPECT THAT AVISTA NATURAL GAS PLAYED A ROLE IN STARTING THE FIRE. PER AVISTA’S GAS EMERGENCY AND SERVICE HANDBOOK, WITH NO INDICATION OF NATURAL GAS FOUND DURING THE CGI SWEEP COUPLED WITH FIRE PERSONNEL STATING THERE WAS NO INDICATION OF THE FIRE BEING CAUSED BY NATURAL GAS, BARHOLES WERE NOT REQUIRED. THE FIRST RESPONDER LEFT THE SITE AT APPROXIMATELY 06:33 WITH NO INDICATION THAT AN INCIDENT REPORT TO THE NRC WAS REQUIRED AT THE TIME. TEN DAYS LATER AT APPROXIMATELY 09:30, AN ENGINEER IN THE NATURAL GAS COMPLIANCE DEPARTMENT NOTICED A NEWS FEED FROM THE LOCAL NEWSPAPER THAT MENTIONED A CHURCH FIRE IN POST FALLS, IDAHO THAT WAS NATURAL GAS RELATED. (THIS BECAME THE CONFIRMED DISCOVERY TIMEFRAME.) THAT INDIVIDUAL NOTIFIED THE COMPANY’S PRINCIPAL PIPELINE SAFETY ENGINEER OF THE FACT. THESE TWO PEOPLE ASSEMBLED SUFFICIENT DETAILS TO MAKE THE REPORT TO THE NRC AT 11:10. THE METER/REGULATOR STILL NEED TO BE TESTED BY THIRD PARTY ENTITY TO DETERMINE IF THE NATURAL GAS REGULATOR WAS TRULY THE CAUSE OF THE FIRE AS HAS BEEN NOTED BY THE IDAHO STATE DEPARTMENT OF INSURANCE IN THEIR NEWS RELEASE ON 3/24/26.
2026-06-30 10:38 | NO | YES | NO | 20260034 | 42231 | 2026-05-01 13:35 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2026-03-30 10:52 | EASTERN | YES | 2026 | 340 WEST PEACHTREE STREET NW | ATLANTA | FULTON | GA | 30308 | 33.7639 | -84.3875 | [6 empty] | YES |  |  | 2026-04-01 16:34 | 1458781 | 1458933 | NATURAL GAS |  | 3.21 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2026-03-30 10:52 | NO |  |  | 2026-03-30 11:12 | 2026-04-01 16:02 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 60 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1980 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.188 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 4 LOCATION | 174939 | 171501.305192351373996 | 16161 | 15843.423097271566404 | 49322 | 48352.782253797920808 | 0 | 0 |  | 3.67 | 12 | 12 | 0 | 0 | 240434 | 95717.0269181949982217938144329896907216 | 235709.510543420861208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | 45 | 192.619(A)(2) | 1980-01-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PINHOLE LEAK WAS DISCOVERED BY ROUTINE LEAK SURVEY, AND THE ASSOCIATED RELEASED VOLUME WAS MINIMAL, SO IT DID NOT REACH THE ALARM THRESHOLDS FOR THE CONTROL ROOM. FIELD OPERATIONS PERSONNEL NOTIFIED THE CONTROL ROOM ABOUT THE INCIDENT; HOWEVER, THE CONTROL ROOM’S ACTIONS WERE NOT A FACTOR IN THIS EVENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1980 | YES | YES | YES |  |  | 2026 |  |  |  |  | YES | COAL TAR |  | YES | [19 empty] | 2026-03-30 | NO | [227 empty] | RALPH T MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | 4045843733 | (404) 584-4710 |  |  |  | JOE CAUBO | MANAGER COMPLIANCE AND QA | 4044607894 | jfcaubo@southernco.com | A GRADE 1 LEAK WAS DISCOVERED BY ROUTINE LEAKAGE SURVEY ON 3/30/2026. UPON EXCAVATING THE MAIN, COMPANY PERSONNEL NOTED THE WRAP COATING WAS DISBONDED IN THE AREA OF PINHOLE LEAK ON THE BOTTOMSIDE OF THE PIPE. INITIALLY THE LEAK DID NOT MEET ANY OF THE CRITERIA FOR BEING REPORTABLE BUT WAS EVENTUALLY CALLED IN AT 16:02 ON 4/1/2026 WHEN COMPANY PERSONNEL DETERMINED THE TOTAL COST OF REPAIR, EMERGENCY RESPONSE, AND PAVEMENT RESTORATION WOULD AT SOME POINT MEET THE $149,700 PROPERTY DAMAGE THRESHOLD. AGLC REPORTED THIS INCIDENT TO THE NRC UNDER REPORT #1458782 AND THE 48-HR FOLLOW UP FILED UNDER REPORT #1458933. THE PROPERTY DAMAGE COSTS GIVEN IN PART D OF THIS REPORT ARE LESS THAN WHAT WAS ORIGINALLY REPORTED IN THE NRC REPORTS DUE TO THE FOLLOWING: - HAVING ACTUALS VS. ESTIMATED COSTS FROM INITIAL REPORTING - ISOLATING COSTS OF THE REPAIR FROM THE CONVENIENCE COSTS OF ADDITIONAL PIPE REPLACEMENTS DONE IN CONJUNCTION WITH THE LEAK REPAIR.
2026-06-30 10:38 | NO | YES | YES | 20260036 | 42285 | 2026-05-15 14:56 | ORIGINAL | 15938 | ENBRIDGE GAS NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2026-04-20 13:45 | EASTERN | YES | 2026 | 2401 NEW BETHEL CHURCH ROAD | GARNER | WAKE | NC | 27529 | 35.6504 | -79.5808 | [5 empty] | YES |  |  |  | 2026-04-20 15:05 | 1460224 | 1460424 | NATURAL GAS |  | 44 | 0 | NO | [5 empty] | 0 | YES | 0 | 2 | 0 | 0 | 0 | 2 | YES | 2026-04-20 13:45 | ALLOWED TO BURN OUT |  | 44 | NO | 0 | 2026-04-20 14:08 | YES | OPERATOR | 2026-04-20 14:15 | 2026-04-20 14:47 | 2026-04-20 14:47 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | NEW CONSTRUCTION TRENCH | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2026 | 2025 |  |  |  |  | 4.5 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | OTHER | [8 empty] | INCIDENT OCCURRED WHILE PURGING MAIN INTO SERVICE | CLASS 3 LOCATION | 12000 | 11764.190159473968 | 0 | 0 | 1611 | 1579.342528909380204 | 0 | 0 |  | 3.26 | 143 | 143 | 0 | 0 | 13754 | 5534.73441862167937687628865979381443299 | 13486.532688383348204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 2026-04-19 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA WAS NOT A CONTRIBUTING FACTOR IN THIS INCIDENT AS THE SYSTEM PRESSURE DID NOT DECREASE ENOUGH TO TRIGGER A LOW-PRESSURE ALARM. | [12 empty] | NO |  |  | YES | 2 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | CONTRACTOR DID NOT FOLLOW PURGING PROCEDURE |  |  | YES |  |  | COMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ANDREW MOORE | DIRECTOR CONSTRUCTION DESIGN AND CAPITAL PROJECTS | andrew.w.moore@enbridge.com | 7047184114 |  | ANDREW MOORE | andrew.w.moore@enbridge.com | 7047184114 | ANDREW MOORE | DIRECTOR CONSTRUCTION DESIGN AND CAPITAL PROJECTS | 7047184114 | andrew.w.moore@enbridge.com | ON MONDAY, APRIL 20, 2026, TWO CONTRACTORS, WORKING ON BEHALF OF ENBRIDGE GAS NORTH CAROLINA (EGNC), WERE INJURED DUE TO ACCIDENTAL IGNITION OF NATURAL GAS WHILE PURGING A PLASTIC GAS MAIN IN A NEW RESIDENTIAL SUBDIVISION. BOTH CONTRACTORS SUSTAINED BURNS THAT NECESSITATED HOSPITALIZATION. THEIR INJURIES REQUIRED MEDICAL INTERVENTION AND EXTENDED MONITORING, BUT WERE NOT LIFE-THREATENING. BOTH CONTRACTORS WERE RELEASED FROM THE HOSPITAL ON SATURDAY, MAY 2, 2026. THE INCIDENT ALSO RESULTED IN FIRE DAMAGE TO ONE OF THE CONTRACTOR’S VEHICLES AND SOME PLASTIC FUSION EQUIPMENT. AN NEARBY MEMBER OF THE CONTRACTOR CREW ALERTED TO THE FIRE CLOSED THE NEIGHBORHOOD SUPPLY VALVE A FEW MINUTES AFTER THE INCIDENT OCCURRED TO STOP THE FLOW OF GAS AND ALLOW THE FIRE TO BURN ITSELF OUT. THE CONTRACTORS DID NOT FOLLOW EGNC’S PROCEDURES FOR PURGING AND THE CONTROL OF ACCIDENTAL IGNITION. THE ACCIDENTAL IGNITION LIKELY RESULTED FROM THE DISCHARGE OF ACCUMULATED STATIC ELECTRICITY.
2026-06-30 10:38 | NO | YES | YES | 20260037 | 42310 | 2026-05-21 16:19 | ORIGINAL | 18104 | CPS ENERGY | 500 MCCULLOUGH | SAN ANTONIO | TX | 78215 | 2026-04-21 18:04 | CENTRAL | NO | 2026 | 15062 PRESTON HOLLOW | SAN ANTONIO | TEXAS | TX | 78250 | 29.5725 | -98.4312 | [7 empty] | YES | PLUG | 2026-04-21 19:40 | 1460558 |  | NATURAL GAS |  | 123 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 5 | 5 | YES | 2026-04-21 18:04 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 34 | 2026-04-21 18:12 |  |  |  | 2026-04-21 18:32 | 2026-04-21 18:50 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 49 | YES | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1993 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1 | ASTM 2513 | PERFORMANCE PIPE-DRISCOPIPE 8000 | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3350 | LEAK |  |  | OTHER | STILL UNDER NTSB INVESTIGATION | [5 empty] | CLASS 3 LOCATION | 1500000 | 1470523.769934246 | 0 | 0 | 18900 | 18528.5995011714996 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1518900 | 604644.1160909978619 | 1489052.3694354174996 | 0 | 0 | 2 | 1 | 0 | 4 | 0 | 8.2 | 9 | 33 | 192.619(A)(2) | 1993-11-05 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.1 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DURING THE INITIAL FAILURE INVESTIGATION ALL FACTORS WERE REVIEWED AND NEITHER THE CONTROLLER’S ACTION NOR CONTROL ROOM ISSUES WERE DETERMINED TO BE A CONTRIBUTING FACTOR. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | JOEL SETTLES | MANAGER GAS OPERATIONS COMPLIANCE | jsettles@cpsenergy.com | 2102593185 |  | JOEL SETTLES | jsettles@cpsenergy.com | 2102593185 | JOEL SETTLES | MANAGER GAS OPERATIONS COMPLIANCE | 2102593185 | jsettles@cpsenergy.com | ON APRIL 21, 2026 AT APPROXIMATELY 6:04 P.M., THE CPS ENERGY SYSTEM OPERATOR RECEIVED CALLS FROM THE SAN ANTONIO FIRE DEPARTMENT INDICATING A STRUCTURE FIRE AT 15062 PRESTON HOLLOW DRIVE. AT APPROXIMATELY 6:12 P.M., CPS ENERGY CREATED A GAS FIRE ORDER AND DISPATCHED A GAS TROUBLEMAN TO THE SCENE. THE GAS TROUBLEMAN ARRIVED AT APPROXIMATELY 6:32 P.M. AND FOUND THE STRUCTURE AT 15066 PRESTON HOLLOW DRIVE TO HAVE BEEN DAMAGED IN AN EXPLOSION AND FIRE. THE GAS TROUBLEMAN BEGAN MAKING THE SCENE SAFE AND ENSURING CPS ENERGY GAS METERS WERE SHUT OFF FOR THE SUBJECT PROPERTY. AFTER DETERMINING THE FIRE DEPARTMENT HAD ALREADY SHUT GAS OFF TO 15066 PRESTON HOLLOW DRIVE, THE GAS TROUBLEMAN LOCKED AND RED SEALED THE METER AT THAT ADDRESS. CPS ENERGY HAD ALSO DISPATCHED AN ELECTRIC TROUBLEMAN TO ENSURE THE ELECTRIC SERVICE METER WAS ALSO SHUT OFF. THE GAS TROUBLEMAN THEN BEGAN BAR HOLE TESTING NEAR 15066 PRESTON HOLLOW DRIVE AND THE SURROUNDING HOMES, INCLUDING 15070 PRESTON HOLLOW DRIVE AND 15062 PRESTON HOLLOW DRIVE. HE DID NOT FIND ANY POSITIVE READS IN THE BACKYARD OF 15070 PRESTON HOLLOW DRIVE. UPON SEEING POSITIVE READS IN THE BACKYARD OF 15062 PRESTON HOLLOW DRIVE, HE ASKED THE SYSTEM OPERATOR TO CONTACT A LEAK CREW TO INVESTIGATE FURTHER. THE LEAK CREW RECEIVED THE CALL FROM THE SYSTEM OPERATOR AT 6:55 P.M. AND ARRIVED ON SITE AT 7:35 P.M. THE GAS SERVICES MANAGER ARRIVED ON SITE AT APPROXIMATELY 7:30 P.M. AND, AFTER CONSULTING WITH THE TROUBLEMAN AND FIRE CREWS, DETERMINED THAT NATURAL GAS MAY HAVE BEEN INVOLVED IN THE EXPLOSION. ACCORDINGLY, THE MANAGER CALLED IN ADDITIONAL PERSONNEL AND RELAYED THE INFORMATION TO THE DIRECTOR OF GAS CONSTRUCTION AND THE VICE PRESIDENT OF GAS SOLUTIONS WHO HAD BEEN PREVIOUSLY NOTIFIED OF THE INCIDENT. ADDITIONALLY, THE MANAGER CONTACTED PHMSA AT 7:40 P.M. AND THE RAILROAD COMMISSION AT 7:50 P.M. THE CPS ENERGY CREW AT THE SCENE, WHICH WAS COMPRISED OF VARIOUS CRAFTS AND SPECIALTIES, CONTINUED BAR HOLE TESTING AND PERFORMING OTHER ANALYSES OF CPS ENERGY EQUIPMENT AND FACILITIES. AT APPROXIMATELY 8:25 P.M., THE STRUCTURE AT 15058 PRESTON HOLLOW DRIVE WAS DAMAGED IN A SECOND EXPLOSION AND FIRE. POWER WAS SHUT OFF TO THE NEIGHBORHOOD AT APPROXIMATELY 8:26 P.M. ONCE THE FIRE DEPARTMENT EXTINGUISHED THE FIRE AT 15058 PRESTON HOLLOW DRIVE, THE CPS ENERGY CREW AT THE SCENE CONTINUED BAR HOLE TESTING AND PERFORMING ITS INVESTIGATION INTO THE NIGHT. ADDITIONAL RESOURCES WERE CALLED TO THE SCENE AS APPROPRIATE AND AS NEEDED TO ASSIST THE CREW AND THE DISPLACED RESIDENTS OF PRESTON HOLLOW DRIVE. A LEAK WAS DISCOVERED, AND A CPS ENERGY LEAK CREW STOPPED THAT LEAK AT APPROXIMATELY 1:40 A.M. SHORTLY THEREAFTER, THE NATIONAL TRANSPORTATION SAFETY BOARD CONTACTED CPS ENERGY, ADVISED IT WOULD BE TAKING OVER THE SCENE, AND BEGAN DIRECTING THE CPS ENERGY CREW ON SITE REGARDING THE NTSB’S INVESTIGATION AND REMOVAL OF EQUIPMENT AND/OR EVIDENCE. THE INVESTIGATORY WORK AND ANALYSES THAT WAS CONDUCTED THEREAFTER WAS DIRECTED BY THE NTSB. THE SCENE WAS RELEASED TO THE CITY OF SAN ANTONIO IN THE EARLY EVENING ON APRIL 26, 2026.
2026-06-30 10:38 | YES | NO | NO | 20260038 | 42314 | 2026-05-22 15:53 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2026-04-24 09:48 | PACIFIC | YES | 2026 | 15946 WASHOAN ROAD | APPLE VALLEY | SAN BERNARDINO | CA | 92307 | 34.5412 | -117.2113 |  |  |  |  | YES |  |  | YES | SERVICE LINE ABANDONMENT | 2026-04-24 15:37 | 1460631 | 1460922 | NATURAL GAS |  | 0.01 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2026-04-24 13:33 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.01 | NO | 0 | 2026-04-24 09:48 |  |  |  | 2026-04-24 10:36 | 2026-04-24 13:33 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | SERVICE RISER AND OUTSIDE METER/REGULATOR SET | 2020 | UNKNOWN | [7 empty] | OTHER | STEEL SERVICE RISER AND OUTDOOR MSA | [9 empty] | OTHER | [8 empty] | GAS RELEASE FROM RISER DUE TO EXTREME HEAT FROM STRUCTURE FIRE AND/OR STRUCTURAL COLLAPSE | CLASS 3 LOCATION | 468900 | 459685.7304814452996 | 296 | 290.183357267024544 | 3242 | 3178.292041417883688 | 0 | 0 |  | 6.63 | 0 | 0 | 0 | 0 | 472438 | 188068.244728289451498 | 463154.205880130207832 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 37 | 37 | 40 | 192.619(A)(1) | 2020-11-10 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | BROOKE BACHMANN | COMPLIANCE ADMINISTRATOR ENGINEERING SERVICES | brooke.bachmann@swgas.com | (760)953-0271 |  | BROOKE BACHMANN | brooke.bachmann@swgas.com | (760) 953-0271 | SAMUEL GRANDLIENARD | VICE PRESIDENT SOUTHERN CALIFORNIA DIVISION | (760) 951-4024 | sam.grandlienard@swgas.com | SOUTHWEST GAS (SWG) RESPONDED TO A RESIDENTIAL STRUCTURE FIRE FOLLOWING A DOMESTIC DISPUTE INVOLVING TWO INDIVIDUALS. THE INCIDENT RESULTED IN ONE MALE SUSTAINING STAB WOUNDS AND BEING HOSPITALIZED, AND ONE FEMALE FATALITY. UPON ARRIVAL, SWG CONDUCTED AN AREA LEAK SURVEY, WITH NO GAS LEAKS DETECTED. THE STRUCTURE COLLAPSED DUE TO SEVERE FIRE DAMAGE, INCLUDING AT THE RISER AND METER LOCATION. DUE TO THE EXTENT OF STRUCTURAL AND GAS INFRASTRUCTURE DAMAGE, SWG ABANDONED THE SERVICE LINE. WHEN PROVIDED ACCESS TO THE PROPERTY, A SUPPLEMENTAL LEAK SURVEY WAS PERFORMED WITH NO GAS LEAKS DETECTED. AS OF THIS REPORT, INVESTIGATIVE AUTHORITIES FROM THE APPLE VALLEY FIRE PROTECTION DISTRICT AND THE SAN BERNARDINO COUNTY ARSON AND BOMB UNIT HAVE NOT DEFINITIVELY RULED OUT NATURAL GAS INVOLVEMENT IN THE FIRE'S ORIGIN OR CAUSE, AS THE INVESTIGATION REMAINS ONGOING. BASED ON INFORMATION RECEIVED FROM AUTHORITIES, FIRE PATTERNS, VIDEO EVIDENCE, EARLY RESPONDER ACCOUNT, AND OTHER CIRCUMSTANTIAL FACTORS, INVESTIGATORS HAVE A HIGH LEVEL OF CONFIDENCE THAT THE FIRE ORIGINATED FROM INSIDE THE STRUCTURE. NOTABLY, AUTHORITIES DO NOT SUSPECT FAILURE OF SOUTHWEST GAS INFRASTRUCTURE AS A CONTRIBUTING FACTOR TO THE ORIGIN OR CAUSE OF THE FIRE.
2026-06-30 10:38 | NO | YES | NO | 20260039 | 42316 | 2026-05-23 22:26 | ORIGINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2026-04-21 15:21 | EASTERN | YES | 2026 | 5722 FOXGLOVE PL. | WESTERVILLE | DELAWARE | OH | 43082 | 40.1267 | -82.9319 |  |  | YES | [6 empty] | 2026-04-21 15:21 | 146032 | 1460450 | NATURAL GAS |  | 0.1 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-04-21 12:31 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.1 | NO | 4 | 2026-04-21 12:36 |  |  |  | 2026-04-21 12:54 | 2026-04-21 15:16 | NO | PRIVATE PROPERTY | TRANSITION AREA | SOIL/AIR INTERFACE |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 2004 | 2004 | SINGLE FAMILY RESIDENTIAL | YES | YES | YES |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.099 |  | 2406 | LEAK |  |  | OTHER | LIKELY HEAT DAMAGE | [5 empty] | CLASS 3 LOCATION | 200000 | 196069.8359912328 | 1200 | 1176.4190159473968 | 6000 | 5882.095079736984 | 0 | 0 |  | 5.04 | 1 | 1 | 1 | 1 | 207202 | 82483.8599898550526432989690721649484536 | 203130.3500869171808 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 51.5 | 51 | 60 | 192.619(A)(2) | 2002-11-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.9 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS A SMALL RELEASE, TOO SMALL TO REGISTER ON SCADA EQUIPMENT | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | SETTING AND RISER SUSTAINED HEAT AND FIRE DAMAGE, INVESTIGATION IS ONGOING AND NO CAUSE HAS BEEN ASCERTAINED. | [154 empty] | ROB R. SMITH | MANAGER OF OPERATION COMPLIANCE AND RISK MGMT. | rrsmith@nisource.com | 6144605491 |  | ROB R. SMITH | rrsmith@nisource.com | 6144605491 | ROB R. SMITH | MANAGER OF OPERATION COMPLIANCE AND RISK MGMT. | 6144605491 | rrsmith@nisource.com | COLUMBIA GAS OF OHIO, INC. (COLUMBIA) ARRIVED ONSITE PER THE FIRE DEPARTMENT'S REQUEST AND MADE THE SITUATION SAFE. COLUMBIA FOUND THE METER SETTING AND RISER SUSTAINED HEAT AND FIRE DAMAGE FROM A STRUCTURE FIRE. THE INVESTIGATION IS ONGOING THAT WILL INCLUDE A LABORATORY EXAMINATION, TO DATE NO CAUSE HAS BEEN ASCERTAINED. PLEASE NOTE COLUMBIA ESTIMATED VALUES ON A.7, A.8, A.21.C, D.2.F, D.2G AND D.2.H. A LAB EXAM NEEDS TO BE HELD TO APPROXIMATE THE HOLE SIZE ON THE CARRIER PIPE WITHIN THE HEAT DAMAGED RISER PROTECTIVE SLEEVE. COLUMBIA WILL FILE SUPPLEMENTAL REPORTS AS REQUIRED.
2026-06-30 10:38 | NO | YES | NO | 20260040 | 42333 | 2026-05-29 10:26 | ORIGINAL FINAL | 4060 | ENBRIDGE GAS OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2026-04-30 09:36 | EASTERN | YES | 2026 | 1018 N STATE ST | GIRARD | TRUMBULL | OH | 44420 | 41.1645 | -80.706 | YES | [8 empty] | 2026-04-30 11:47 | 1461228 |  | NATURAL GAS |  | 23.04 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-04-30 09:36 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 29 | 2026-04-30 10:30 |  |  |  | 2026-04-30 10:30 | 2026-04-30 10:30 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 40 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2003 | UNKNOWN |  |  |  |  | 6.625 | PL-MD PE 2306 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2306 | MECHANICAL PUNCTURE | 3 | 3 | [7 empty] | CLASS 3 LOCATION | 125000 | 122543.6474945205 | 2500 | 2450.87294989041 | 7867 | 7712.406998715142188 | 0 | 0 |  | 3.7 | 85 | 85 | 0 | 0 | 135452 | 53956.1581774136629972061855670103092784 | 132791.927443126052188 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 41 | 41 | 60 | 192.619(A)(2) | 2003-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 36 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | YES | 18” – 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2612002464 | 811 | NO | CONTRACT LOCATOR | YES | YES | 7 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | B DEREK GOINS | SUPERVISOR PIPELINE SAFETY AND COMPLIANCE | derek.goins@enbridge.com | 3304147251 |  | B DEREK GOINS | derek.goins@enbridge.com | 3304147251 | B DEREK GOINS | SUPERVISOR PIPELINE SAFETY AND COMPLIANCE | 3304147251 | derek.goins@enbridge.com | ON 4-30-26 AT APPROX. 9:43 A.M., ENBRIDGE GAS OHIO RECEIVED A CALL FROM THE GIRARD FIRE DEPARTMENT THAT A GAS LINE WAS HIT NEAR 1018 N. STATE ST., IN GIRARD, OHIO 44420. WHILE IN ROUTE TO THE SCENE, ENBRIDGE GAS RECEIVED A CALL FROM TRUMBULL COUNTY 911 AT APPROX. 10:10 A.M. THAT A HOUSE ON THE CORNER IN FRONT OF THE HIT GAS LINE EXPLODED AND WAS ON FIRE. ENBRIDGE GAS ARRIVED ON SITE AT APPROX. 10:30 A.M. AND CONFIRMED THAT THE EXPLOSION OCCURRED AT 1018 N. STATE ST. A TOTAL OF 29 STRUCTURES WERE EVACUATED BY THE GIRARD FIRE DEPARTMENT. ENBRIDGE GAS ISOLATED AND STOPPED THE FLOW OF GAS TO THE DAMAGED GAS LINE AT APPROX. 11:12 A.M. DURING ENBRIDGE GAS’ INVESTIGATION, IT WAS DETERMINED THAT REDBIRD, A CONTRACTOR INSTALLING FIBER OPTIC CABLE FOR LUMOS, STRUCK A 6” PLASTIC GAS MAINLINE ON GORDON ST. NEAR THE INTERSECTION OF N. STATE ST. WHILE PERFORMING HORIZONTAL DIRECTIONAL DRILLING BENEATH THE PAVEMENT AND PERPENDICULAR TO THE MAINLINE WITHIN THE MUNICIPAL RIGHT-OF-WAY. REDBIRD DID NOT EXPOSE AND CONFIRM THE LOCATION OF THE MAINLINE (ALSO KNOWN AS POTHOLING) AS REQUIRED UNDER OHIO REVISED CODE § 3781.30(B)(1) PRIOR TO BORING. NO POTHOLING EQUIPMENT WAS FOUND IN REDBIRD’S POSSESSION ON SITE. REDBIRD ALSO DID NOT POTHOLE A MARKED WATER LINE ON GORDON ST. PRIOR TO CROSSING IT PERPENDICULARLY WITH ITS BORE. IN ADDITION, IT WAS DETERMINED THAT BENCHMARK, ENBRIDGE GAS’ LOCATING SERVICE PROVIDER, MIS-MARKED THE MAINLINE BY APPROX. 4 FEET. ENBRIDGE GAS IDENTIFIED THE CORRECT LOCATION OF THE MAINLINE AT APPROX. 3:30 P.M. LEAK DETECTION SURVEYS WERE CONDUCTED AT 1022, 1020, AND 1018 N. STATE ST. AND ON GORDON ST. RESIDUAL GAS FROM THE DAMAGED MAINLINE WAS DETECTED AND MONITORED WITHIN MANHOLES AND SEWERS. ODORANT TESTING AT 9 WASHINGTON AVE. CONFIRMED THAT ODOR WAS READILY DETECTABLE AT 0.70% ON THE FIRST TEST AND 0.72% ON THE SECOND TEST. ENBRIDGE GAS REPAIRED THE DAMAGED MAINLINE AT APPROX. 6:00 P.M. THE MAINLINE WAS REPRESSURIZED WITH GAS AT APPROX. 6:25 P.M. AT APPROX. 6:50 P.M., THE GAS SERVICE LINE TO 1018 N. STATE ST. WAS LEAK TESTED AT OPERATING PRESSURE FOR 10 MINUTES AND HELD PRESSURE. ON 5-1-26, FOLLOW-UP LEAK SURVEYS WERE PERFORMED AT N. STATE ST. AND GORDON ST. RESIDUAL GAS WAS DETECTED AT THE INTERSECTION OF N. STATE ST. AND GORDON ST. A HOLE WAS DRILLED IN THE BLACKTOP IN THIS AREA TO AERATE THE GAS TO THE ATMOSPHERE. SUBSEQUENTLY, NO SUSTAINED READING OF GAS WAS DETECTED. ENBRIDGE GAS HAS COMPLETED ITS INVESTIGATION AND CLASSIFIES THIS EVENT AS JURISDICTIONAL WITH THE APPARENT CAUSE BEING EXCAVATION DAMAGE BY A THIRD PARTY (REDBIRD). A CONTRIBUTING CAUSE OF THE EVENT IS THE MIS-MARKED MAINLINE BY BENCHMARK.
2026-06-30 10:38 | NO | YES | YES | 20260041 | 42380 | 2026-06-11 13:26 | ORIGINAL | 7348 | HOPE GAS, INC | 781 CHESTNUT RIDGE RD | MORGANTOWN | WV | 26505 | 2026-05-18 14:00 | EASTERN | YES | 2026 | 21 NOLTE LANE | PROCTOR | MARSHALL | WV | 26055 | 39.7342 | -80.706 |  | YES | [7 empty] | 2026-05-18 18:27 | 1462747 | 1462949 | NATURAL GAS |  | 25.71 | 0.14 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2026-05-18 14:00 | ALLOWED TO BURN OUT |  | 25.71 | NO | 0 | 2026-05-18 14:24 |  |  |  | 2026-05-18 15:20 | 2026-05-18 18:00 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | OTHER | EXPOSED DUE TO LOSS OF COVER |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | STEEL |  | LAP WELDED |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 5 | 0.5 | [7 empty] | CLASS 2 LOCATION | 35000 | 34312.22129846574 | 0 | 0 | 1491 | 1461.700627314640524 | 0 | 0 |  | 14.478 | 372 | 372 | 2 | 2 | 36865 | 14830.9449262782445579072164948453608247 | 36147.921925780380524 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 20 | 20 | 60 | 192.619(A)(4) | 1994-07-26 | PRESSURE DID NOT EXCEED MAOP | OTHER | ODOR FROM PRODUCTION GAS |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HOMEOWNER STRUCK THE PIPELINE WITH A VENTRAC LAWNMOWER. "DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION" DID NOT FIT THIS SCENARIO. | [154 empty] | MATTHEW ALDEN | GAS PIPELINE COMPLIANCE ANALYST | matthew.g.alden@hopegas.com | 681-896-7593 |  |  |  |  | ETHAN GARTON | PIPELINE SAFETY PROGRAM MANAGER | 304-641-3255 | ethan.garton@hopegas.com | ON MAY 18, AT APPROXIMATELY 14:00 HOURS THERE WAS A FIRE AT 21 NOLTE LANE, PROCTOR, WEST VIRGINIA 26055. THE INCIDENT IS STILL UNDER ACTIVE INVESTIGATION BY MULTIPLE PARTIES. HOPE GAS, INC. PERSONNEL RESPONDING TO THE SCENE FOUND DAMAGE TO HOPE'S LINE M-2372. AT APPROXIMATELY 14:00 HOURS ON 5/18/2026, THE HOMEOWNER STRUCK THE GAS LINE WITH THEIR MOWING TRACTOR, CAUSING A FIRE. THE ST. JOSEPH'S VOLUNTEER FIRE DEPARTMENT WAS NOTIFIED OF THE FIRE AT 14:00 HOURS. THE FIRE DEPARTMENT SHUT OFF THE GAS AT 14:15. HOPE GAS DISPATCH WAS NOTIFIED BY MARSHALL COUNTY EMERGENCY SERVICES AT 14:24. THE HOPE GAS FIRST RESPONDER ARRIVED ON-SITE AT 15:20. AFTER THE MOWER WAS MOVED, THE FIRST RESPONDER IDENTIFIED A HOLE IN THE PIPE APPROXIMATELY 5" LONG AND 0.5" WIDE. PIPELINE REPAIR WAS COMPLETED WITH A REPAIR CLAMP, AND THE LINE WAS PURGED AT 17:30. THE LINE WAS ENERGIZED AT 18:00. SERVICE RESTORATION IN THE AREA WAS COMPLETED AT 19:00. THE INFORMATION CONTAINED IN THIS REPORT IS PRELIMINARY AND MAY BE AMENDED OR SUPPLEMENTED PURSUANT TO 49 CFR § 191.9(B) OR AS OTHERWISE AUTHORIZED.
2026-06-30 10:38 | NO | YES | NO | 20260042 | 42383 | 2026-06-12 11:29 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2026-05-13 12:14 | EASTERN | YES | 2026 | 5121 MORNING WOOD DRIVE | MATTHEWS | MECKLENBURG | NC | 28105 | 35.0863 | -80.7039 |  | YES |  |  |  | YES |  |  |  | 2026-05-13 14:50 | 1462335 | 1462436 | NATURAL GAS |  | 1688.2 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-05-13 12:28 | ALLOWED TO BURN OUT |  | 1688.2 | NO | 3 | 2026-05-13 12:14 |  |  |  | 2026-05-13 12:33 | 2026-05-13 12:33 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2021 | 2020 |  |  |  |  | 8 | UNKNOWN | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 5 | 7 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1000000 | 980349.179956164 | 5000 | 4901.74589978082 | 0 | 0 |  | 4 | 6753 | 6753 | 0 | 0 | 1011753 | 405570.5333514617982989690721649484536082 | 992003.92585594482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 70 | 75 | 192.619(A)(1) | 2021-06-07 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.6 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS A 3RD-PARTY LINE STRIKE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [5 empty] | NO | NO | > 36” |  | CONTRACTOR | AUGER | POLE | YES | 2612401877 |  | NO | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | RANDALL SUTTLES | MANAGER- GAS REGULATORY COMPLIANCE | 513-287-3346 | randall.suttles@duke-energy.com | ON MAY 13TH, 2026 AT APPROXIMATELY 12:14PM, A NATURAL GAS INCIDENT/FIRE OCCURRED AT 5121 MORNING WOOD DRIVE IN MATTHEWS, NC. THE EVENT INVOLVED DAMAGE TO AN 8-INCH PLASTIC NATURAL GAS DISTRIBUTION MAIN, WHICH WAS STRUCK BY A THIRD-PARTY CONTRACTOR DURING THE INSTALLATION OF POWER POLES. THE IMPACT TO THE PIPELINE RESULTED IN THE RELEASE OF NATURAL GAS AND THE SUBSEQUENT IGNITION OF A GAS-FED FIRE. NO INJURIES OR FATALITIES WERE REPORTED AS A RESULT OF THE INCIDENT. THE CAUSE OF THE INCIDENT WAS DETERMINED TO BE A THIRD-PARTY DAMAGE RESULTING FROM EXCAVATION ACTIVITIES DUE TO MISMARKED LINES.
2026-06-30 10:38 | NO | YES | NO | 20260043 | 42385 | 2026-06-12 12:06 | ORIGINAL | 4060 | ENBRIDGE GAS OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2026-05-16 03:30 | EASTERN | YES | 2026 | 721 FIFTH ST | BELPRE | WASHINGTON | OH | 45714 | 39.274 | -81.5729 |  |  | YES | YES | [5 empty] | 2026-05-16 17:55 | 1462604 | 1462723 | NATURAL GAS |  | 1368 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2026-05-16 15:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1368 | YES | 0 | 2026-05-16 15:55 |  |  |  | 2026-05-16 15:54 | 2026-05-16 17:38 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | HOUSELINE | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | FLEXIBLE CONNECTOR WAS DISCONNECTED AT THE GAS DRYER FROM THE HOUSELINE | CLASS 3 LOCATION | 200000 | 196069.8359912328 | 0 | 0 | 3500 | 3431.222129846574 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 203500 | 81009.3341395207485 | 199501.058121079374 | 0 | 0 | 3 | 0 | 0 | 1 | 0 | 0.5 | 0.5 | 1 | 192.619(A)(2) | 1968-12-06 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.7 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [137 empty] | YES | [18 empty] | B DEREK GOINS | SUPERVISOR PIPELINE SAFETY AND COMPLIANCE | derek.goins@enbridge.com | 3304147251 |  | B DEREK GOINS | derek.goins@enbridge.com | 3304147251 | B DEREK GOINS | SUPERVISOR PIPELINE SAFETY AND COMPLIANCE | 3304147251 | derek.goins@enbridge.com | AT APPROXIMATELY 15:55 ON 5-16-2026, ENBRIDGE GAS RECEIVED A CALL THAT THERE WAS A FIRE/EXPLOSION AT A THREE-UNIT APARTMENT COMPLEX WITH THE ADDRESSES 719, 721 AND 723 FIFTH ST, BELPRE, OH. AROUND 16:03 ENBRIDGE GAS WAS DISPATCHED TO THE SCENE AND ARRIVED AROUND 16:54. UPON ARRIVAL, THE OUTSIDE GAS METERS HAD BEEN SHUT OFF BY THE FIRE DEPARTMENT. THE METERS FOR 719 AND 721 WERE FED OFF A SINGLE SERVICE LINE ON THE EAST SIDE OF THE BUILDING AND THE METER FOR 723 WAS FED OFF A SINGLE SERVICE LINE ON THE WEST SIDE OF THE BUILDING. BAR HOLE TESTING WAS PERFORMED FOR 100 FEET ALONG BOTH SERVICE LINES. A PINHOLE LEAK WAS FOUND ON THE RISER ON THE EAST SIDE OF THE BUILDING AT 719/721 FIFTH ST BUT WAS FOUND NOT TO BE CAUSAL. ENBRIDGE GAS SHUT THE CURB VALVE ON BOTH SERVICE LINES TO STOP THE FLOW OF GAS. ODOR READINGS WERE TAKEN FROM THE METER AT 714 FIFTH ST. AND FOUND READILY DETECTIBLE AT 0.68%. PRESSURE READINGS AT A NEARBY REGULATOR STATION MEASURED 8.09OZ OUTLET PRESSURE NEAR THE TIME OF THE EXPLOSION. A GAS DRYER IN THE CENTER UNIT (721 FIFTH ST.) WAS FOUND DISCONNECTED FROM THE HOUSE LINE WITH THE VALVE ON THE HOUSE LINE OPEN. METER DATA INDICATED A SPIKE IN GAS USAGE DOWNSTREAM FROM THE METER AT 721 FIFTH ST IN THE FOUR HOURS PRECEDING THE EXPLOSION. ENBRIDGE GAS HAS DETERMINED THE APPARENT CAUSE OF THE INCIDENT WAS OTHER OUTSIDE FORCES DAMAGE, SPECIFICALLY VANDALISM ON NON-JURISDICTIONAL PIPING. THE IGNITION SOURCE WAS NOT IDENTIFIED.
2026-06-30 10:38 | NO | YES | YES | 20260044 | 42408 | 2026-06-19 09:42 | ORIGINAL | 11800 | ATMOS ENERGY CORPORATION - LOUISIANA | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2026-05-20 08:08 | CENTRAL | YES | 2026 | 460 E HONORS POINT COURT | SLIDELL | ST. TAMMANY | LA | 70458 | 30.2401 | -89.7819 |  |  |  |  | YES |  |  |  |  | 2026-05-20 10:40 | 1462903 | 1463097 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2026-05-20 08:08 | OTHER | THE EXCESS FLOW VALVE ENGAGED, INTERRUPTED THE GAS FLOW, AND EXTINGUISHED THE FIRE. | 1 | NO | 0 | 2026-05-20 08:57 | NO |  |  | 2026-05-20 08:57 | 2026-05-20 10:44 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2004 | 2002 | SINGLE FAMILY RESIDENTIAL | YES | YES | NO | 0.75 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 1 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 4 | 3.921396719824656 | 912 | 894.078452120021568 | 0 | 0 |  | 3.1 | 3 | 3 | 0 | 0 | 919 | 367.084822663426000948453608247422680412 | 900.999848839846224 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 76 | 76 | 100 | 192.619(A)(1) | 1998-02-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 6.6 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES |  |  | YES | PRIVATE LANDOWNER | [6 empty] | NO | NO | 18” – 36” |  | CONTRACTOR | AUGER | UNKNOWN/OTHER | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 3 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | ANGELA MATHERNE | COMPLIANCE MANAGER | angela.matherne@atmosenergy.com | 504-206-7718 |  |  |  |  | ERIC SINGLETARY | VP TECH SERVICES | 504-756-9099 | eric.singletary@atmosenergy.com | ATMOS ENERGY'S FACILITY WAS DAMAGED BY A THIRD-PARTY EXCAVATOR. NO LOCATE TICKET REQUEST WAS SUBMITTED FOR THE EXCAVATION. ATMOS ENERGY WAS NOTIFIED OF THE DAMAGE AT 8:08 AM ON MAY 20, 2026. AN ATMOS ENERGY TECHNICIAN ARRIVED AT THE ADDRESS AT 8:57 AM. CONFIRMED DISCOVERY OCCURRED AT 10:44 AM.
2026-06-30 10:38 | NO | YES | NO | 20260045 | 42412 | 2026-06-19 15:04 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2026-05-20 21:17 | PACIFIC | YES | 2026 | 9600 S SEPULVEDA BLVD | LOS ANGELES | LOS ANGELES | CA | 90045 | 33.9471 | -118.3963 |  | YES | [7 empty] | 2026-05-21 01:23 | 1462987 | 1463133 | NATURAL GAS |  | 4447 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2026-05-20 21:17 |  |  |  | 2026-05-20 21:43 | 2026-05-21 01:20 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 44 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1970 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.195 | [6 empty] | RUPTURE |  |  |  |  | LONGITUDINAL |  | 4 | 3 |  | CLASS 1 LOCATION | 0 | 0 | 350000 | 343122.2129846574 | 400 | 392.1396719824656 | 0 | 0 |  | 6 | 26682 | 26682 | 0 | 0 | 377082 | 161218.0262519994334515463917525773195876 | 370196.3526566398656 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 78.8 | 175 | 175 | 192.619(A)(2) | 1970-02-03 | PRESSURE DID NOT EXCEED MAOP | OTHER | SOCALGAS ODORIZATION TAKES PLACE AT GAS SUPPLY ENTRY POINTS USING INJECTION PUMP ODORIZATION SYSTEMS | 7.8 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | WATER MAIN RUPTURE CAUSED DAMAGE TO EXISTING GAS MAIN. | [154 empty] | JERRY BOLIVAR | PIPELINE SAFETY ASSURANCE SENIOR I | bjerry@socalgas.com | 951-287-4591 |  | JERRY BOLIVAR | bjerry@socalgas.com | 951-287-4591 | JERRY BOLIVAR | PIPELINE SAFETY ASSURANCE SENIOR I | 951-287-4591 | bjerry@socalgas.com | ON 05/20/2026, SOCALGAS RESPONDED TO AN EXCAVATION INCIDENT. THE INITIAL REPORT INDICATED THAT A THIRD-PARTY CONTRACTOR MAY HAVE STRUCK A 6-IN STEEL GAS MAIN WITH GRADING EQUIPMENT DURING BACKFILL CONSTRUCTION ACTIVITIES, RESULTING IN A NATURAL GAS RELEASE. PRIOR TO BACKFILL, THERE WERE NO INDICATIONS OF DAMAGE OR LEAKS. AS BACKFILL NEARED COMPLETION, CREWS REPORTED DETECTING A GAS ODOR AND HEARING A HISSING SOUND. SOCALGAS CREWS WERE UNABLE TO OBSERVE THE CONDITION OF THE PIPE UNTIL GAS FLOW WAS CONTROLLED ON 05/21/2026 AT 02:05. FOLLOWING INSPECTION OF THE EXPOSED PIPE, SOCALGAS ASSESSED THE DAMAGE AND DETERMINED IT WAS CONSISTENT WITH A RUPTURE OF A WATER LINE LOCATED BENEATH THE GAS MAIN, WHICH WAS IDENTIFIED AS THE ROOT CAUSE OF THE INCIDENT. SOCALGAS MADE PERMANENT REPAIRS AND RESTORED SERVICE TO AFFECTED CUSTOMERS. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE CPUC ONCE SOCALGAS WAS MADE AWARE OF MEDIA COVERAGE AND THEN REPORTED TO DOT ONCE GAS RELEASE REACHED 3MMCF.
2026-06-30 10:38 | NO | YES | YES | 20260046 | 42439 | 2026-06-25 21:00 | ORIGINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2026-05-28 13:17 | CENTRAL | YES | 2026 | 409 E. 9TH STREET | DALLAS | DALLAS | TX | 75203 | 32.7485 | -96.8191 | [5 empty] | YES |  |  |  | 2026-05-28 14:56 | 1463665 | 1463667, 1463737 | NATURAL GAS |  | 46.4 | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2026-05-28 13:17 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 46.4 | YES | 10 | 2026-05-28 13:20 |  |  |  | 2026-05-28 13:20 | 2026-05-28 13:20 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 34 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1988 |  | MULTI-FAMILY RESIDENTIAL | NO |  | NO | 1.25 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 10 |  |  | 2306 | MECHANICAL PUNCTURE | 1.3 | 1.3 | [7 empty] | CLASS 3 LOCATION | 1765000 | 1730316.30262262946 | 1 | 0.980349179956164 | 0 | 0 | 0 | 0 |  | 8.4259 | 391 | 391 | 0 | 0 | 1765392 | 702930.5109431374290359484536082474226804 | 1730708.282971809416164 | 0 | 0 | 4 | 2 | 0 | 11 | 0 | 38 | 38 | 55 | 192.619(A)(2) | 1988-06-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 8.4 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM OPERATING PERFORMANCE WAS WITHIN TYPICAL PRESSURE RANGES. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [6 empty] | NO | NO | 18” – 36” |  | DEVELOPER | DRILLING | SITE DEVELOPMENT | YES | 2664191775 | ONE-CALL CENTER | NO | CONTRACT LOCATOR | YES | YES | 100 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | NTSB INVESTIGATION ONGOING | [169 empty] | BILL BROOKS | DIRECTOR OF REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 806-787-9422 |  |  |  |  | MARC ROTHBAUER | V.P. COMPLIANCE AND REGULATORY REPORTING | 469-236-8616 | marc.rothbauer@atmosenergy.com | THIS REPORT REFLECTS PRELIMINARY INFORMATION. THE INVESTIGATION, TO WHICH THE RAILROAD COMMISSION OF TEXAS AND PHMSA ARE PARTIES, IS ONGOING UNDER THE DIRECTION OF THE NATIONAL TRANSPORTATION SAFETY BOARD {NTSB}. ACCORDINGLY, THE RESPONSES IN THE REPORT WILL BE SUPPLEMENTED WHEN THE INFORMATION IS PERMITTED TO BE RELEASED BY THE NTSB. A22 REPRESENTS THE NUMBER OF BUILDINGS AS THE NUMBER OF PEOPLE ARE UNKNOWN.